## Notes
Notes
1 | Tab 'Cohort Table' follows the layout suggested in Ofwat's 'CW20-Additional-Cohort-Table-Guidance.xlsx' - this covers all mains.
2 | Primary and Secondary variables for material, age and pipe size are included.
3 | Additional variables were used in the analysis, as described in the Commentary, but it was impractical to include them in this table.
4 | The additional variables can be seen in the COHORT_ID and the structure is given in the GROUP field.
5 | For example, COHORT_REF 713 has:
| COHORT_ID: | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-NORTH_CEREDIGION-ABERYSTWYTH_BONTGOCH__LOVESGROVE-CEFNLLAN SR OUTLETS-ST DAVIDS RD
| GROUP: | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME
6 | The tab 'Cumulative Plot' is the requested plot of cumulative average annual bursts versus cumulative mains length. It is colour coded by condition grade.
7 | At pipe level, we have retained the ASSET_MATERIAL_BIN categories as used in our deterioration modelling:
Ferrous_1 includes Cast Iron and similar
Ferrous_2 includes Ductile Iron and similar
The Mains Material list provided in Table CW20.3 in the Ofwat guidance does not separately identify some of our key materials, such as AC, Alkathene, Ductile Iron, Steel
i.e this appears less suitable for our asset base than the categories we had already defined in our detrioration modelling work.
However, on the Cohort Table tab, three materials - CONC, GRP and VC - do not appear. This is because all pipes of these materials fall within Cohort IDs DIAM_GT_320 or DIAM_LT_320, a result of the automated, sequential approach described in the commentary.
8 | Cohort Refs 0.1 and 0.2 have been added to reconcile the total length from the analysis to the total length reported in APR23, both <320mm and >320mm.
The length difference was 0.4% of our APR23 reported mains length, and was due to the fact that our analysis was based on a GIS extract taken in March 2021, i.e. before the end of financial year 2023.
Virtually all of this additional length will be Plastic_PE laid as new pipe in FYE22 and FYE23, i.e. it is reasonable to assume zero bursts and condition grade 1 for this reconciliation length.
9 | A further requirement of the guidance was to reconcile total bursts/yr (average past five years) from the analysis with the equivalent APR-reported mains repairs.
Our analysis for CW20 was carried out on bursts that could be confidently linked to mains in the March '21 GIS extract, a lower number than APR-reported.
To reconcile these bursts with the APR-reported bursts, we have applied a universal uplift of 1.106107702 to derive the bursts/yr numbers in tab 'Cohort Table'
This ensures that the total bursts/yr in the tab 'Cohort Table, i.e. 4,033, matches the five-year average of APR-reported mains repairs.
10 | An additional tab - Cohort Table_MainsAge>5 - has been included to derive CW20 values for those lines requiring exclusion of mains laid in the last five years.
11 | Table CW20 lines have been generated using pivot tables from Cohort Table_all Mains and Cohort Table_MainsAge>5
Tab CW20 links each line to values pasted from these pivot tables.

## Cohort Table_All Mains
|  |  | Primary | Primary | Secondary |  | Primary | Secondary
COHORT_REF | COHORT_ID | GROUP | ASSET_MATERIAL_BIN | DATE_INSTALL_BIN_20YRS | DATE_INSTALL_BIN | DIAM_>GT or < LT 320mm | DIAM_BIN_PRIMARY | DIAM_BIN_SECOND | Sum of LENGTH_KM | Average of bursts_year | Nominal expected bursts | (Average Annual Bursts - Nominal expected)/Nominal expected % | Tolerance | Within Tolerance | Average of bursts_1000km_year | CONDITION_GRADE
0.1 | LENGTH RECONCILE <320mm |  |  |  |  | DIAM_LT_320 |  |  | 110.102 | 0 |  |  |  |  | 0 | 1
0.2 | LENGTH RECONCILE >320mm |  |  |  |  | DIAM_GT_320 |  |  | -2.6845 | 0 |  |  |  |  | 0 | 1
1 | DIAM_GT_320 | DIAM_LT_320 |  |  |  | DIAM_GT_320 |  |  | 581.7686 | 1.5494 | 1 | 54.94% | +/- 50% | OVER | 2.6633 | 1
2 | DIAM_GT_320-AC->320mm and <=450mm-B12_1960 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN | AC |  |  | DIAM_GT_320 | >320mm and <=450mm | (320,450] | 13.8486 | 0.88537 | 1 | -11.46% | +/- 50% | PASS | 63.9322 | 1
3 | DIAM_GT_320-AC->320mm and <=450mm-B14_1980-1961_1980-CENTRAL-NONE-(320,450]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__RUMNEY-ROVER WAY BULK-ROVER WAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B14_1980 | DIAM_GT_320 | >320mm and <=450mm | (320,450] | 0.92426 | 0.66403 | 1 | -33.6% | +/- 50% | PASS | 718.4464 | 4
4 | DIAM_GT_320-AC->450mm and <=610mm-B12_1960-1961_1980-NORTHERN-NONE-(450,610]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-YNYS MON SOSI TM-AREA FED BY S/SUPPLY 3B100F02 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_GT_320 | >450mm and <=610mm | (450,610] | 4.5664 | 0.66403 | 1 | -33.6% | +/- 50% | PASS | 145.415 | 2
5 | DIAM_GT_320-AC->610mm-B13_1970-1961_1980-NORTHERN-NONE-(610,1.7e+03]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON-BUCKLEY LIVERPOOL ROAD-EWLOE/HAWARDEN. | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B13_1970 | DIAM_GT_320 | >610mm | (610,1.7e+03] | 5.9835 | 0.66403 | 1 | -33.6% | +/- 50% | PASS | 110.976 | 1
6 | DIAM_GT_320-FERROUS_1->320mm and <=450mm | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY | FERROUS_1 |  |  | DIAM_GT_320 | >320mm and <=450mm | (320,450] | 122.4038 | 1.3281 | 1 | 32.81% | +/- 50% | PASS | 10.8498 | 1
7 | DIAM_GT_320-FERROUS_1->320mm and <=450mm-B06_1900-1881_1900 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | FERROUS_1 | 1881_1900 | B06_1900 | DIAM_GT_320 | >320mm and <=450mm | (320,450] | 13.4468 | 0.66403 | 1 | -33.6% | +/- 50% | PASS | 49.3821 | 1
8 | DIAM_GT_320-FERROUS_1->320mm and <=450mm-B06_1900-1901_1920 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | FERROUS_1 | 1901_1920 | B06_1900 | DIAM_GT_320 | >320mm and <=450mm | (320,450] | 22.1351 | 0.66403 | 1 | -33.6% | +/- 50% | PASS | 29.9989 | 1
9 | DIAM_GT_320-FERROUS_1->320mm and <=450mm-B08_1920-1901_1920-NORTHERN-NONE-(320,450]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT VALLEY TRUNK-AREA FED BY S/SUPPLY 3SC20M18 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_GT_320 | >320mm and <=450mm | (320,450] | 9.7304 | 0.88537 | 1 | -11.46% | +/- 50% | PASS | 90.9901 | 1
10 | DIAM_GT_320-FERROUS_1->320mm and <=450mm-B08_1920-1921_1940 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | FERROUS_1 | 1921_1940 | B08_1920 | DIAM_GT_320 | >320mm and <=450mm | (320,450] | 34.0957 | 0.66403 | 1 | -33.6% | +/- 50% | PASS | 19.4754 | 1
11 | DIAM_GT_320-FERROUS_1->320mm and <=450mm-B12_1960-1961_1980 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_GT_320 | >320mm and <=450mm | (320,450] | 27.5945 | 0.88537 | 1 | -11.46% | +/- 50% | PASS | 32.0851 | 1
12 | DIAM_GT_320-FERROUS_1->450mm and <=610mm | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY | FERROUS_1 |  |  | DIAM_GT_320 | >450mm and <=610mm | (450,610] | 70.762 | 1.5494 | 1 | 54.94% | +/- 50% | OVER | 21.8959 | 1
13 | DIAM_GT_320-FERROUS_1->450mm and <=610mm-B07_1910-1901_1920 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_GT_320 | >450mm and <=610mm | (450,610] | 31.2287 | 0.66403 | 1 | -33.6% | +/- 50% | PASS | 21.2634 | 1
14 | DIAM_GT_320-FERROUS_1->450mm and <=610mm-B08_1920 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN | FERROUS_1 |  |  | DIAM_GT_320 | >450mm and <=610mm | (450,610] | 44.2272 | 0.66403 | 1 | -33.6% | +/- 50% | PASS | 15.014 | 1
15 | DIAM_GT_320-FERROUS_1->450mm and <=610mm-B09_1930-1921_1940-CENTRAL-NONE-(450,610]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_GT_320 | >450mm and <=610mm | (450,610] | 4.594 | 0.66403 | 1 | -33.6% | +/- 50% | PASS | 144.5439 | 2
16 | DIAM_GT_320-FERROUS_1->450mm and <=610mm-B11_1950-1941_1960 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_GT_320 | >450mm and <=610mm | (450,610] | 29.4214 | 0.66403 | 1 | -33.6% | +/- 50% | PASS | 22.5696 | 1
17 | DIAM_GT_320-FERROUS_1->450mm and <=610mm-B12_1960-1961_1980-EASTERN-NONE-(450,610] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_GT_320 | >450mm and <=610mm | (450,610] | 20.4383 | 0.66403 | 1 | -33.6% | +/- 50% | PASS | 32.4895 | 1
18 | DIAM_GT_320-FERROUS_2 | DIAM_LT_320,ASSET_MATERIAL_BIN | FERROUS_2 |  |  | DIAM_GT_320 |  |  | 314.9393 | 0.66403 | 1 | -33.6% | +/- 50% | PASS | 2.1084 | 1
19 | DIAM_GT_320-FERROUS_2->320mm and <=450mm-B13_1970-1961_1980 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_GT_320 | >320mm and <=450mm | (320,450] | 29.5641 | 0.66403 | 1 | -33.6% | +/- 50% | PASS | 22.4607 | 1
20 | DIAM_GT_320-FERROUS_2->320mm and <=450mm-B13_1970-1961_1980-EASTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_GT_320 | >320mm and <=450mm | (320,450] | 21.1797 | 0.66403 | 1 | -33.6% | +/- 50% | PASS | 31.3521 | 1
21 | DIAM_GT_320-FERROUS_2->320mm and <=450mm-B13_1970-1961_1980-EASTERN-NONE-(320,450]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RASSAU__SIRHOWY_VALLEY-8119-CONFIRMED OUTSIDE OF SDMAS-UNALLOCATED LAND TREFIL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_GT_320 | >320mm and <=450mm | (320,450] | 1.0905 | 1.1067 | 1 | 10.67% | +/- 50% | PASS | 1014.8718 | 5
22 | DIAM_GT_320-FERROUS_2->320mm and <=450mm-B13_1970-1961_1980-EASTERN-NONE-(320,450]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_SW__RISCA__ABERCARN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_GT_320 | >320mm and <=450mm | (320,450] | 11.5111 | 0.66403 | 1 | -33.6% | +/- 50% | PASS | 57.6857 | 1
23 | DIAM_GT_320-FERROUS_2->320mm and <=450mm-B13_1970-1961_1980-NORTHERN-CEMENT_MORTAR-(320,450]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_GT_320 | >320mm and <=450mm | (320,450] | 20.4083 | 0.88537 | 1 | -11.46% | +/- 50% | PASS | 43.3829 | 1
24 | DIAM_GT_320-FERROUS_2->320mm and <=450mm-B13_1970-1961_1980-WESTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_GT_320 | >320mm and <=450mm | (320,450] | 33.3787 | 0.66403 | 1 | -33.6% | +/- 50% | PASS | 19.8938 | 1
25 | DIAM_GT_320-FERROUS_2->320mm and <=450mm-B14_1980-1961_1980-WESTERN-CEMENT_MORTAR-(320,450]-TYWI_C.U._AREA-CAERAU__YSTRADFELLTE-ONLLWYN OUTLET-ONLLWYN POST OFFICE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_2 | 1961_1980 | B14_1980 | DIAM_GT_320 | >320mm and <=450mm | (320,450] | 0.43955 | 0.88537 | 1 | -11.46% | +/- 50% | PASS | 2014.2681 | 5
26 | DIAM_GT_320-FERROUS_2->320mm and <=450mm-B14_1980-1981_2000 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | FERROUS_2 | 1981_2000 | B14_1980 | DIAM_GT_320 | >320mm and <=450mm | (320,450] | 96.7943 | 0.66403 | 1 | -33.6% | +/- 50% | PASS | 6.8602 | 1
27 | DIAM_GT_320-FERROUS_2->320mm and <=450mm-B15_1990-1981_2000 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | FERROUS_2 | 1981_2000 | B15_1990 | DIAM_GT_320 | >320mm and <=450mm | (320,450] | 97.9906 | 0.66403 | 1 | -33.6% | +/- 50% | PASS | 6.7765 | 1
28 | DIAM_GT_320-FERROUS_2->320mm and <=450mm-B15_1990-1981_2000-EASTERN-CEMENT_MORTAR-(320,450] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1981_2000 | B15_1990 | DIAM_GT_320 | >320mm and <=450mm | (320,450] | 43.6626 | 1.1067 | 1 | 10.67% | +/- 50% | PASS | 25.347 | 1
29 | DIAM_GT_320-FERROUS_2->320mm and <=450mm-B16_2000-2001_2020 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | FERROUS_2 | 2001_2020 | B16_2000 | DIAM_GT_320 | >320mm and <=450mm | (320,450] | 43.3081 | 0.66403 | 1 | -33.6% | +/- 50% | PASS | 15.3327 | 1
30 | DIAM_GT_320-FERROUS_2->320mm and <=450mm-B16_2000-2001_2020-EASTERN-EPOXY_RESIN-(320,450]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_2 | 2001_2020 | B16_2000 | DIAM_GT_320 | >320mm and <=450mm | (320,450] | 18.707 | 0.66403 | 1 | -33.6% | +/- 50% | PASS | 35.4963 | 1
31 | DIAM_GT_320-PLASTIC_PE->320mm and <=450mm-B16_2000-2001_2020-CENTRAL-NONE-(320,450] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 2001_2020 | B16_2000 | DIAM_GT_320 | >320mm and <=450mm | (320,450] | 0.78978 | 0.66403 | 1 | -33.6% | +/- 50% | PASS | 840.772 | 4
32 | DIAM_GT_320-PLASTIC_PVC->320mm and <=450mm-B13_1970-1961_1980-NORTHERN-NONE-(320,450]-NORTH_ERYRI_/_YNYS_MON-SOUTH_ANGLESEY_CWELLYN__MYNYDD-YNYS MON SOSI TM-AREA FED BY S/SUPPLY 3B300A03 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_GT_320 | >320mm and <=450mm | (320,450] | 3.3272 | 3.0988 | 1 | 209.9% | +/- 50% | OVER | 931.3456 | 4
33 | DIAM_GT_320-STEEL->320mm and <=450mm | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY | STEEL |  |  | DIAM_GT_320 | >320mm and <=450mm | (320,450] | 100.2912 | 1.1067 | 1 | 10.67% | +/- 50% | PASS | 11.035 | 1
34 | DIAM_GT_320-STEEL->320mm and <=450mm-B07_1910-1901_1920-NORTHERN-NONE-(320,450]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-BRYNIAU (CONWY)-BRYNIAU RES OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | STEEL | 1901_1920 | B07_1910 | DIAM_GT_320 | >320mm and <=450mm | (320,450] | 1.0956 | 0.66403 | 1 | -33.6% | +/- 50% | PASS | 606.0885 | 4
35 | DIAM_GT_320-STEEL->320mm and <=450mm-B07_1910-1901_1920-WESTERN-NONE-(320,450]-TYWI_C.U._AREA-BRYNGWYN-TWYNLLANAN-CEFN BEDW GOWER INPUT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | STEEL | 1901_1920 | B07_1910 | DIAM_GT_320 | >320mm and <=450mm | (320,450] | 8.7748 | 1.3281 | 1 | 32.81% | +/- 50% | PASS | 151.3498 | 2
36 | DIAM_GT_320-STEEL->320mm and <=450mm-B11_1950-1941_1960-WESTERN-NONE-(320,450]-PEMBROKESHIRE-PRESELI_SUPPLY-PRESELI USL OUTLETS-CLARBESTON RD/SCOLTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | STEEL | 1941_1960 | B11_1950 | DIAM_GT_320 | >320mm and <=450mm | (320,450] | 5.2198 | 1.1067 | 1 | 10.67% | +/- 50% | PASS | 212.0244 | 2
37 | DIAM_GT_320-STEEL->450mm and <=610mm-B07_1910-1901_1920 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | STEEL | 1901_1920 | B07_1910 | DIAM_GT_320 | >450mm and <=610mm | (450,610] | 9.9824 | 0.66403 | 1 | -33.6% | +/- 50% | PASS | 66.5203 | 1
38 | DIAM_GT_320-STEEL->450mm and <=610mm-B09_1930-1921_1940-CENTRAL-NONE-(450,610]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF-RHYDLAFAR 18 TDMA-SUPPLY SUB-SYSTEM BOUNDARY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | STEEL | 1921_1940 | B09_1930 | DIAM_GT_320 | >450mm and <=610mm | (450,610] | 0.89 | 1.1067 | 1 | 10.67% | +/- 50% | PASS | 1243.4971 | 5
39 | DIAM_GT_320-STEEL->610mm-B13_1970-1961_1980-WESTERN-NONE-(610,1.7e+03]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | STEEL | 1961_1980 | B13_1970 | DIAM_GT_320 | >610mm | (610,1.7e+03] | 2.3707 | 0.66403 | 1 | -33.6% | +/- 50% | PASS | 280.0994 | 3
40 | DIAM_LT_320 | DIAM_LT_320 |  |  |  | DIAM_LT_320 | <=320mm |  | 21.3205 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 124.5804 | 1
41 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm |  | 5.8399 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 341.1168 | 3
42 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-CENTRAL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm |  | 5.2457 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 295.3669 | 3
43 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(0,70]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (0,70] | 4.1092 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 377.0549 | 3
44 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (120,160] | 3.5494 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 748.3179 | 4
45 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF-TREFOREST-TREFOREST IND. EST. WEST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (120,160] | 1.5931 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 1945.1179 | 5
46 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(160,320] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (160,320] | 16.385 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 94.5619 | 1
47 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 6.9185 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 255.942 | 3
48 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RHYMNEY__BARGOED-WINDSOR HOTEL-THE GARTH ABERTRIDWR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 0.77481 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 2571.0789 | 5
49 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 12.9324 | 4.4269 | 2.5 | 77.07% | +/- 50% | OVER | 342.3085 | 3
50 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__RUMNEY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 1.902 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 814.613 | 4
51 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-VALE_OF_GLAM__RHONDDA_VALLEYS-LILLYPOT RESERVOIR-WELSH ST DONATS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 1.0857 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 2446.4234 | 5
52 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-EASTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm |  | 12.7852 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 190.4367 | 2
53 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(0,70]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (0,70] | 3.8631 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 401.0745 | 3
54 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(0,70]-TALYBONT-ABERGAVENNY__CWMTILLERY-PONTYPOOL TDMA-AREA FED BY SUB SUPPLY SYSTEM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (0,70] | 0.83958 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 2372.7288 | 5
55 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(120,160]-TALYBONT-ABERGAVENNY__CWMTILLERY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (120,160] | 1.8673 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 829.7712 | 4
56 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 13.5533 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 146.9819 | 2
57 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(70,120]-ELAN_/_BUILTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 0.71939 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 2461.4429 | 5
58 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 11.2162 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 138.1393 | 2
59 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM-ST BRIDES ROAD-MAGOR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 2.5896 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 940.2154 | 4
60 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-PONTYPOOL TDMA-AREA FED BY SUB SUPPLY SYSTEM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 1.6552 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 936.0783 | 4
61 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(0,70]-ALWEN_/_DEE-DENBIGH_ALWEN-MEIFOD-1104 FOELAS (G10) | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (0,70] | 0.68782 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 4505.2726 | 5
62 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-BEUDY MAWR-BEUDY MAWR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (0,70] | 0.82088 | 3.5415 | 2.5 | 41.66% | +/- 50% | PASS | 4314.247 | 5
63 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-BUTLINS-LLANGYBI - BODOWEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (0,70] | 0.57811 | 3.5415 | 2.5 | 41.66% | +/- 50% | PASS | 6125.9846 | 5
64 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (120,160] | 8.5262 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 181.7212 | 2
65 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 11.6219 | 4.2055 | 2.5 | 68.22% | +/- 50% | OVER | 361.8617 | 3
66 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 8.0434 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 302.7043 | 3
67 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-CONWY-GYFFIN-CASTLE VIEW | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 0.050541 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 30656.1545 | 5
68 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT & GORSWEN TRUNK-OUTLET LLANGERNYW SRV | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 2.7041 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 1064.098 | 5
69 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 4.7678 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 371.3969 | 3
70 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-CEMAES-CEMAES BAY VILLAGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 2.3822 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 743.3376 | 4
71 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-WESTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm |  | 4.1556 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 372.8448 | 3
72 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (0,70] | 6.1077 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 434.878 | 3
73 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-LLANLLWNI-BELL VUE TO LLANYBYDDER | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (0,70] | 2.1487 | 4.2055 | 2.5 | 68.22% | +/- 50% | OVER | 1957.2115 | 5
74 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-WESTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 2.8808 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 614.6761 | 4
75 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 15.6574 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 113.0931 | 1
76 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-GORLLWYN RHOS TREALAU-RHOS RES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 3.2204 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 1030.9672 | 5
77 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-BETTWS LLANGYBI AND LLANDDEWI BREFI-BETTWS BLEDRWS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 10.2832 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 150.6736 | 2
78 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-DERI GOCH PS TO RHOSYMRYSON SR-CAPEL Y GROES TO LLANWNEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 4.8674 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 318.3244 | 3
79 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | AC | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm |  | 11.2804 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 215.8407 | 2
80 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-EASTERN-NONE-(0,70]-ELAN_/_BUILTH-BUILTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (0,70] | 1.4022 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 1104.9859 | 5
81 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-NORTHERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | AC | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm |  | 9.4721 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 210.3098 | 2
82 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (0,70] | 6.1236 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 469.8966 | 3
83 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(0,70]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (0,70] | 1.5846 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 1117.4688 | 5
84 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (120,160] | 4.6256 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 478.5221 | 3
85 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(120,160]-ALWEN_/_DEE-DENBIGH_ALWEN-ALWEN TO PEN Y COED & ACCRE TRUNK-ACCRE PUMPING STATION | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (120,160] | 3.012 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 661.388 | 4
86 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(120,160]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-GWYTHERIN-GWYTHERIN RESOUTLET (R00) | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (120,160] | 2.8529 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 698.2568 | 4
87 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 3.7616 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 470.7388 | 3
88 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-ALWEN TO PEN Y COED & ACCRE TRUNK-ERYRYS PUMPING STATION | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 4.4887 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 345.1774 | 3
89 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-LLANGWYFAN-WAEN ABERWHEELER GEINAS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 3.5935 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 800.7289 | 4
90 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 3.4417 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 643.1134 | 4
91 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 3.4514 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 577.1877 | 4
92 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-BRYN BEDDAU SOUTH-BICELL RESERVOIR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 2.0079 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 1543.3199 | 5
93 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (0,70] | 1.0706 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 1654.0103 | 5
94 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (0,70] | 2.0403 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 759.4004 | 4
95 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(0,70]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH-CAPEL SEION LLANRHYSTUD-LLANFARIAN VILLAGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (0,70] | 0.60058 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 3316.958 | 5
96 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(0,70]-PEMBROKESHIRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (0,70] | 1.7768 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 872.0114 | 4
97 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 3.2862 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 471.4828 | 3
98 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 10.772 | 3.5415 | 2.5 | 41.66% | +/- 50% | PASS | 328.768 | 3
99 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-CRYMYCH-CRYMYCH AT GARN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 1.4875 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 1339.2198 | 5
100 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-CRYMYCH-PENTREGALAR AT GARN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 3.0278 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 950.3328 | 4
101 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-NORTH_CEREDIGION | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 5.1362 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 301.6632 | 3
102 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-NORTH_CEREDIGION-ABERYSTWYTH_BONTGOCH__LOVESGROVE-CEFNLLAN SR OUTLETS-ST DAVIDS RD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 0.37258 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 4752.6859 | 5
103 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 4.8758 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 317.7705 | 3
104 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE-MYNYDD NEWYDD TO FFOREST FACH-BLEAN Y MAES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 3.1898 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 485.7387 | 3
105 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm |  | 10.8718 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 142.5161 | 2
106 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm |  | 3.8971 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 511.1715 | 4
107 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-CENTRAL-NONE-(0,70]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (0,70] | 2.8204 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 706.3105 | 4
108 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 13.8036 | 4.6482 | 2.5 | 85.93% | +/- 50% | OVER | 336.7378 | 3
109 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_HEATH_&_LLANISHEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 3.3258 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 998.2997 | 4
110 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-EASTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (0,70] | 2.5498 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 781.276 | 4
111 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-EASTERN-NONE-(0,70]-BRECON_/_PORTIS-PORTIS-PORTIS LOW-LOWER CHAPEL LINE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (0,70] | 1.3053 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 1356.5295 | 5
112 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-EASTERN-NONE-(0,70]-ELAN_/_BUILTH-BUILTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (0,70] | 0.16572 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 9349.2358 | 5
113 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-EASTERN-NONE-(0,70]-ELAN_/_BUILTH-BUILTH-BUILTH WELLS-AREA FEED BY 1T810231 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (0,70] | 1.279 | 5.9763 | 2.5 | 139.1% | +/- 50% | OVER | 4672.6662 | 5
114 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-EASTERN-NONE-(0,70]-ELAN_/_BUILTH-BUILTH-BUILTH WELLS-BUILTH TO CILMERY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (0,70] | 0.35372 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 4380.2431 | 5
115 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-EASTERN-NONE-(0,70]-ELAN_/_BUILTH-BUILTH-GARTH SR-LLANWRTYD WELLS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (0,70] | 0.69857 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 2217.9474 | 5
116 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-EASTERN-NONE-(120,160]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL-WESTHIDE HEREFORD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (120,160] | 3.6672 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 422.5038 | 3
117 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 11.2538 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 177.0146 | 2
118 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-EASTERN-NONE-(70,120]-PILLETH-PILLETH_KNIGHTON__BLEDDFA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 4.0589 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 381.7248 | 3
119 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (0,70] | 8.1131 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 300.1033 | 3
120 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(0,70]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (0,70] | 1.1018 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 1406.2892 | 5
121 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (0,70] | 0.90435 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 2202.7806 | 5
122 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (120,160] | 12.6438 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 140.0478 | 2
123 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(120,160]-SOUTH_MEIRIONNYDD-LLWYNGWRIL_GWASTADCOED-GWASTADCOED-HENBLAS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (120,160] | 4.262 | 3.7628 | 2.5 | 50.51% | +/- 50% | OVER | 882.878 | 4
124 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 19.3447 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 114.4203 | 1
125 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(70,120]-BARMOUTH-BARMOUTH_-_HARLECH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 3.3617 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 592.5818 | 4
126 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(70,120]-BARMOUTH-BARMOUTH_-_HARLECH-DYFFRYN TALYBONT LLANBEDR-TALYBONT VILLAGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 0.69619 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 3815.2261 | 5
127 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 7.6012 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 291.1954 | 3
128 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-HOLLAND ARMS 9INCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 6.6768 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 265.2077 | 3
129 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-HOLLAND ARMS 9INCH-DWYRAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 5.1358 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 301.689 | 3
130 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm |  | 10.7973 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 163.9981 | 2
131 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (0,70] | 5.3968 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 369.1243 | 3
132 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (0,70] | 11.3849 | 4.4269 | 2.5 | 77.07% | +/- 50% | OVER | 388.837 | 3
133 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-CROSSROADS TO CRUGIAU AND TREGAMMON-TREGAMMON WD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (0,70] | 11.0909 | 8.6324 | 2.5 | 245.3% | +/- 50% | OVER | 778.3277 | 4
134 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-EGLWYSWRW-BRYNBERIAN WD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (0,70] | 1.2282 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 1802.2405 | 5
135 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-FFYNNON LLAWDDOG-BEULAH TO CWMCOU | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (0,70] | 3.2952 | 4.4269 | 2.5 | 77.07% | +/- 50% | OVER | 1343.4325 | 5
136 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-NEWQUAY-SYNOD INN TO NEW QUAY 6 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (0,70] | 2.0653 | 7.083 | 2.5 | 183.3% | +/- 50% | OVER | 3429.5888 | 5
137 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-PENPARC SR TO CARDIGAN SR-PENPARC SOUTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (0,70] | 2.0532 | 5.0909 | 2.5 | 103.6% | +/- 50% | OVER | 2479.5297 | 5
138 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SARNAU CROSS CONNECTION-SARNAU BPT OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (0,70] | 3.6154 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 857.1217 | 4
139 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-MAESTIR TO BRYNGARREG-MAESTIR TO BRYNGARREG | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (0,70] | 0.21322 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 7266.5871 | 5
140 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-NORTH_CEREDIGION | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (0,70] | 0.98235 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 1577.2454 | 5
141 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (0,70] | 9.9933 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 287.9384 | 3
142 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-CEFN BRYN OUTLETS TO S W GOWER-PENMAEN WD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (0,70] | 1.3151 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 2019.7044 | 5
143 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (120,160] | 9.5513 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 231.7408 | 2
144 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-CEFN BRYN HOUSE-REYNOLDSTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (120,160] | 1.3203 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 1173.5481 | 5
145 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (120,160] | 7.1162 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 248.8318 | 2
146 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 18.7472 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 177.1009 | 2
147 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-BEULAU TO ABERBANC-BLEANGWENLLAN X NCE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 2.9898 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 814.3504 | 4
148 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-CROSSROADS TO CRUGIAU AND TREGAMMON-TREGAMMON WD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 2.3846 | 6.6403 | 2.5 | 165.6% | +/- 50% | OVER | 2784.6183 | 5
149 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-FFYNNON LLAWDDOG-FFYNNON LLAWDDDOG SCHEME | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 4.9998 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 664.0599 | 4
150 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-GWENLLI-PENBONTARBOTHAU BPT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 1.0639 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 1456.3003 | 5
151 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-HAFOD FELINWYNT-HAFOD FELINWYNT 5 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 3.5242 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 942.0971 | 4
152 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-HAFOD LLECHRYD-LECHRYD VILLIAGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 1.2023 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 1472.7799 | 5
153 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-NEWQUAY-SYNOD INN TO NEW QUAY 6 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 5.736 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 424.4722 | 3
154 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-PENTREGAT CROSS CONNECTION-PENTREGAT RES OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 4.3563 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 508.0978 | 4
155 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SARNAU CROSS CONNECTION-SARNAU BPT OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 5.0112 | 5.0909 | 2.5 | 103.6% | +/- 50% | OVER | 1015.9064 | 5
156 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SARNAU CROSS CONNECTION-TANYGROES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 1.9396 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 1711.7578 | 5
157 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SARNAU CROSS CONNECTION-TRESAITH SCHEME | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 3.1246 | 5.0909 | 2.5 | 103.6% | +/- 50% | OVER | 1629.2987 | 5
158 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 3.9624 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 558.6093 | 4
159 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 13.783 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 208.7678 | 2
160 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 4.8045 | 5.3122 | 2.5 | 112.5% | +/- 50% | OVER | 1105.6862 | 5
161 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-PORTHYRHYD TO CEFNEITHIN-FOELGASTELL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 0.13471 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 14788.1964 | 5
162 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-TRAPP BULK EXPORT-PENYBANK/NANTGARDEIG 6 INCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 1.6162 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 1232.5745 | 5
163 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAPEL_DEWI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 0.50267 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 3082.3542 | 5
164 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAPEL_DEWI-POLIN TO RHYDARGAEAU-RHYDARGAEAU P S | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 4.0586 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 490.836 | 3
165 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-LLANELLI_FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 3.5694 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 434.0778 | 3
166 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 14.803 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 104.6678 | 1
167 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-CEFN BRYN OUTLETS TO S W GOWER | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 15.1447 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 116.9214 | 1
168 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-CEFN BRYN OUTLETS TO S W GOWER-OXWICH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 2.5153 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 1143.9595 | 5
169 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-CEFN BRYN OUTLETS TO S W GOWER-PENMAEN WD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 4.2806 | 8.6324 | 2.5 | 245.3% | +/- 50% | OVER | 2016.6247 | 5
170 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 10.4762 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 169.0255 | 2
171 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm |  | 33.1212 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 86.8766 | 1
172 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm |  | 19.3949 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 102.7117 | 1
173 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 1.8729 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 1418.2103 | 5
174 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(0,70]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 4.2062 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 578.8498 | 4
175 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 5.4197 | 5.5336 | 2.5 | 121.3% | +/- 50% | OVER | 1021.0115 | 5
176 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_EAST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 0.9101 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 1702.4568 | 5
177 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-PENARTH-ST TEILOS PENDINE AND SKOMER RD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 0.29837 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 5192.8793 | 5
178 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(160,320]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_HEATH_&_LLANISHEN-BLACKOAK ROAD-BLACKOAK ROAD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (160,320] | 0.7559 | 7.9683 | 2.5 | 218.7% | +/- 50% | OVER | 10541.5364 | 5
179 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 4.7049 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 376.3609 | 3
180 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-PONTYPRIDD_PONTSTICILL_HIGH-TY GWYN 12INCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 1.3237 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 1170.5027 | 5
181 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-VALE_OF_GLAM__RHONDDA_VALLEYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 5.0536 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 306.5938 | 3
182 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 14.3354 | 3.5415 | 2.5 | 41.66% | +/- 50% | PASS | 247.0445 | 2
183 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__CANTON__CATHAYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 2.4999 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 708.3125 | 4
184 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_EAST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 4.3021 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 360.153 | 3
185 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_HEATH_&_LLANISHEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 10.6719 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 207.4067 | 2
186 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 7.0003 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 284.572 | 3
187 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 10.1224 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 218.6656 | 2
188 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(0,70]-ELAN_/_BUILTH-BUILTH-GARTH SR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 5.7607 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 499.4978 | 3
189 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(0,70]-ELAN_/_BUILTH-BUILTH-GARTH SR-GARTH-BEALAH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 0.67056 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 3300.8639 | 5
190 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(0,70]-ELAN_/_BUILTH-BUILTH-GARTH SR-TIRABAD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 0.72706 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 3348.7765 | 5
191 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(0,70]-ELAN_/_BUILTH-ELAN-NEUADD NORTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 2.035 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 978.9268 | 4
192 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(0,70]-TALYBONT-ABERGAVENNY__CWMTILLERY-PONTYPOOL TDMA-AREA FED BY SUB SUPPLY SYSTEM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 0.1904 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 8137.7708 | 5
193 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 21.1255 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 104.7753 | 1
194 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(120,160]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL-WESTHIDE HEREFORD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 0.76275 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 2031.3397 | 5
195 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(120,160]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL-WESTHIDE NEWTON-WESTHIDE TO NEWTOWN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 3.0441 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 581.6913 | 4
196 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(120,160]-PILLETH-PILLETH_KNIGHTON__BLEDDFA-LLANGUNLLO LINE-AREA FEED BY 1T810701 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 4.0872 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 649.8656 | 4
197 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 6.5519 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 236.4795 | 2
198 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 29.6322 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 112.0452 | 1
199 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 26.063 | 3.5415 | 2.5 | 41.66% | +/- 50% | PASS | 135.8817 | 2
200 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 12.5944 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 193.3212 | 2
201 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN-PONTNEWYDD-MAENDY WAY TOP | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 4.9681 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 356.4235 | 3
202 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 5.653 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 313.2388 | 3
203 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-CROSS ASH-THE BOOT NEWCASTLE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 1.7035 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 1429.2934 | 5
204 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-LLANELLEN 6INCH-LLANELLEN BRIDGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 1.5261 | 4.6482 | 2.5 | 85.93% | +/- 50% | OVER | 3045.8136 | 5
205 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-WHITBOURNE-WHITBOURNE-RIDGEWAY STIFFORDS BRIDGE-STIFFORDS BRIDGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 0.5745 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 3082.234 | 5
206 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-POLYURETHANE-(0,70]-BRECON_/_PORTIS-PORTIS-PORTIS LOW-LLANDEW LINE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 0.14504 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 15260.9132 | 5
207 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 6.2282 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 497.5396 | 3
208 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-ALWEN_/_DEE-DENBIGH_ALWEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 8.1172 | 5.5336 | 2.5 | 121.3% | +/- 50% | OVER | 681.7082 | 4
209 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-ALWEN_/_DEE-DENBIGH_ALWEN-ALWEN TO BWLCH GAP | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 2.9132 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 531.8526 | 4
210 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-ALWEN_/_DEE-DENBIGH_ALWEN-BYLCHAU HIGH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 4.5143 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 637.4031 | 4
211 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-BALA-BALA-COED TALOG OUTLET-PANT SAER OUTLETS NEW DMA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 0.90111 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 2456.3299 | 5
212 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 4.8863 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 498.2891 | 3
213 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-LLEYNHARLECH-BANGOR__CAERNARFON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 0.84518 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 2095.1046 | 5
214 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 3.6751 | 5.3122 | 2.5 | 112.5% | +/- 50% | OVER | 1445.4707 | 5
215 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-CWMYSTRADLLYN GAP-CENIN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 0.7125 | 4.2055 | 2.5 | 68.22% | +/- 50% | OVER | 5902.4448 | 5
216 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-NORTH_ERYRI_/_YNYS_MON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 5.9678 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 407.9831 | 3
217 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-DEINIOLEN CEFN COCH-ASHTON HOUSE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 0.65502 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 4392.9363 | 5
218 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-PENTIR BRYNREFAIL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 0.84082 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 1842.7329 | 5
219 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-NORTH_ERYRI_/_YNYS_MON-SOUTH_ANGLESEY_CWELLYN__MYNYDD-PENMYNYDD CADNANT GAERWEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 0.69039 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 2564.8303 | 5
220 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-SOUTH_MEIRIONNYDD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 3.4271 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 516.6819 | 4
221 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 25.9641 | 4.6482 | 2.5 | 85.93% | +/- 50% | OVER | 179.0244 | 2
222 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(120,160]-ALWEN_/_DEE-DENBIGH_ALWEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 14.396 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 169.1284 | 2
223 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(120,160]-BALA-BALA-ARENIG TRUNK MAINS-LLANERCH ARENIG NEW DMA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 5.6694 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 351.3731 | 3
224 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(120,160]-BALA-BALA-COED TALOG OUTLET-COED TALOG OUTLET NEW DMA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 2.5251 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 1314.8417 | 5
225 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(120,160]-CLWYD_COASTAL-ABERGELE__RHYL_GLASCOED-RHUALLT TO BODFARI-0702TREMEIRCHION/BODFARI (R70) | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 2.8584 | 6.1976 | 2.5 | 147.9% | +/- 50% | OVER | 2168.2312 | 5
226 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(120,160]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 6.7118 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 230.8461 | 2
227 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(120,160]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-SYCHNANT-MAENHIR PENGROESLON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 1.6524 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 937.6497 | 4
228 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(120,160]-TYWYN_/_ABERDYFI-BRYNCRUG-ESCUAN ABERDYFI TRUNK-AREA FED BY S/SUPPLY 3H900394 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 4.5654 | 5.3122 | 2.5 | 112.5% | +/- 50% | OVER | 1163.5831 | 5
229 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 19.9056 | 4.2055 | 2.5 | 68.22% | +/- 50% | OVER | 211.273 | 2
230 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 7.7878 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 227.3738 | 2
231 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 25.4566 | 7.3043 | 2.5 | 192.2% | +/- 50% | OVER | 286.9325 | 3
232 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-ACCRE OUTLET-ACCRE/LLANDEGLA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 4.3715 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 405.0651 | 3
233 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-CARROG-TYN CEFN TRAFFICLIGHTS. | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 5.9052 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 487.2735 | 3
234 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-CORWEN GAP-BETTWS GG O/TLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 1.3161 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 1681.81 | 5
235 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-CORWEN GAP-BETWS GG TYRPEG | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 1.0661 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 2491.4625 | 5
236 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-LLANGWYFAN-WAEN ABERWHEELER GEINAS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 2.5309 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 699.6594 | 4
237 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-UWCH Y DRE CYNWYD-LLANDRILLO | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 5.2739 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 335.7562 | 3
238 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-BALA-BALA-COED TALOG OUTLET-COED TALOG OUTLET NEW DMA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 3.6343 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 609.0355 | 4
239 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-BALA-BALA-RHYD UCHAF OUTLET-LLWYN IOLYN OUTLET NEW DMA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 5.1114 | 5.9763 | 2.5 | 139.1% | +/- 50% | OVER | 1169.2081 | 5
240 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-CLWYD_COASTAL-ABERGELE__RHYL_GLASCOED-RHUALLT TO BODFARI-0702TREMEIRCHION/BODFARI (R70) | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 5.1457 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 473.1679 | 3
241 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-CLWYD_COASTAL-ABERGELE__RHYL_GLASCOED-ST ASAPH 10 GAP | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 17.3176 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 166.1578 | 2
242 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 18.1773 | 6.8616 | 2.5 | 174.5% | +/- 50% | OVER | 377.4826 | 3
243 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-BETWS-Y-COED-BETWS Y COED / DOLWYDDELAN VILLAGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 1.8476 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 958.3924 | 4
244 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-BRYNIAU (CONWY)-BRYNIAU RES OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 10.2625 | 3.5415 | 2.5 | 41.66% | +/- 50% | PASS | 345.091 | 3
245 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-CERRIG-RHYDLYDAN PENTREFOELAS SRV O/L | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 4.5385 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 341.3877 | 3
246 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT & GORSWEN MINOR-LLANDDOGED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 0.87424 | 3.7628 | 2.5 | 50.51% | +/- 50% | OVER | 4304.1014 | 5
247 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT AND GORSWEN GAP-BODRACH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 4.6094 | 11.2885 | 2.5 | 351.5% | +/- 50% | OVER | 2448.9891 | 5
248 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT AND GORSWEN GAP-MAENAN INLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 3.6985 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 897.7116 | 4
249 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT VALLEY GAP-EGLWYSBACH TALYCAFN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 2.4545 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 631.258 | 4
250 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT VALLEY GAP-MAENAN RISING | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 0.81406 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 3806.5874 | 5
251 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT VALLEY TRUNK-AREA FED BY S/SUPPLY 3SC20M18 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 1.0697 | 4.4269 | 2.5 | 77.07% | +/- 50% | OVER | 4138.5613 | 5
252 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-LLANFAIRFECHAN-LLANFAIRFECHAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 5.0201 | 4.2055 | 2.5 | 68.22% | +/- 50% | OVER | 837.7269 | 4
253 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-LLYN CONWY TRUNK-PENMACHNO/LLYN CONWY SILOAM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 3.1168 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 497.1085 | 3
254 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-PEN TO LLANFAIRFECHAN TRUNK-AREA FED BY S/SUPPLY 30C30A07 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 0.42211 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 4719.3881 | 5
255 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-LLEYNHARLECH-BANGOR__CAERNARFON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 2.3254 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 761.4652 | 4
256 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 12.6457 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 157.5308 | 2
257 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-COED Y FRON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 6.5822 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 269.0214 | 3
258 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-CWMYSTRADLLYN GAP-CENIN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 1.6539 | 3.5415 | 2.5 | 41.66% | +/- 50% | PASS | 2141.2289 | 5
259 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-PENRHYNDEUDRAETH-PENRHYD LLANFROTHEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 0.23856 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 10205.9932 | 5
260 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 13.472 | 3.9842 | 2.5 | 59.37% | +/- 50% | OVER | 295.7381 | 3
261 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-PENTIR BRYNREFAIL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 4.2656 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 415.1185 | 3
262 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-WAUNFAWR-WAUNFAWR NEW | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 0.36525 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 8484.0953 | 5
263 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 10.2107 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 173.4199 | 2
264 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-HOLLAND ARMS 9INCH-LLYS LEW TO LLANDDANIEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 1.6983 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 1433.6795 | 5
265 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-SOUTH_ANGLESEY_CWELLYN__MYNYDD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 4.5919 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 385.6267 | 3
266 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-SOUTH_ANGLESEY_CWELLYN__MYNYDD-CADNANT BEAUMARIS-LLANDEGFAN BOOSTER | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 2.0143 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 988.9845 | 4
267 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-SOUTH_MEIRIONNYDD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 4.8665 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 591.2806 | 4
268 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-SOUTH_MEIRIONNYDD-DINAS_MAWDDWY-DINAS MAWDDWY-MALLWYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 2.7764 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 637.7829 | 4
269 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-SOUTH_MEIRIONNYDD-DOLGELLAU_PEN_Y_CEFN-DOLGELLAU | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 1.6716 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 1324.0987 | 5
270 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-SOUTH_MEIRIONNYDD-DOLGELLAU_PEN_Y_CEFN-FAIRBOURNE-FAIRBOURNE FRIOG | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 3.8366 | 6.1976 | 2.5 | 147.9% | +/- 50% | OVER | 1615.3768 | 5
271 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-SOUTH_MEIRIONNYDD-DOLGELLAU_PEN_Y_CEFN-PENYCEFN GAP-BRITHDIR VILLAGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 0.73185 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 2721.9719 | 5
272 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-SOUTH_MEIRIONNYDD-DOLGELLAU_PEN_Y_CEFN-PENYCEFN GAP-PENCEFN ROAD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 0.41137 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 3766.4094 | 5
273 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-SOUTH_MEIRIONNYDD-DOLGELLAU_PEN_Y_CEFN-PENYCEFN GAP-PENMAENPOOL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 0.54572 | 4.2055 | 2.5 | 68.22% | +/- 50% | OVER | 7706.3579 | 5
274 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-SOUTH_MEIRIONNYDD-PENNAL__CORRIS_SEVERN_TRENT-CORRIS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 7.3288 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 453.0237 | 3
275 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-SOUTH_MEIRIONNYDD-PENNAL__CORRIS_SEVERN_TRENT-CORRIS TALGARTH TRUNK-PLASTALGARTH RES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 0.8293 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 2402.1206 | 5
276 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm |  | 15.2255 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 116.3012 | 1
277 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-CEMENT_MORTAR-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 5.0757 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 392.4747 | 3
278 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 15.4357 | 10.1818 | 2.5 | 307.3% | +/- 50% | OVER | 659.6248 | 4
279 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-BEULAU TO ABERBANC-BLAENGWENLLAN CROSS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 6.9358 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 478.6972 | 3
280 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-EGLWYSWRW-BRYNBERIAN WD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 2.1834 | 5.3122 | 2.5 | 112.5% | +/- 50% | OVER | 2432.9572 | 5
281 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-FFYNNON LLAWDDOG-BEULAH TO CWMCOU | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 1.0176 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 2392.7441 | 5
282 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-HAFOD LLECHRYD-LECHRYD VILLIAGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 1.9164 | 4.6482 | 2.5 | 85.93% | +/- 50% | OVER | 2425.5116 | 5
283 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-MYNYDD CROGWY TO EGLWYSWRW AND CRYMYCH-POST GWYN BONCATH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 3.7736 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 762.5192 | 4
284 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-MYNYDD CROGWY TO EGLWYSWRW AND CRYMYCH-POSTGWYN CRYMYCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 0.88567 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 3498.8277 | 5
285 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-MYNYDD CROGWY TO EGLWYSWRW AND CRYMYCH-STAR PUMPS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 4.7385 | 5.7549 | 2.5 | 130.2% | +/- 50% | OVER | 1214.499 | 5
286 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-NEWQUAY-SYNOD INN 4 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 2.377 | 5.5336 | 2.5 | 121.3% | +/- 50% | OVER | 2327.9167 | 5
287 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-PENTREGAT CROSS CONNECTION-BRYNHOFFNANT RHYDLEWIS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 4.8751 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 317.8212 | 3
288 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-RHOSHILL TO CROSSROADS-PENYBRYN TO CARDIGAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 1.7856 | 5.3122 | 2.5 | 112.5% | +/- 50% | OVER | 2975.1104 | 5
289 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-RHOSHILL TO CROSSROADS-PENYBRYN TO CILGERRAN WD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 0.96657 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 3205.9612 | 5
290 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-RHOSYMRYSON TO PENRHYWLLAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 5.4299 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 448.4022 | 3
291 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-RHOSYMRYSON TO PENRHYWLLAN-HOREB TO FFOSTRASOL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 2.015 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 988.6146 | 4
292 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SARNAU CROSS CONNECTION-BEULAH SCHEME | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 4.563 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 727.6227 | 4
293 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SARNAU CROSS CONNECTION-GOGERDDAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 2.5399 | 3.5415 | 2.5 | 41.66% | +/- 50% | PASS | 1394.367 | 5
294 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SYNOD INN LLANARTH-LLANARTH TO ABERAERON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 1.8191 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 851.7596 | 4
295 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SYNOD INN SR TO RHOSYMRYSON SR-CROESGWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 1.2196 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 1270.3725 | 5
296 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SYNOD INN SR TO RHOSYMRYSON SR-GRESFFORDD MOUNT BRANCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 2.4366 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 817.5819 | 4
297 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 5.5226 | 3.5415 | 2.5 | 41.66% | +/- 50% | PASS | 641.2737 | 4
298 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-DERI GOCH PS TO RHOSYMRYSON SR-CAPEL Y GROES TO LLANWNEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 1.0864 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 1426.2433 | 5
299 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-PONTRHYDFENDIGAID-PONTRHYDFENDIGAID NORTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 0.86401 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 2305.6398 | 5
300 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 7.3259 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 271.9222 | 3
301 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 22.0138 | 5.9763 | 2.5 | 139.1% | +/- 50% | OVER | 271.4775 | 3
302 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-BOLTON_HILL-QUARRY LINE-QUARRY LINE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 1.1318 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 1760.0464 | 5
303 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-BOLTON_HILL-TESCO SOUTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 2.1042 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 841.5165 | 4
304 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-BOLTON_HILL-TTM OFF PENT PUMPS-DEVON DRIVE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 2.0497 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 1079.892 | 5
305 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-PENDINE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 1.0571 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 1465.7602 | 5
306 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-PENDINE-BRANDY HILL TO ST. CLEARS-PWLL TRAPP | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 0.93087 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 3566.6917 | 5
307 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-PENDINE-BRANDY HILL TO ST. CLEARS-THE SMITHY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 1.4686 | 5.7549 | 2.5 | 130.2% | +/- 50% | OVER | 3918.6108 | 5
308 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-PRESELI_SUPPLY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 7.6815 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 201.706 | 2
309 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-PRESELI_SUPPLY-LETTERSTON-LLANGLOFFAN CROSS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 2.4834 | 3.7628 | 2.5 | 50.51% | +/- 50% | OVER | 1515.2143 | 5
310 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-PRESELI_SUPPLY-PENYGARN TO HOTWELLS-PENYGARN/AMBLESTON 3 INCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 1.3525 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 1472.9285 | 5
311 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-PRESELI_SUPPLY-PRESELI USL OUTLETS-WISTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 4.7299 | 5.3122 | 2.5 | 112.5% | +/- 50% | OVER | 1123.1114 | 5
312 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-PRESELI_SUPPLY-TENBY MAIN-PICTON/RHOS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 4.3868 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 756.8435 | 4
313 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 4.6609 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 427.4072 | 3
314 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-BRYNGWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 4.401 | 3.9842 | 2.5 | 59.37% | +/- 50% | OVER | 905.2943 | 4
315 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-BRYNGWYN-SALEM SR OUTLET-SALEM LLANFYNYDD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 1.0648 | 6.4189 | 2.5 | 156.8% | +/- 50% | OVER | 6028.1478 | 5
316 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-BRYNGWYN-SALEM SR OUTLET-SALEM VILLAGE METER | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 3.3562 | 11.2885 | 2.5 | 351.5% | +/- 50% | OVER | 3363.5009 | 5
317 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-BRYNGWYN-TRAPP BULK EXPORT-CARMARTHEN RD. LLANDEILO RD. | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 0.25877 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 11975.2808 | 5
318 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-BRYNGWYN-TRAPP BULK EXPORT-PENYBANK/NANTGARDEIG 6 INCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 0.5771 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 4986.0489 | 5
319 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-CAERAU__YSTRADFELLTE-RESOLVEN SR OUTLET-GLYN CASTLE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 0.48646 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 5460.0524 | 5
320 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 2.7111 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 816.4427 | 4
321 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-CEFN BRYN HOUSE-CEFN BRYN HOUSE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 0.65943 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 3356.5986 | 5
322 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-MID_-_SOUTH_CEREDIGION-LLECHRYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 9.1075 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 340.2485 | 3
323 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-MID_-_SOUTH_CEREDIGION-LLECHRYD-EGLWYSWRW-POST GWYN - EGLWYSWRW | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 4.4953 | 4.2055 | 2.5 | 68.22% | +/- 50% | OVER | 935.5289 | 4
324 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SYNOD INN LLANARTH-LLANARTH TO ABERAERON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 0.80227 | 3.9842 | 2.5 | 59.37% | +/- 50% | OVER | 4966.1365 | 5
325 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SYNOD INN LLANARTH-LLANARTH VILLAGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 0.34019 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 6506.4868 | 5
326 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-MID_-_SOUTH_CEREDIGION-LLECHRYD-WAUNLLWYD TO GORLLWYN -CAPEL IWAN TO CENARTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 1.3745 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 1771.3974 | 5
327 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 7.2639 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 426.6007 | 3
328 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-DERI GOCH PS TO RHOSYMRYSON SR-FFYNON RHYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 5.5141 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 441.5523 | 3
329 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 19.8948 | 3.5415 | 2.5 | 41.66% | +/- 50% | PASS | 178.0107 | 2
330 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-PEMBROKESHIRE-BOLTON_HILL-ROSEPOOL-FOXHILL RES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 0.78737 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 1967.8161 | 5
331 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 13.0866 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 118.3955 | 1
332 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-BRYNGWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 7.2026 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 307.3079 | 3
333 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-BRYNGWYN-BRYNCOCH - PENTWYN-FOLLAND ROAD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 2.488 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 622.7401 | 4
334 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 8.1666 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 325.2404 | 3
335 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 5.2894 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 460.3154 | 3
336 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE-CLASE SR OUTLET TO GWYROSEDD-LLANGYFELACH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 0.52356 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 3382.126 | 5
337 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(160,320]-MID_-_SOUTH_CEREDIGION | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (160,320] | 12.3368 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 125.5922 | 2
338 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(160,320]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SYNOD INN SR TO RHOSYMRYSON SR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (160,320] | 6.4782 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 375.8384 | 3
339 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(160,320]-PEMBROKESHIRE-BOLTON_HILL-ORIELTON TO WOGASTON-ORIELTON WOGASTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (160,320] | 3.0463 | 8.8537 | 2.5 | 254.1% | +/- 50% | OVER | 2906.3447 | 5
340 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(160,320]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (160,320] | 24.7813 | 3.7628 | 2.5 | 50.51% | +/- 50% | OVER | 151.8413 | 2
341 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 49.4402 | 9.7391 | 2.5 | 289.6% | +/- 50% | OVER | 196.9872 | 2
342 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-BEULAU TO ABERBANC-BLAENGWENLLAN CROSS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 4.4493 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 348.2335 | 3
343 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-CARDIGAN SR OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 2.2792 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 874.0322 | 4
344 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-EGLWYSWRW-BRYNBERIAN WD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 6.6829 | 4.6482 | 2.5 | 85.93% | +/- 50% | OVER | 695.5389 | 4
345 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-GORLLWYN HERMON AND TANGLWYST-GORLLWYN TO HERMON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 4.6167 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 575.33 | 4
346 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-GORLLWYN RHOS TREALAU-GORLLWYN TO RHOS/TREALAU | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 2.6571 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 916.31 | 4
347 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-GORLLWYN RHOS TREALAU-TREALAU RES OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 8.8023 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 377.1896 | 3
348 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-HAFOD LLECHRYD-LLANDYGWYDD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 4.1336 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 803.2068 | 4
349 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-MYNYDD CROGWY TO EGLWYSWRW AND CRYMYCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 7.1176 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 279.8831 | 3
350 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-MYNYDD CROGWY TO EGLWYSWRW AND CRYMYCH-WAUNYDD TEGRYN WD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 5.8435 | 3.5415 | 2.5 | 41.66% | +/- 50% | PASS | 606.0506 | 4
351 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-NEWQUAY-SYNOD INN TO NEW QUAY 6 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 2.6072 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 1018.7787 | 5
352 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-RHOSHILL TO CROSSROADS-RHOSHILL CROSSROADS WD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 3.3337 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 464.7746 | 3
353 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-RHOSYMRYSON TO PENRHYWLLAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 7.6639 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 202.1675 | 2
354 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-RHOSYMRYSON TO PENRHYWLLAN-HOREB BANGOR TEIFI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 4.1171 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 430.0925 | 3
355 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-RHOSYMRYSON TO PENRHYWLLAN-HOREB TO FFOSTRASOL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 7.6949 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 201.3538 | 2
356 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-RHOSYMRYSON TO PENRHYWLLAN-PENRHIWLLAN SCHEME | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 1.2826 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 2416.1152 | 5
357 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SARNAU CROSS CONNECTION-BEULAH SCHEME | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 5.5356 | 8.411 | 2.5 | 236.4% | +/- 50% | OVER | 1519.4514 | 5
358 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SYNOD INN LLANARTH-LLANARTH TO ABERAERON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 2.248 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 787.6896 | 4
359 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SYNOD INN SR TO RHOSYMRYSON SR-CROESGWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 13.0218 | 6.4189 | 2.5 | 156.8% | +/- 50% | OVER | 492.9369 | 3
360 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SYNOD INN SR TO RHOSYMRYSON SR-GRESFFORDD MOUNT BRANCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 4.6187 | 4.2055 | 2.5 | 68.22% | +/- 50% | OVER | 910.5335 | 4
361 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SYNOD INN SR TO RHOSYMRYSON SR-TALGERREG PISGAH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 1.333 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 1328.3794 | 5
362 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-WAUNLLWYD TO GORLLWYN -CAPEL IWAN TO CENARTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 18.6134 | 5.7549 | 2.5 | 130.2% | +/- 50% | OVER | 309.1815 | 3
363 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 20.8369 | 7.5257 | 2.5 | 201% | +/- 50% | OVER | 361.1705 | 3
364 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-BETHANIA TO CROSS INN-CROSSINN TO LLANON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 9.2424 | 6.8616 | 2.5 | 174.5% | +/- 50% | OVER | 742.4058 | 4
365 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-BETHANIA TO CROSS INN-CROSSINN TO LLANRHYSTUD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 5.3651 | 3.7628 | 2.5 | 50.51% | +/- 50% | OVER | 701.3477 | 4
366 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-BETTWS LLANGYBI AND LLANDDEWI BREFI-LANGYBI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 1.7786 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 995.5806 | 4
367 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-DERI GOCH PS TO RHOSYMRYSON SR-CAPEL Y GROES TO LLANWNEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 6.3604 | 4.2055 | 2.5 | 68.22% | +/- 50% | OVER | 661.2062 | 4
368 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-DERI GOCH PS TO RHOSYMRYSON SR-CWRTNEWYDD CWRT FARM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 4.095 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 540.5169 | 4
369 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-DERI GOCH PS TO RHOSYMRYSON SR-CWRTNEWYDD QUARRY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 7.0326 | 3.9842 | 2.5 | 59.37% | +/- 50% | OVER | 566.5254 | 4
370 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-DERIGOCH TO ABERAERON-DERI GOCH TO ABERAERON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 2.3651 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 1029.4778 | 5
371 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-MAESTIR TO BRYNGARREG-BRYNCARREG RES OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 0.37557 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 5304.2001 | 5
372 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-MAESTIR TO BRYNGARREG-MAESTIR TO BRYNGARREG | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 4.9561 | 4.8695 | 2.5 | 94.78% | +/- 50% | OVER | 982.5265 | 4
373 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-PENWCH SERVICE RES OUTLET-MAESBEIDIOG TO LLANGWYRYFON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 0.59785 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 3702.2863 | 5
374 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-PENWCH SERVICE RES OUTLET-PENUWCH TO BWLCHLLAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 0.43483 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 3563.1939 | 5
375 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-PONTRHYDFENDIGAID-PONTRHYDFENDIGAID LLANAFAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 5.0669 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 480.5282 | 3
376 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-TREGARON TOWN-LLANIO ROAD TO LLANGEITHO | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 2.5404 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 1045.5514 | 5
377 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-NORTH_CEREDIGION-ABERYSTWYTH_BONTGOCH__LOVESGROVE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 4.8806 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 362.8129 | 3
378 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 21.2153 | 4.2055 | 2.5 | 68.22% | +/- 50% | OVER | 198.2298 | 2
379 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH-FRONGOCH SR OUT-FRONGOCH TO CLARACH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 2.6207 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 591.2144 | 4
380 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH-MAESNEWYDD TO TRE’RDDOL -MAESNEWYDD TO GLANDYFI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 4.06 | 4.4269 | 2.5 | 77.07% | +/- 50% | OVER | 1090.3682 | 5
381 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 60.8503 | 8.411 | 2.5 | 236.4% | +/- 50% | OVER | 138.2248 | 2
382 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL-ADMIRALTY SITE-ADMIRALTY SITE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 3.8853 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 683.6243 | 4
383 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL-TEMPLETON TO TAVERNSPITE-LLANTEG OFF T/SPITE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 0.524 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 4224.0656 | 5
384 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PRESELI_SUPPLY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 21.2774 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 72.8189 | 1
385 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PRESELI_SUPPLY-PENYGARN TO HOTWELLS-PENYGARN/AMBLESTON 3 INCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 5.5288 | 3.7628 | 2.5 | 50.51% | +/- 50% | OVER | 680.5855 | 4
386 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PRESELI_SUPPLY-PRESELI DOLWEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 6.2263 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 248.8462 | 2
387 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PRESELI_SUPPLY-PRESELI USL OUTLETS-WISTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 11.9922 | 3.9842 | 2.5 | 59.37% | +/- 50% | OVER | 332.2289 | 3
388 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 16.4508 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 121.0932 | 1
389 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 14.2112 | 6.8616 | 2.5 | 174.5% | +/- 50% | OVER | 482.8322 | 3
390 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-BETTWS-BUTCHERS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 1.5358 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 1441.1839 | 5
391 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-BETTWS-SCOTCH PINES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 0.63905 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 2424.539 | 5
392 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-CARMEL AND PENTREGWENLAIS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 5.2919 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 376.4405 | 3
393 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-MAESTWYNOG-CYNGHORDY OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 10.3974 | 20.8062 | 2.5 | 732.2% | +/- 50% | OVER | 2001.1007 | 5
394 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-MAESTWYNOG-PANTYBRYN CILYCWM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 0.8953 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 3708.3945 | 5
395 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-SALEM SR OUTLET-SALEM LLANFYNYDD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 9.9712 | 4.8695 | 2.5 | 94.78% | +/- 50% | OVER | 488.3614 | 3
396 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-SALEM SR OUTLET-SALEM VILLAGE METER | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 27.0711 | 18.1501 | 2.5 | 626% | +/- 50% | OVER | 670.46 | 4
397 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-TRAPP BULK EXPORT-CWM ISAF TO BETHLEHEM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 4.7513 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 698.7927 | 4
398 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-TRAPP BULK EXPORT-PENYBANC RHOSMAEN LLANDILO | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 5.3818 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 534.6643 | 4
399 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-TRAPP BULK EXPORT-PENYBANK/NANTGARDEIG 6 INCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 5.7406 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 308.4593 | 3
400 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-TRAPP BULK EXPORT-TRAPP 4 INCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 2.3534 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 1128.6139 | 5
401 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-TWYNLLANAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 15.1152 | 4.2055 | 2.5 | 68.22% | +/- 50% | OVER | 278.2308 | 3
402 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-TWYNLLANAN-MOUNTPLEASANT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 1.7758 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 1495.7223 | 5
403 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAPEL_DEWI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 3.5917 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 924.3808 | 4
404 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAPEL_DEWI-FOEL SR TO RHYDARGAEAU-PENIEL BRONWYDD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 2.1343 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 725.9432 | 4
405 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CRAY__CLYDACH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 6.3517 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 418.174 | 3
406 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CRAY__CLYDACH-GURNOS CROSS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 1.9484 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 1136.037 | 5
407 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-LLANELLI_FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 5.2692 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 294.049 | 3
408 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 19.6374 | 5.3122 | 2.5 | 112.5% | +/- 50% | OVER | 270.5157 | 3
409 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-CEFN BRYN HOUSE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 6.2703 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 388.2996 | 3
410 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-CEFN BRYN HOUSE-BURRY GREEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 7.3366 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 211.1885 | 2
411 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-CEFN BRYN HOUSE-KENNEXESTONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 2.2098 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 801.3168 | 4
412 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-CEFN BRYN HOUSE-LLANGENNITH WD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 4.6615 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 332.3841 | 3
413 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKEWEN__LLANDARCY_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 8.1282 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 190.6199 | 2
414 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm |  | 20.7141 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 74.7994 | 1
415 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm |  | 4.3762 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 354.0516 | 3
416 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(120,160]-PONTSTICILL_LOW_LEVEL-CAERPHILLY-MORNINGTON MEADOWS-MORNINGTON MEADOW | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 0.52768 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 3355.7317 | 5
417 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 3.9888 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 388.4339 | 3
418 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 11.5865 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 210.1378 | 2
419 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_EAST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 5.9495 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 260.4244 | 3
420 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-EASTERN-NONE-(0,70]-WHITBOURNE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 2.6991 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 574.0352 | 4
421 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 7.6225 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 319.4191 | 3
422 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-EASTERN-NONE-(70,120]-WHITBOURNE-WHITBOURNE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 11.038 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 200.5272 | 2
423 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 6.4393 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 274.9911 | 3
424 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(0,70]-ALWEN_/_DEE-DENBIGH_ALWEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 2.013 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 989.6024 | 4
425 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(0,70]-ALWEN_/_DEE-DENBIGH_ALWEN-LLANFWROG-1511 LLANFWROG(G50) | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 3.1549 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 841.8891 | 4
426 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(0,70]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 2.8846 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 844.0705 | 4
427 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(0,70]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-CERRIG-POINT D TO CERRIG | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 0.75421 | 5.7549 | 2.5 | 130.2% | +/- 50% | OVER | 7630.3853 | 5
428 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(0,70]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT & GORSWEN MINOR-LLANDDOGED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 3.3292 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 930.8051 | 4
429 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 2.1655 | 3.5415 | 2.5 | 41.66% | +/- 50% | PASS | 1635.3805 | 5
430 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-LLANNOR SAETHON TRUNK-AREA FED BY S/SUPPLY 3A401608 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 1.2388 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 1965.452 | 5
431 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-MYNYTHO WILLIS-SAETHON BACH MYNYTHO PUMPED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 0.67435 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 2954.0812 | 5
432 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-SYCHNANT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 1.6357 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 947.2408 | 4
433 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(120,160]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 10.7619 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 308.509 | 3
434 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 11.9747 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 240.2944 | 2
435 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-ALWEN TO BWLCH TRUNK-CRICOR SUPPLY FROM ALWEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 2.4038 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 644.5659 | 4
436 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-MEIFOD-CYFFYLLIOG | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 4.389 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 554.7392 | 4
437 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON-RHOSESMOR MOEL Y CREO-BABELL TO CAERWYS(RHOS) | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 6.889 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 224.909 | 2
438 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 8.3517 | 4.6482 | 2.5 | 85.93% | +/- 50% | OVER | 556.5549 | 4
439 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT & GORSWEN MINOR-LLANDDOGED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 2.0766 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 1065.9039 | 5
440 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-LLYN CONWY TRUNK-AREA FED BY S/SUPPLY 3SC70B08 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 0.7372 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 2702.2439 | 5
441 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 12.4928 | 3.5415 | 2.5 | 41.66% | +/- 50% | PASS | 283.4831 | 3
442 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-CRICCIETH LLANYSTUMDWY-GAERDDU BACH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 2.7469 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 564.0497 | 4
443 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-MAENLLWYD-MAENLLWYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 1.7608 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 879.9496 | 4
444 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-SYCHNANT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 4.5657 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 339.3557 | 3
445 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-SYCHNANT-MAEN HIR BRYNCROES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 5.5027 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 482.6953 | 3
446 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm |  | 17.0554 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 142.7566 | 2
447 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-BEULAU TO ABERBANC-BLAENGWENLLAN CROSS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 2.1062 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 840.7483 | 4
448 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 19.435 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 148.0556 | 2
449 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-BOLTON_HILL-BRAWDY TO FELINWYNT-BRAWDY FELINWYNT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 8.212 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 377.3509 | 3
450 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-BOLTON_HILL-PLUMSTONE TO BRAWDY-DRUIDSTON CROSS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 3.9411 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 561.6325 | 4
451 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-PRESELI_SUPPLY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 3.9705 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 445.9715 | 3
452 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-PRESELI_SUPPLY-CROESFORDD OUTLET-CROESFORDD 4 INCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 1.0068 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 1538.9112 | 5
453 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-PRESELI_SUPPLY-HOTWELLS TO LETTERSTON-CO/OP LETTERSTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 5.4127 | 5.0909 | 2.5 | 103.6% | +/- 50% | OVER | 940.5511 | 4
454 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(120,160]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 6.5979 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 234.8326 | 2
455 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 4.4696 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 346.6554 | 3
456 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(160,320] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (160,320] | 9.1414 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 169.492 | 2
457 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 9.1606 | 3.5415 | 2.5 | 41.66% | +/- 50% | PASS | 386.5991 | 3
458 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 35.1541 | 3.9842 | 2.5 | 59.37% | +/- 50% | OVER | 113.3345 | 1
459 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL-PLUMSTONE TO BRAWDY-DRUIDSTON CROSS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 4.6737 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 473.5946 | 3
460 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PRESELI_SUPPLY-CROESFORDD OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 6.3562 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 313.4073 | 3
461 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PRESELI_SUPPLY-CROESFORDD OUTLET-BRYN DERI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 5.3659 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 288.7468 | 3
462 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PRESELI_SUPPLY-HOTWELLS TO LETTERSTON-CO/OP LETTERSTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 2.9991 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 738.0322 | 4
463 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 5.5303 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 400.2365 | 3
464 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm |  | 42.8351 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 56.8406 | 1
465 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm |  | 5.9516 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 334.7156 | 3
466 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-PENARTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 1.4053 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 1260.0037 | 5
467 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(160,320] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (160,320] | 9.867 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 179.4604 | 2
468 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-CYNON-PENDERYN__PONTSTICILL-RHIGOS VILLAGE 8IN & 10IN OUTLETS-RHIGOS VILLAGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 2.4999 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 973.9494 | 4
469 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-VALE_OF_GLAM__RHONDDA_VALLEYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 6.6847 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 231.7823 | 2
470 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 12.0951 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 146.402 | 2
471 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF-PENTREBANE NORTH-PENTREBANE NORTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 0.2747 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 5640.4063 | 5
472 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH__BARRY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 3.165 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 699.3514 | 4
473 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm |  | 25.8013 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 77.2087 | 1
474 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 8.6199 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 282.4605 | 3
475 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 17.9495 | 3.9842 | 2.5 | 59.37% | +/- 50% | OVER | 221.9661 | 2
476 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(120,160]-WHITBOURNE-WHITBOURNE-LEYSTERS 8INCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 3.1606 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 700.3108 | 4
477 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(160,320]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM-PENHOW QUARRY TDMA-PENHOW QUARRY TO HIGHMOOR HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (160,320] | 3.8971 | 3.9842 | 2.5 | 59.37% | +/- 50% | OVER | 1022.3418 | 5
478 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(160,320]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN-BETTWS EAST-BETTWS EAST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (160,320] | 1.7217 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 1928.3665 | 5
479 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 31.9332 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 55.4514 | 1
480 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-PILLETH-PILLETH_KNIGHTON__BLEDDFA-WHITTON BEGGARS BUSH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 5.6352 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 392.7845 | 3
481 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-PILLETH-PILLETH_KNIGHTON__BLEDDFA-WHITTON BEGGARS BUSH-MAESTREYLOW TO NORTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 0.84929 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 2084.9713 | 5
482 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 5.3294 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 456.8574 | 3
483 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-CROSS ASH-THE BOOT NEWCASTLE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 0.28281 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 9391.9137 | 5
484 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-WHITBOURNE-UPPER_SAPEY-LEYSTER SR 3" OUTLET GAP-THE FOX(SEVERN TRENT) | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 1.0203 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 3037.1692 | 5
485 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-WHITBOURNE-WHITBOURNE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 21.9832 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 100.6875 | 1
486 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-WHITBOURNE-WHITBOURNE-LEYSTERS 8INCH-POLE FARM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 5.1526 | 3.5415 | 2.5 | 41.66% | +/- 50% | PASS | 687.3257 | 4
487 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-WHITBOURNE-WHITBOURNE-WARRENWOOD-HOLLY TREE METER | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 2.8672 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 1157.98 | 5
488 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-CEMENT_MORTAR-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-BANGOR FROM BRYNIAU-PENRHOS ROAD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 0.8752 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 1770.3374 | 5
489 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 3.8801 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 513.4058 | 4
490 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(0,70]-ALWEN_/_DEE-DENBIGH_ALWEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 3.0928 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 572.5432 | 4
491 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(0,70]-ALWEN_/_DEE-DENBIGH_ALWEN-BYLCHAU HIGH-1008 BWLCHOUTLET(LLANNEFYDD) ( | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 1.2837 | 3.5415 | 2.5 | 41.66% | +/- 50% | PASS | 2758.8174 | 5
492 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(0,70]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 0.58756 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 3013.7165 | 5
493 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 4.7184 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 422.196 | 3
494 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-BEUDY MAWR-BEUDY MAWR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 1.1418 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 2132.3727 | 5
495 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-GARNFADRYN-GARNFADRYN RES OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 1.695 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 1175.2613 | 5
496 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-SAETHON GAP-CAPEL TYDDYN PUMPED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 1.8714 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 1064.4819 | 5
497 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(0,70]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-RHOSGADFAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 0.17869 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 8670.9028 | 5
498 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(0,70]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-WAENHIR-PENTIR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 0.20736 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 7471.9384 | 5
499 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 17.8249 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 86.9235 | 1
500 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(120,160]-ALWEN_/_DEE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 12.9304 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 171.1796 | 2
501 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(120,160]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 6.105 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 326.305 | 3
502 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(120,160]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-CERRIG-CERRIGYDRUDION SRV O/LET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 4.8866 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 407.6643 | 3
503 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(120,160]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-BUTLINS-LLANGYBI - BODOWEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 2.8464 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 1010.9265 | 5
504 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(120,160]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-DOLBENMAEN WEST TRUNK -AREA FED BY S/SUPPLY 3A401601 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 2.7145 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 570.7843 | 4
505 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(120,160]-NORTH_ERYRI_/_YNYS_MON-EAST_ANGLESEY_CEFNI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 5.6395 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 392.4838 | 3
506 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(120,160]-NORTH_ERYRI_/_YNYS_MON-EAST_ANGLESEY_CEFNI-TREFOR BLAS LLANDDONA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 7.7808 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 256.0257 | 3
507 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(120,160]-SOUTH_MEIRIONNYDD-DOLGELLAU_PEN_Y_CEFN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 2.4835 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 623.8862 | 4
508 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(160,320]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-CERRIG-POINT D TO CERRIG | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (160,320] | 3.1411 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 916.0781 | 4
509 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(160,320]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-LLYN CONWY TRUNK-AREA FED BY S/SUPPLY 3SC70B08 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (160,320] | 9.4852 | 6.4189 | 2.5 | 156.8% | +/- 50% | OVER | 676.7333 | 4
510 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 26.1909 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 109.8646 | 1
511 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-CARROG-TY CERRIG 6 INCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 4.2704 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 466.484 | 3
512 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 15.11 | 3.9842 | 2.5 | 59.37% | +/- 50% | OVER | 263.6772 | 3
513 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 10.3059 | 5.5336 | 2.5 | 121.3% | +/- 50% | OVER | 536.9343 | 4
514 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-CERRIG | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 5.5255 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 560.8154 | 4
515 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-TREFRIW-TREFRIW SERVICE RES. O/LET. | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 0.17521 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 8843.0359 | 5
516 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 1.4579 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 1062.7862 | 5
517 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 12.4874 | 3.9842 | 2.5 | 59.37% | +/- 50% | OVER | 319.0565 | 3
518 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-COED Y FRON-BODWI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 2.3042 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 864.5273 | 4
519 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-LLANAELHAEARN AND TRALLWYN-TRALLWYN RES OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 2.5272 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 700.6679 | 4
520 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-MAENLLWYD-MAENLLWYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 4.3518 | 4.4269 | 2.5 | 77.07% | +/- 50% | OVER | 1017.2558 | 5
521 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-MOEL Y PENMAEN-MOEL PENMAEN RES OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 2.7443 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 645.2391 | 4
522 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-PENMORFA-PENMORFA RES OUTLET-PRENTEG | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 3.8275 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 404.8083 | 3
523 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-PENRHYNDEUDRAETH-PENRHYD LLANFROTHEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 0.23962 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 7389.8561 | 5
524 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-SYCHNANT-MAEN HIR BRYNCROES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 2.0864 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 1379.1286 | 5
525 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-SYCHNANT-RHOSHIRWAEN HALL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 10.9472 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 303.2879 | 3
526 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-SYCHNANT-RHYDLIOS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 7.2904 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 212.5265 | 2
527 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 16.2236 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 177.3623 | 2
528 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 9.4603 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 257.3668 | 3
529 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-Y FELINHELI-BUSH RES Y FELINHELI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 1.1638 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 1901.9409 | 5
530 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-BRYN GWENALLT-BRYNGWENALLT TO LLANDDEUSANT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 1.8271 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 1211.4455 | 5
531 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm |  | 31.4827 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 70.3061 | 1
532 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 11.3475 | 3.9842 | 2.5 | 59.37% | +/- 50% | OVER | 351.1061 | 3
533 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-LLANWNEN TO LLANLLWNI-LLANYBYTHER RES OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 0.39386 | 4.6482 | 2.5 | 85.93% | +/- 50% | OVER | 11801.6539 | 5
534 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-PONTRHYDFENDIGAID-FFAIR RHOS YSBYTY YSTWYTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 1.9243 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 805.1905 | 4
535 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-BRYNGWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 0.66632 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 2989.6891 | 5
536 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-BRYNGWYN-BETTWS-MAESQUERRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 0.56229 | 4.8695 | 2.5 | 94.78% | +/- 50% | OVER | 8660.1696 | 5
537 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-BRYNGWYN-TRAPP BULK EXPORT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 1.6498 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 1475.7913 | 5
538 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-BRYNGWYN-TWYNLLANAN-BRYNGLAS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 0.37396 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 5327.022 | 5
539 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-MID_-_SOUTH_CEREDIGION-LLECHRYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 10.2277 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 173.1314 | 2
540 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-MID_-_SOUTH_CEREDIGION-LLECHRYD-PENPARC SR TO CARDIGAN SR-PENPARC SOUTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 1.9395 | 3.9842 | 2.5 | 59.37% | +/- 50% | OVER | 2054.1802 | 5
541 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH-CAPEL SEION LLANRHYSTUD-ABERMAD TO LLANRHYSTUD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 4.1751 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 424.1171 | 3
542 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH-CAPEL SEION LLANRHYSTUD-CAPEL SEION/LLANRHYSTUD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 2.8445 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 544.6934 | 4
543 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH-PENYCWM-PENYCWM CAPEL SEION RES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 2.6017 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 935.828 | 4
544 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 16.4983 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 93.9129 | 1
545 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-BRYNGWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 4.7251 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 374.7536 | 3
546 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-DAFEN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 3.0644 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 505.6124 | 4
547 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 15.6569 | 3.9842 | 2.5 | 59.37% | +/- 50% | OVER | 254.467 | 3
548 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-DERLWYN-DERLWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 0.95812 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 1617.1296 | 5
549 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SKEWEN__LLANDARCY_FELINDRE__CRAY-TYDRAW ROAD-MAES YR HAF | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 1.0702 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 1861.4704 | 5
550 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 4.9067 | 3.5415 | 2.5 | 41.66% | +/- 50% | PASS | 721.7655 | 4
551 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE-MYNYDD NEWYDD TO FFOREST FACH-IVORITES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 0.2168 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 7146.8371 | 5
552 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(160,320]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY-SOUTHERNDOWN-OGMORE BY SEA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (160,320] | 0.96763 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 1829.9774 | 5
553 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(160,320]-TYWI_C.U._AREA-BRYNGWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (160,320] | 1.1116 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 1393.8638 | 5
554 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 6.1094 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 362.2998 | 3
555 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-PONTRHYDFENDIGAID-FFAIR RHOS YSBYTY YSTWYTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 1.5759 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 1825.8725 | 5
556 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 7.7967 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 227.1137 | 2
557 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH-CAPEL SEION LLANFI AND TRAWSCOED-CAPEL SEION LLANFIHANGEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 9.4923 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 209.8643 | 2
558 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 2.5565 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 606.0696 | 4
559 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PENDINE-THREE LORDS OUTLET-THREE LORDS (BROADWAY/LAUGHARN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 0.32191 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 5500.7108 | 5
560 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 11.7898 | 5.0909 | 2.5 | 103.6% | +/- 50% | OVER | 431.8057 | 3
561 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 7.0228 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 409.7318 | 3
562 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CRAY__CLYDACH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 10.9566 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 282.825 | 3
563 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CRAY__CLYDACH-CLYDACH AREA ALT-YNYSTAWE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 1.4882 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 1487.367 | 5
564 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 39.7727 | 5.5336 | 2.5 | 121.3% | +/- 50% | OVER | 139.1298 | 2
565 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-NEWTON P.O.-CAMBRIDGE WD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 3.0906 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 572.9489 | 4
566 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKEWEN__LLANDARCY_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 5.3162 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 582.8925 | 4
567 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 18.7665 | 3.5415 | 2.5 | 41.66% | +/- 50% | PASS | 188.7128 | 2
568 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm |  | 36.2423 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 42.7511 | 1
569 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 2.7935 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 633.8844 | 4
570 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-VALE_OF_GLAM__RHONDDA_VALLEYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 6.6235 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 434.4307 | 3
571 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-EASTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm |  | 16.8962 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 91.7009 | 1
572 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(0,70]-TALYBONT-ABERGAVENNY__CWMTILLERY-PONTYPOOL TDMA-AREA FED BY SUB SUPPLY SYSTEM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (0,70] | 0.91095 | 4.2055 | 2.5 | 68.22% | +/- 50% | OVER | 4616.6183 | 5
573 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 8.4464 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 288.2611 | 3
574 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (0,70] | 4.0392 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 767.1819 | 4
575 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(0,70]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (0,70] | 7.6249 | 4.6482 | 2.5 | 85.93% | +/- 50% | OVER | 609.607 | 4
576 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (0,70] | 2.2789 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 679.9037 | 4
577 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(0,70]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (0,70] | 1.8393 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 1444.1064 | 5
578 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(0,70]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (0,70] | 0.89996 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 1967.5818 | 5
579 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(0,70]-SOUTH_MEIRIONNYDD-DOLGELLAU_PEN_Y_CEFN-PENYCEFN TRUNK-GANLLWYN RES INLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (0,70] | 0.32803 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 4723.2955 | 5
580 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 6.8078 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 325.1314 | 3
581 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160]-ALWEN_/_DEE-DENBIGH_ALWEN-DENBIGH TRUNK-1402 LLANGWYFAN(G40) | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 1.8709 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 1537.9938 | 5
582 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160]-ALWEN_/_DEE-FLINT__CONNAHS_QUAY_BRETTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 19.1169 | 3.7628 | 2.5 | 50.51% | +/- 50% | OVER | 196.8329 | 2
583 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 47.8008 | 7.747 | 2.5 | 209.9% | +/- 50% | OVER | 162.0684 | 2
584 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON-BUCKLEY LIVERPOOL ROAD-EWLOE/HAWARDEN. | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 3.3099 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 668.7333 | 4
585 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON-HOLYWELL ST PHILOMENIA-ST.PHILOMENIAHOLYWELL. | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 0.59805 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 2590.7349 | 5
586 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON-PEN Y BALL TO GWESPYR & AXTON TRUNK-AREA FED BY S/SUPPLY 3SF8100 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 7.328 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 241.642 | 2
587 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON-WHITFORD SR TO MOSTYN DOCKS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 3.1987 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 484.3825 | 3
588 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 8.7767 | 4.2055 | 2.5 | 68.22% | +/- 50% | OVER | 479.1697 | 3
589 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-FLINT__CONNAHS_QUAY_BRETTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 25.9864 | 6.1976 | 2.5 | 147.9% | +/- 50% | OVER | 238.4942 | 2
590 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 93.3489 | 15.494 | 2.5 | 519.8% | +/- 50% | OVER | 165.9795 | 2
591 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON-BUCKLEY BROOKE STREET-BROOKEST.BUCKLEY. | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 3.0739 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 576.0625 | 4
592 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON-BUCKLEY PRECINCT WAY-PRECINCT WAYBUCKLEY. | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 4.9969 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 398.6644 | 3
593 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON-RHOSESMOR BERTH DDU | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 3.726 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 415.8398 | 3
594 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 4.4817 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 493.8789 | 3
595 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 5.6022 | 4.6482 | 2.5 | 85.93% | +/- 50% | OVER | 829.7036 | 4
596 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 7.1095 | 4.6482 | 2.5 | 85.93% | +/- 50% | OVER | 653.8019 | 4
597 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-FFYNNON WEN-GROESLON VILLAGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 0.81518 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 1900.6879 | 5
598 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm |  | 16.2434 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 122.6398 | 1
599 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (0,70] | 0.18787 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 8247.0154 | 5
600 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 19.1257 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 162.0225 | 2
601 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 19.4519 | 3.9842 | 2.5 | 59.37% | +/- 50% | OVER | 204.8216 | 2
602 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CRAY__CLYDACH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 8.9634 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 370.4124 | 3
603 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 11.4182 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 232.6202 | 2
604 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-DRUIDS STONE-DRUID'S STONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 0.41905 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 4225.5891 | 5
605 | DIAM_LT_320-AC-<=320mm-B14_1980 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN | AC |  |  | DIAM_LT_320 | <=320mm |  | 14.3958 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 107.6283 | 1
606 | DIAM_LT_320-AC-<=320mm-B14_1980-1961_1980-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-HAFOD FELINWYNT-HAFOD FELINWYNT 5 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B14_1980 | DIAM_LT_320 | <=320mm | (70,120] | 0.15081 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 14677.0597 | 5
607 | DIAM_LT_320-AC-<=320mm-B14_1980-1981_2000-EASTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | AC | 1981_2000 | B14_1980 | DIAM_LT_320 | <=320mm |  | 1.7123 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 1034.1276 | 5
608 | DIAM_LT_320-AC-<=320mm-B14_1980-1981_2000-NORTHERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | AC | 1981_2000 | B14_1980 | DIAM_LT_320 | <=320mm |  | 8.2412 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 241.7238 | 2
609 | DIAM_LT_320-AC-<=320mm-B14_1980-1981_2000-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1981_2000 | B14_1980 | DIAM_LT_320 | <=320mm | (70,120] | 2.247 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 886.5399 | 4
610 | DIAM_LT_320-ALKATHENE-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | ALKATHENE | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 1.628 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 1087.691 | 5
611 | DIAM_LT_320-ALKATHENE-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(0,70]-PONTSTICILL_LOW_LEVEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | ALKATHENE | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 1.8519 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 956.1997 | 4
612 | DIAM_LT_320-ALKATHENE-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | ALKATHENE | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 10.0147 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 221.0175 | 2
613 | DIAM_LT_320-ALKATHENE-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(0,70]-BRECON_/_PORTIS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | ALKATHENE | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 2.3933 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 739.8712 | 4
614 | DIAM_LT_320-ALKATHENE-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | ALKATHENE | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 8.5448 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 181.3276 | 2
615 | DIAM_LT_320-ALKATHENE-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | ALKATHENE | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 5.5747 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 357.343 | 3
616 | DIAM_LT_320-ALKATHENE-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | ALKATHENE | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 22.8675 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 106.4728 | 1
617 | DIAM_LT_320-ALKATHENE-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | ALKATHENE | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 21.4541 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 113.4874 | 1
618 | DIAM_LT_320-ALKATHENE-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-BRYNGWYN-LLANNON WEST-PONT MORLAIS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | ALKATHENE | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 2.6164 | 4.4269 | 2.5 | 77.07% | +/- 50% | OVER | 1691.9859 | 5
619 | DIAM_LT_320-ALKATHENE-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-LLANELLI_FELINDRE-POLIN TO RHYDARGAEAU-NANTGAREDIG BRIDGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | ALKATHENE | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 1.4401 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 2151.8061 | 5
620 | DIAM_LT_320-ALKATHENE-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-LLANELLI_FELINDRE-REHOBOTH RED DMA-REHOBOTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | ALKATHENE | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 1.0196 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 2388.067 | 5
621 | DIAM_LT_320-ALKATHENE-<=320mm-B12_1960-1941_1960 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | ALKATHENE | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm |  | 8.3767 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 184.9645 | 2
622 | DIAM_LT_320-ALKATHENE-<=320mm-B12_1960-1941_1960-EASTERN-NONE-(0,70]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_SW__RISCA__ABERCARN-MICHAELSTONE TO MARSHFIELD SOUTH-MICHAELSTONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | ALKATHENE | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 0.43602 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 3553.5344 | 5
623 | DIAM_LT_320-ALKATHENE-<=320mm-B12_1960-1961_1980 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | ALKATHENE | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm |  | 6.489 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 238.7748 | 2
624 | DIAM_LT_320-ALKATHENE-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(0,70]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | ALKATHENE | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 2.5052 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 883.5162 | 4
625 | DIAM_LT_320-ALKATHENE-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(0,70]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_EAST-BRYN CELYN-BRYN CELYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | ALKATHENE | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 0.03781 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 40978.149 | 5
626 | DIAM_LT_320-ALKATHENE-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | ALKATHENE | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 8.6837 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 229.4051 | 2
627 | DIAM_LT_320-ALKATHENE-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | ALKATHENE | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 10.611 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 229.4578 | 2
628 | DIAM_LT_320-ALKATHENE-<=320mm-B13_1970-1961_1980 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | ALKATHENE | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (0,70] | 7.7481 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 285.6744 | 3
629 | DIAM_LT_320-ALKATHENE-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | ALKATHENE | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (0,70] | 7.2912 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 212.5025 | 2
630 | DIAM_LT_320-ALKATHENE-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-PORTHMADOG WEST-TYDDYN LLWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | ALKATHENE | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (0,70] | 0.25081 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 7942.6177 | 5
631 | DIAM_LT_320-ALKATHENE-<=320mm-B14_1980 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN | ALKATHENE |  |  | DIAM_LT_320 | <=320mm |  | 8.712 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 279.4731 | 3
632 | DIAM_LT_320-COPPER-<=320mm | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY | COPPER |  |  | DIAM_LT_320 | <=320mm | (0,70] | 12.851 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 120.5665 | 1
633 | DIAM_LT_320-FERROUS_1-<=320mm | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY | FERROUS_1 |  |  | DIAM_LT_320 | <=320mm |  | 108.5588 | 7.3043 | 2.5 | 192.2% | +/- 50% | OVER | 67.2844 | 1
634 | DIAM_LT_320-FERROUS_1-<=320mm-B01_1850-PRE_1880-NORTHERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_1 | PRE_1880 | B01_1850 | DIAM_LT_320 | <=320mm |  | 6.3191 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 315.2474 | 3
635 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_1 | PRE_1880 | B02_1860 | DIAM_LT_320 | <=320mm |  | 50.5648 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 43.7741 | 1
636 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-CEMENT_MORTAR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | PRE_1880 | B02_1860 | DIAM_LT_320 | <=320mm |  | 6.471 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 239.4368 | 2
637 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-EPOXY_RESIN-(120,160]-PEMBROKESHIRE-BOLTON_HILL-MOUNTAIN TREFFGARNE AND RUDBAXTON-MOUNTAIN WATER | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | PRE_1880 | B02_1860 | DIAM_LT_320 | <=320mm | (120,160] | 7.503 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 206.5044 | 2
638 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-EPOXY_RESIN-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | PRE_1880 | B02_1860 | DIAM_LT_320 | <=320mm | (70,120] | 5.445 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 365.8533 | 3
639 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | PRE_1880 | B02_1860 | DIAM_LT_320 | <=320mm | (70,120] | 21.0209 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 157.9451 | 2
640 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY-SOUTHERNDOWN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | PRE_1880 | B02_1860 | DIAM_LT_320 | <=320mm | (70,120] | 5.823 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 266.0823 | 3
641 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA-BRYNGWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | PRE_1880 | B02_1860 | DIAM_LT_320 | <=320mm | (70,120] | 19.6227 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 90.2395 | 1
642 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | PRE_1880 | B02_1860 | DIAM_LT_320 | <=320mm | (0,70] | 4.4448 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 348.5873 | 3
643 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | PRE_1880 | B02_1860 | DIAM_LT_320 | <=320mm | (120,160] | 50.1718 | 4.2055 | 2.5 | 68.22% | +/- 50% | OVER | 83.8222 | 1
644 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | PRE_1880 | B02_1860 | DIAM_LT_320 | <=320mm | (120,160] | 3.9657 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 390.6999 | 3
645 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(160,320] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | PRE_1880 | B02_1860 | DIAM_LT_320 | <=320mm | (160,320] | 37.4145 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 53.2436 | 1
646 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(160,320]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | PRE_1880 | B02_1860 | DIAM_LT_320 | <=320mm | (160,320] | 9.7443 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 249.8672 | 2
647 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | PRE_1880 | B02_1860 | DIAM_LT_320 | <=320mm | (70,120] | 10.7059 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 206.748 | 2
648 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-PENCOED__BRIDGEND_VALLEYS-BRIDGEND ROAD-LLANHARRY ROAD 7IN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | PRE_1880 | B02_1860 | DIAM_LT_320 | <=320mm | (70,120] | 1.4002 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 1106.5241 | 5
649 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | PRE_1880 | B02_1860 | DIAM_LT_320 | <=320mm | (70,120] | 28.2314 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 109.7641 | 1
650 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | PRE_1880 | B02_1860 | DIAM_LT_320 | <=320mm | (70,120] | 4.7119 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 375.8052 | 3
651 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-BETTWS-BUTCHERS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | PRE_1880 | B02_1860 | DIAM_LT_320 | <=320mm | (70,120] | 1.021 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 1734.2968 | 5
652 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAERAU__YSTRADFELLTE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | PRE_1880 | B02_1860 | DIAM_LT_320 | <=320mm | (70,120] | 10.0027 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 309.7961 | 3
653 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CRAY__CLYDACH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | PRE_1880 | B02_1860 | DIAM_LT_320 | <=320mm | (70,120] | 6.0554 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 292.4254 | 3
654 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-DAFEN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | PRE_1880 | B02_1860 | DIAM_LT_320 | <=320mm | (70,120] | 5.9861 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 258.831 | 3
655 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-LLANELLI_FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | PRE_1880 | B02_1860 | DIAM_LT_320 | <=320mm | (70,120] | 14.3069 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 123.7684 | 1
656 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-LLANELLI_FELINDRE-FURNACE ROAD TO KIDWELLY RED DMA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | PRE_1880 | B02_1860 | DIAM_LT_320 | <=320mm | (70,120] | 4.058 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 490.9022 | 3
657 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PENCOED__BRIDGEND_VALLEYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | PRE_1880 | B02_1860 | DIAM_LT_320 | <=320mm | (70,120] | 23.1132 | 4.4269 | 2.5 | 77.07% | +/- 50% | OVER | 191.5294 | 2
658 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PENCOED__BRIDGEND_VALLEYS-RED COW TO NANT ST EAST ALT-REVLON OAKWOOD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | PRE_1880 | B02_1860 | DIAM_LT_320 | <=320mm | (70,120] | 0.55881 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 2772.667 | 5
659 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PORT_TALBOT_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | PRE_1880 | B02_1860 | DIAM_LT_320 | <=320mm | (70,120] | 14.2791 | 3.5415 | 2.5 | 41.66% | +/- 50% | PASS | 248.0193 | 2
660 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-POLYURETHANE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | PRE_1880 | B02_1860 | DIAM_LT_320 | <=320mm |  | 12.7871 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 155.789 | 2
661 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-POLYURETHANE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | PRE_1880 | B02_1860 | DIAM_LT_320 | <=320mm | (70,120] | 11.6155 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 209.6137 | 2
662 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-POLYURETHANE-(70,120]-TYWI_C.U._AREA-BRYNGWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | PRE_1880 | B02_1860 | DIAM_LT_320 | <=320mm | (70,120] | 8.263 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 321.4453 | 3
663 | DIAM_LT_320-FERROUS_1-<=320mm-B03_1870-PRE_1880 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | FERROUS_1 | PRE_1880 | B03_1870 | DIAM_LT_320 | <=320mm |  | 17.6455 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 100.3512 | 1
664 | DIAM_LT_320-FERROUS_1-<=320mm-B03_1870-PRE_1880-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | PRE_1880 | B03_1870 | DIAM_LT_320 | <=320mm |  | 15.0976 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 131.9473 | 2
665 | DIAM_LT_320-FERROUS_1-<=320mm-B04_1880 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN | FERROUS_1 |  |  | DIAM_LT_320 | <=320mm |  | 13.0934 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 118.3347 | 1
666 | DIAM_LT_320-FERROUS_1-<=320mm-B04_1880-1881_1900-CENTRAL-EPOXY_RESIN-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1881_1900 | B04_1880 | DIAM_LT_320 | <=320mm | (70,120] | 1.6079 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 963.6213 | 4
667 | DIAM_LT_320-FERROUS_1-<=320mm-B04_1880-1881_1900-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | 1881_1900 | B04_1880 | DIAM_LT_320 | <=320mm |  | 13.7605 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 144.7679 | 2
668 | DIAM_LT_320-FERROUS_1-<=320mm-B04_1880-1881_1900-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__CANTON__CATHAYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1881_1900 | B04_1880 | DIAM_LT_320 | <=320mm | (70,120] | 2.6068 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 679.2841 | 4
669 | DIAM_LT_320-FERROUS_1-<=320mm-B04_1880-1881_1900-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__RUMNEY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1881_1900 | B04_1880 | DIAM_LT_320 | <=320mm | (70,120] | 10.3938 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 212.956 | 2
670 | DIAM_LT_320-FERROUS_1-<=320mm-B04_1880-1881_1900-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1881_1900 | B04_1880 | DIAM_LT_320 | <=320mm | (120,160] | 3.2653 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 474.5042 | 3
671 | DIAM_LT_320-FERROUS_1-<=320mm-B04_1880-PRE_1880-NORTHERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_1 | PRE_1880 | B04_1880 | DIAM_LT_320 | <=320mm |  | 5.2029 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 425.4228 | 3
672 | DIAM_LT_320-FERROUS_1-<=320mm-B04_1880-PRE_1880-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | PRE_1880 | B04_1880 | DIAM_LT_320 | <=320mm |  | 9.8239 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 157.717 | 2
673 | DIAM_LT_320-FERROUS_1-<=320mm-B04_1880-PRE_1880-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE-HAFOD-HAFOD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | PRE_1880 | B04_1880 | DIAM_LT_320 | <=320mm | (70,120] | 2.3989 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 738.1424 | 4
674 | DIAM_LT_320-FERROUS_1-<=320mm-B05_1890-1881_1900 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | FERROUS_1 | 1881_1900 | B05_1890 | DIAM_LT_320 | <=320mm |  | 33.7739 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 52.4294 | 1
675 | DIAM_LT_320-FERROUS_1-<=320mm-B05_1890-1881_1900-CENTRAL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_1 | 1881_1900 | B05_1890 | DIAM_LT_320 | <=320mm |  | 28.6525 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 69.5257 | 1
676 | DIAM_LT_320-FERROUS_1-<=320mm-B05_1890-1881_1900-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1881_1900 | B05_1890 | DIAM_LT_320 | <=320mm | (120,160] | 9.6966 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 273.9233 | 3
677 | DIAM_LT_320-FERROUS_1-<=320mm-B05_1890-1881_1900-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1881_1900 | B05_1890 | DIAM_LT_320 | <=320mm | (70,120] | 10.4827 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 168.9206 | 2
678 | DIAM_LT_320-FERROUS_1-<=320mm-B05_1890-1881_1900-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__RUMNEY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1881_1900 | B05_1890 | DIAM_LT_320 | <=320mm | (70,120] | 9.1146 | 3.7628 | 2.5 | 50.51% | +/- 50% | OVER | 412.8353 | 3
679 | DIAM_LT_320-FERROUS_1-<=320mm-B05_1890-1881_1900-CENTRAL-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1881_1900 | B05_1890 | DIAM_LT_320 | <=320mm | (70,120] | 8.3356 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 212.4305 | 2
680 | DIAM_LT_320-FERROUS_1-<=320mm-B05_1890-1881_1900-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1881_1900 | B05_1890 | DIAM_LT_320 | <=320mm | (120,160] | 5.6537 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 391.5028 | 3
681 | DIAM_LT_320-FERROUS_1-<=320mm-B05_1890-1881_1900-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1881_1900 | B05_1890 | DIAM_LT_320 | <=320mm | (70,120] | 10.597 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 167.0987 | 2
682 | DIAM_LT_320-FERROUS_1-<=320mm-B05_1890-1881_1900-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_WEST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1881_1900 | B05_1890 | DIAM_LT_320 | <=320mm | (70,120] | 6.4704 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 376.2919 | 3
683 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | FERROUS_1 | 1881_1900 | B06_1900 | DIAM_LT_320 | <=320mm |  | 16.0002 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 110.67 | 1
684 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | 1881_1900 | B06_1900 | DIAM_LT_320 | <=320mm |  | 19.1624 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 103.958 | 1
685 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-CENTRAL-NONE-(70,120]-RHONDDA-MAERDY__PORTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1881_1900 | B06_1900 | DIAM_LT_320 | <=320mm | (70,120] | 16.5057 | 6.1976 | 2.5 | 147.9% | +/- 50% | OVER | 375.4824 | 3
686 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-CENTRAL-NONE-(70,120]-RHONDDA-MAERDY__PORTH-FURNACE ROAD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1881_1900 | B06_1900 | DIAM_LT_320 | <=320mm | (70,120] | 4.9533 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 402.1748 | 3
687 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1881_1900 | B06_1900 | DIAM_LT_320 | <=320mm | (70,120] | 4.6454 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 381.1827 | 3
688 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__CANTON__CATHAYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1881_1900 | B06_1900 | DIAM_LT_320 | <=320mm | (70,120] | 4.4141 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 601.7406 | 4
689 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-CENTRAL-POLYURETHANE-(70,120]-RHONDDA-VALE_OF_GLAM__RHONDDA_VALLEYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1881_1900 | B06_1900 | DIAM_LT_320 | <=320mm | (70,120] | 7.4013 | 3.7628 | 2.5 | 50.51% | +/- 50% | OVER | 508.4033 | 4
690 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-NORTHERN-CEMENT_MORTAR-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1881_1900 | B06_1900 | DIAM_LT_320 | <=320mm | (70,120] | 10.8136 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 204.6893 | 2
691 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-NORTHERN-CEMENT_MORTAR-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1881_1900 | B06_1900 | DIAM_LT_320 | <=320mm | (70,120] | 10.1305 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 262.191 | 3
692 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-NORTHERN-CEMENT_MORTAR-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-CAERNARFON SEGONTIWM-PRINCE OF WALES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1881_1900 | B06_1900 | DIAM_LT_320 | <=320mm | (70,120] | 2.5731 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 774.1837 | 4
693 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-NORTHERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | 1881_1900 | B06_1900 | DIAM_LT_320 | <=320mm |  | 25.4922 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 86.8275 | 1
694 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1881_1900 | B06_1900 | DIAM_LT_320 | <=320mm | (70,120] | 6.4626 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 274.0003 | 3
695 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_1 | 1881_1900 | B06_1900 | DIAM_LT_320 | <=320mm |  | 42.7242 | 4.8695 | 2.5 | 94.78% | +/- 50% | OVER | 113.9761 | 1
696 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-CEMENT_MORTAR-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1881_1900 | B06_1900 | DIAM_LT_320 | <=320mm | (120,160] | 2.5752 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 687.6184 | 4
697 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-EPOXY_RESIN-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1881_1900 | B06_1900 | DIAM_LT_320 | <=320mm | (70,120] | 6.1027 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 362.6962 | 3
698 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-EPOXY_RESIN-(70,120]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1881_1900 | B06_1900 | DIAM_LT_320 | <=320mm | (70,120] | 9.5703 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 185.025 | 2
699 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1881_1900 | B06_1900 | DIAM_LT_320 | <=320mm | (70,120] | 15.0681 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 176.2739 | 2
700 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1881_1900 | B06_1900 | DIAM_LT_320 | <=320mm | (120,160] | 21.1324 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 146.6377 | 2
701 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-NONE-(160,320]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1881_1900 | B06_1900 | DIAM_LT_320 | <=320mm | (160,320] | 10.3559 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 170.9893 | 2
702 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1881_1900 | B06_1900 | DIAM_LT_320 | <=320mm | (70,120] | 11.1292 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 178.9968 | 2
703 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-NONE-(70,120]-NORTH_CEREDIGION-ABERYSTWYTH_BONTGOCH__LOVESGROVE-CHALYBEATE STREET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1881_1900 | B06_1900 | DIAM_LT_320 | <=320mm | (70,120] | 3.0035 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 589.5531 | 4
704 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL-TENBY 7 DMA-TENBY 7 WD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1881_1900 | B06_1900 | DIAM_LT_320 | <=320mm | (70,120] | 1.6621 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 932.2044 | 4
705 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1881_1900 | B06_1900 | DIAM_LT_320 | <=320mm | (70,120] | 22.1184 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 130.0931 | 2
706 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PENCOED__BRIDGEND_VALLEYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1881_1900 | B06_1900 | DIAM_LT_320 | <=320mm | (70,120] | 14.7469 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 165.104 | 2
707 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PORT_TALBOT_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1881_1900 | B06_1900 | DIAM_LT_320 | <=320mm | (70,120] | 13.5455 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 212.429 | 2
708 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-POLYURETHANE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1881_1900 | B06_1900 | DIAM_LT_320 | <=320mm | (120,160] | 10.605 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 146.1012 | 2
709 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-POLYURETHANE-(70,120]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1881_1900 | B06_1900 | DIAM_LT_320 | <=320mm | (70,120] | 12.5667 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 246.5882 | 2
710 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-POLYURETHANE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-TWYNLLANAN-MOUNTPLEASANT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1881_1900 | B06_1900 | DIAM_LT_320 | <=320mm | (70,120] | 2.7287 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 648.923 | 4
711 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-CENTRAL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_1 | 1901_1920 | B06_1900 | DIAM_LT_320 | <=320mm |  | 12.5895 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 123.0713 | 1
712 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | 1901_1920 | B06_1900 | DIAM_LT_320 | <=320mm |  | 21.7692 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 91.5094 | 1
713 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__RUMNEY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B06_1900 | DIAM_LT_320 | <=320mm | (70,120] | 6.6308 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 367.1917 | 3
714 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_WEST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B06_1900 | DIAM_LT_320 | <=320mm | (120,160] | 4.859 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 318.8725 | 3
715 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B06_1900 | DIAM_LT_320 | <=320mm | (70,120] | 16.497 | 3.7628 | 2.5 | 50.51% | +/- 50% | OVER | 228.0918 | 2
716 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_WEST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B06_1900 | DIAM_LT_320 | <=320mm | (70,120] | 10.0796 | 3.5415 | 2.5 | 41.66% | +/- 50% | PASS | 351.3519 | 3
717 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-NORTHERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_1 | 1901_1920 | B06_1900 | DIAM_LT_320 | <=320mm |  | 29.3309 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 52.8248 | 1
718 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-NORTHERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | 1901_1920 | B06_1900 | DIAM_LT_320 | <=320mm |  | 12.9114 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 188.5755 | 2
719 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_1 | 1901_1920 | B06_1900 | DIAM_LT_320 | <=320mm |  | 25.6412 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 94.9554 | 1
720 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-CEMENT_MORTAR-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B06_1900 | DIAM_LT_320 | <=320mm | (70,120] | 11.8543 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 149.375 | 2
721 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-EPOXY_RESIN-(120,160]-TYWI_C.U._AREA-CAPEL_DEWI-CARMARTHEN TOWN-CWMOERNANT - CARMS TOWN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B06_1900 | DIAM_LT_320 | <=320mm | (120,160] | 0.59725 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 2594.2108 | 5
722 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B06_1900 | DIAM_LT_320 | <=320mm | (70,120] | 20.563 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 161.4617 | 2
723 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA-BRYNGWYN-CARMEL TO LLANNON SR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1901_1920 | B06_1900 | DIAM_LT_320 | <=320mm | (70,120] | 7.6275 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 203.1342 | 2
724 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | 1901_1920 | B06_1900 | DIAM_LT_320 | <=320mm |  | 26.229 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 84.3886 | 1
725 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B06_1900 | DIAM_LT_320 | <=320mm | (120,160] | 30.9835 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 100.0146 | 1
726 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B06_1900 | DIAM_LT_320 | <=320mm | (70,120] | 39.4897 | 5.0909 | 2.5 | 103.6% | +/- 50% | OVER | 128.9168 | 2
727 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CRAY__CLYDACH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B06_1900 | DIAM_LT_320 | <=320mm | (70,120] | 6.8058 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 227.6603 | 2
728 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-LLANELLI_FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B06_1900 | DIAM_LT_320 | <=320mm | (70,120] | 16.3754 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 189.2347 | 2
729 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PENCOED__BRIDGEND_VALLEYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B06_1900 | DIAM_LT_320 | <=320mm | (70,120] | 13.5477 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 245.0709 | 2
730 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PENCOED__BRIDGEND_VALLEYS-OGMORE VALE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1901_1920 | B06_1900 | DIAM_LT_320 | <=320mm | (70,120] | 5.3355 | 3.5415 | 2.5 | 41.66% | +/- 50% | PASS | 663.7611 | 4
731 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE-WYCHTREE MORFYDD PENTREMALWED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1901_1920 | B06_1900 | DIAM_LT_320 | <=320mm | (70,120] | 4.8712 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 318.0762 | 3
732 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-POLYURETHANE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B06_1900 | DIAM_LT_320 | <=320mm | (70,120] | 20.1094 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 121.0764 | 1
733 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-EPOXY_RESIN-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (120,160] | 12.6407 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 140.0826 | 2
734 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-EPOXY_RESIN-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 5.3414 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 290.0717 | 3
735 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-EPOXY_RESIN-(70,120]-PONTSTICILL_LOW_LEVEL-RHYMNEY__BARGOED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 13.053 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 237.4019 | 2
736 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-EPOXY_RESIN-(70,120]-RHONDDA-TYNYWAUN-BAGLAN STREET TO DR THOMAS-ROCK DRIVE GELLI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 0.60898 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 2544.2469 | 5
737 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-EPOXY_RESIN-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 13.3802 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 148.883 | 2
738 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm |  | 34.1532 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 58.3279 | 1
739 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (0,70] | 7.6785 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 201.785 | 2
740 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(120,160]-PONTSTICILL_LOW_LEVEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (120,160] | 17.4317 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 165.0699 | 2
741 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(120,160]-RHONDDA-MAERDY__PORTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (120,160] | 1.872 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 827.6612 | 4
742 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (120,160] | 21.7284 | 5.5336 | 2.5 | 121.3% | +/- 50% | OVER | 254.6694 | 3
743 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-PENARTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (120,160] | 15.5337 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 199.4891 | 2
744 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(160,320]-PONTSTICILL_LOW_LEVEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (160,320] | 14.5164 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 121.9822 | 1
745 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(160,320]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (160,320] | 21.1465 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 73.2697 | 1
746 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-CYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 9.3209 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 166.2292 | 2
747 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-MERTHYR__ABERCYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 6.1398 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 324.4545 | 3
748 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RHYMNEY__BARGOED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 11.7622 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 188.1814 | 2
749 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-MAERDY__PORTH-CASTLE INN BRIDGE-MAESYCOED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 3.0378 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 510.04 | 4
750 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-MERTHYR__ABERCYNON-PENTREBACH-PENTREBACH/TROEDYRHIW | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 2.661 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 582.2618 | 4
751 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-RHYMNEY__BARGOED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 18.8361 | 4.6482 | 2.5 | 85.93% | +/- 50% | OVER | 246.7704 | 2
752 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-RHYMNEY__BARGOED-MAESYCWMMER-FLEUR DE LYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 3.3755 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 655.7401 | 4
753 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-VALE_OF_GLAM__RHONDDA_VALLEYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 26.1105 | 4.4269 | 2.5 | 77.07% | +/- 50% | OVER | 169.5431 | 2
754 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-RHONDDA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 9.8463 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 269.7572 | 3
755 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-RHONDDA-MAERDY__PORTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 20.6435 | 6.8616 | 2.5 | 174.5% | +/- 50% | OVER | 332.3873 | 3
756 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-RHONDDA-TYNYWAUN-BAGLAN STREET TO DR THOMAS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 1.6698 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 927.8889 | 4
757 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 9.2444 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 215.4912 | 2
758 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__CANTON__CATHAYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 4.8271 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 366.8361 | 3
759 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__RUMNEY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 12.9905 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 238.5441 | 2
760 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__RUMNEY-PLASNEWYDD ROAD PRV-SUPPLY SUB-SYSTEM BOUNDARY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 1.575 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 983.7762 | 4
761 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 14.5274 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 121.8897 | 1
762 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_HEATH_&_LLANISHEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 6.3868 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 381.2166 | 3
763 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 41.3978 | 10.4031 | 2.5 | 316.1% | +/- 50% | OVER | 251.2963 | 3
764 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-POLYURETHANE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm |  | 35.6343 | 3.5415 | 2.5 | 41.66% | +/- 50% | PASS | 99.384 | 1
765 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-POLYURETHANE-(70,120]-PONTSTICILL_LOW_LEVEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 12.8732 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 137.553 | 2
766 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-POLYURETHANE-(70,120]-PONTSTICILL_LOW_LEVEL-CAERPHILLY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 6.9329 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 351.192 | 3
767 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-POLYURETHANE-(70,120]-PONTSTICILL_LOW_LEVEL-MERTHYR__ABERCYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 5.672 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 312.1914 | 3
768 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-POLYURETHANE-(70,120]-RHONDDA-VALE_OF_GLAM__RHONDDA_VALLEYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 4.5566 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 388.6098 | 3
769 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 6.7052 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 264.0854 | 3
770 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CAERPHILLY-TY CANOL-NANTGARW OFF TYCANOL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 1.3045 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 1357.4065 | 5
771 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 4.3659 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 354.8857 | 3
772 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm |  | 15.6579 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 113.0897 | 1
773 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-EPOXY_RESIN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm |  | 29.3132 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 67.9586 | 1
774 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-EPOXY_RESIN-(120,160]-PONTSTICILL_HIGH_LEVEL/HEADS_O | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (120,160] | 5.9638 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 259.8008 | 3
775 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-EPOXY_RESIN-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RASSAU__SIRHOWY_VALLEY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 9.6167 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 322.2313 | 3
776 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-EPOXY_RESIN-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_SW__RISCA__ABERCARN-SALISBURY STREET-WEST END NEWBRIDGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 1.3219 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 1172.1241 | 5
777 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-EPOXY_RESIN-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 8.7155 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 304.7579 | 3
778 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-EPOXY_RESIN-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-TREVETHIN HILL-TREVETHIN L/LEVEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 2.7927 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 554.794 | 4
779 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-EPOXY_RESIN-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-VARTEG-VARTEG VILLAGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 6.1821 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 393.8452 | 3
780 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (0,70] | 15.3668 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 144.0397 | 2
781 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (120,160] | 11.8098 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 243.6492 | 2
782 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (120,160] | 11.3971 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 194.2104 | 2
783 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_WEST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (120,160] | 4.7656 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 325.1197 | 3
784 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(120,160]-TALYBONT-ABERGAVENNY__CWMTILLERY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (120,160] | 14.4877 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 122.2243 | 1
785 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(160,320] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (160,320] | 31.5964 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 49.0373 | 1
786 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(160,320]-TALYBONT-ABERGAVENNY__CWMTILLERY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (160,320] | 8.2861 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 320.551 | 3
787 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(70,120]-MONMOUTH-MONMOUTH_MAYHILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 3.9595 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 391.3145 | 3
788 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 16.4186 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 148.2933 | 2
789 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-EBBW_VALE__BRYNMAWR-CRAIG DDU | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 3.4101 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 519.2604 | 4
790 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-EBBW_VALE__BRYNMAWR-NANTYGLO AND FFOESMAEN-BLAINA VILLAGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 2.3668 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 654.6416 | 4
791 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 7.1243 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 217.4814 | 2
792 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 5.4353 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 285.0642 | 3
793 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_WEST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 9.7743 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 181.164 | 2
794 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 29.5629 | 5.7549 | 2.5 | 130.2% | +/- 50% | OVER | 194.6667 | 2
795 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-GRWYNE FAWR-GELLI/FELIN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 3.7344 | 4.8695 | 2.5 | 94.78% | +/- 50% | OVER | 1303.966 | 5
796 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-LLANHILLETH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 5.8133 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 380.7548 | 3
797 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-POLYURETHANE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm |  | 22.0264 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 100.4899 | 1
798 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-POLYURETHANE-(120,160]-TALYBONT-ABERGAVENNY__CWMTILLERY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (120,160] | 7.3253 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 362.593 | 3
799 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-POLYURETHANE-(160,320] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (160,320] | 11.891 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 167.529 | 2
800 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-POLYURETHANE-(160,320]-PONTSTICILL_HIGH_LEVEL/HEADS_O-EBBW_VALE__BRYNMAWR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (160,320] | 7.118 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 248.768 | 2
801 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-POLYURETHANE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 5.7727 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 268.401 | 3
802 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-POLYURETHANE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-EBBW_VALE__BRYNMAWR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 8.1362 | 3.5415 | 2.5 | 41.66% | +/- 50% | PASS | 435.2736 | 3
803 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_SW__RISCA__ABERCARN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 17.5194 | 4.8695 | 2.5 | 94.78% | +/- 50% | OVER | 277.9508 | 3
804 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-POLYURETHANE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 19.6888 | 5.0909 | 2.5 | 103.6% | +/- 50% | OVER | 258.5678 | 3
805 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-POLYURETHANE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-PONTYPOOL WEST-CWMYNYSCOY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 2.9886 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 518.4388 | 4
806 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-POLYURETHANE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-TREVETHIN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 3.1098 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 498.2294 | 3
807 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-NORTHERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm |  | 10.8721 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 183.2298 | 2
808 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-NORTHERN-CEMENT_MORTAR-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 8.8591 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 174.8929 | 2
809 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-WESTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm |  | 55.1419 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 44.1546 | 1
810 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-WESTERN-CEMENT_MORTAR-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 15.4169 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 143.5711 | 2
811 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-WESTERN-EPOXY_RESIN-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (120,160] | 11.0755 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 159.8793 | 2
812 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA-CAPEL_DEWI-EBENEZER SR OUTLETS-EBENEZER-LLANGAIN 4 INCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 1.5768 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 982.6153 | 4
813 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-WESTERN-NONE-(120,160]-PEMBROKESHIRE-PENDINE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (120,160] | 7.917 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 223.664 | 2
814 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (120,160] | 19.7873 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 111.861 | 1
815 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-WESTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 8.9554 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 222.4454 | 2
816 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PENDINE-THREE LORDS OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 9.4901 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 186.5876 | 2
817 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 35.1753 | 4.6482 | 2.5 | 85.93% | +/- 50% | OVER | 132.1439 | 2
818 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PORT_TALBOT_FELINDRE__CRAY-RODERICKS AND DYFFRYN YD-RODERICKS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (70,120] | 2.9238 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 757.0293 | 4
819 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-WESTERN-POLYURETHANE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm |  | 8.0111 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 248.6649 | 2
820 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm |  | 14.4806 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 106.9985 | 1
821 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm |  | 32.4763 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 81.7863 | 1
822 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-EPOXY_RESIN-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 7.9106 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 223.8448 | 2
823 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-EPOXY_RESIN-(70,120]-CYNON-MERTHYR__ABERCYNON-PENLOCKS 19INCH-HAWTHORN TERRACE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 0.99484 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 1557.4428 | 5
824 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-EPOXY_RESIN-(70,120]-CYNON-PENDERYN__PONTSTICILL-MOUNTAIN ASH WEST-MOUNTAIN ASH WEST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 1.7987 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 984.4779 | 4
825 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-EPOXY_RESIN-(70,120]-PONTSTICILL_LOW_LEVEL-CAERPHILLY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 4.7771 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 370.677 | 3
826 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-EPOXY_RESIN-(70,120]-PONTSTICILL_LOW_LEVEL-CAERPHILLY-BEDWAS OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 2.5776 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 686.981 | 4
827 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (120,160] | 13.3278 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 182.6838 | 2
828 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(120,160]-PONTSTICILL_HIGH_LEVEL/HEADS_O-MERTHYR__ABERCYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (120,160] | 8.4187 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 236.6269 | 2
829 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(120,160]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RHYMNEY__BARGOED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (120,160] | 15.5846 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 184.6345 | 2
830 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(120,160]-PONTSTICILL_LOW_LEVEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (120,160] | 19.6385 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 157.7917 | 2
831 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-PENARTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (120,160] | 4.8862 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 317.0962 | 3
832 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(160,320] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (160,320] | 44.4028 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 34.8942 | 1
833 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(160,320]-PONTSTICILL_HIGH_LEVEL/HEADS_O | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (160,320] | 34.6583 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 51.0914 | 1
834 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-CYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 10.4834 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 211.1366 | 2
835 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-CYNON-MERTHYR__ABERCYNON-TAFF 8INCH HIGH LEVEL-HIRWAUN 8 INCH SUPPLY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 2.0744 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 1067.0183 | 5
836 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-CYNON-MERTHYR__ABERCYNON-TAFF 8INCH HIGH LEVEL-SUB SUPPLY SYSTEM BOUNDARY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 1.2905 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 1200.6097 | 5
837 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-MERTHYR__ABERCYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 16.2995 | 4.2055 | 2.5 | 68.22% | +/- 50% | OVER | 258.0142 | 3
838 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RHYMNEY__BARGOED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 28.0022 | 5.9763 | 2.5 | 139.1% | +/- 50% | OVER | 213.4208 | 2
839 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RHYMNEY__BARGOED-BRITHDIR AND DERI-DERI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 4.6101 | 4.4269 | 2.5 | 77.07% | +/- 50% | OVER | 960.2464 | 4
840 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RHYMNEY__BARGOED-RHYMNEY CENTRAL AND NORTH-RHYMNEY CENTRAL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 2.9727 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 893.4911 | 4
841 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RHYMNEY__BARGOED-RHYMNEY SOUTH-PONTLOTTYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 3.2696 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 1015.4569 | 5
842 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 17.9941 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 123.0086 | 1
843 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-MAERDY__PORTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 5.047 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 306.9958 | 3
844 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-MERTHYR__ABERCYNON-BLACK LION | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 2.5713 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 602.5812 | 4
845 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-MERTHYR__ABERCYNON-QUAKERS YARD 24INCH-SUB SUPPLY SYSTEM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 1.2103 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 2011.7358 | 5
846 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-MERTHYR__ABERCYNON-QUAKERS YARD 24INCH-TRELEWIS - STORMTOWN (PT 4) | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 2.9251 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 605.3693 | 4
847 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-PONTYPRIDD_PONTSTICILL_HIGH-CILFYNDD SR AND TY GWYN 9IN OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 7.7379 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 343.2589 | 3
848 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-PONTYPRIDD_PONTSTICILL_HIGH-CILFYNYDD HIGH-CILFYNYDD HIGH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 3.1292 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 636.6073 | 4
849 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-RHYMNEY__BARGOED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 10.9232 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 263.4274 | 3
850 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-RHYMNEY__BARGOED-CEFN FOREST NORTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 1.1954 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 1296.1468 | 5
851 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-RHYMNEY__BARGOED-QUAKERS YARD 31INCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 4.764 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 371.6925 | 3
852 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-RHONDDA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 9.9037 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 268.1954 | 3
853 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-RHONDDA-MAERDY__PORTH-GRAIGWEN AND LANWOOD-GRAIGWEN & LANWOOD OFF R.L | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 2.4722 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 716.2507 | 4
854 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 21.4405 | 5.3122 | 2.5 | 112.5% | +/- 50% | OVER | 247.7657 | 2
855 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-POLYURETHANE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 15.403 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 201.1811 | 2
856 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-POLYURETHANE-(70,120]-CYNON-MERTHYR__ABERCYNON-ABERCYNON WEST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 3.0853 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 645.6654 | 4
857 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-POLYURETHANE-(70,120]-PONTSTICILL_LOW_LEVEL-CAERPHILLY-MAESYCWMMER-MAESYCWMMER | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 3.2232 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 480.7058 | 3
858 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-POLYURETHANE-(70,120]-PONTSTICILL_LOW_LEVEL-MERTHYR__ABERCYNON-TREHARRIS TANK-TREHARRIS TANK | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 2.965 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 597.2091 | 4
859 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-POLYURETHANE-(70,120]-PONTSTICILL_LOW_LEVEL-VALE_OF_GLAM__RHONDDA_VALLEYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 4.6097 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 384.1362 | 3
860 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-POLYURETHANE-(70,120]-RHONDDA-VALE_OF_GLAM__RHONDDA_VALLEYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 1.8106 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 855.7589 | 4
861 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-NORTHERN-CEMENT_MORTAR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm |  | 13.5213 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 163.6997 | 2
862 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-NORTHERN-CEMENT_MORTAR-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-DEINIOLEN CEFN COCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 2.3533 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 846.5074 | 4
863 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-NORTHERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm |  | 33.5288 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 66.0157 | 1
864 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 9.9685 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 244.2466 | 2
865 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 7.0287 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 220.4399 | 2
866 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-WESTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm |  | 30.5232 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 87.0195 | 1
867 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-WESTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 8.6606 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 178.9011 | 2
868 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 3.9435 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 392.9021 | 3
869 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PORT_TALBOT_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 8.8126 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 226.0504 | 2
870 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-CENTRAL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_1 | 1921_1940 | B08_1920 | DIAM_LT_320 | <=320mm |  | 15.2383 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 101.6782 | 1
871 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | 1921_1940 | B08_1920 | DIAM_LT_320 | <=320mm |  | 35.8787 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 67.8613 | 1
872 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 30.0272 | 3.5415 | 2.5 | 41.66% | +/- 50% | PASS | 117.9428 | 1
873 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-CENTRAL-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 14.1355 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 109.6106 | 1
874 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-EASTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | 1921_1940 | B08_1920 | DIAM_LT_320 | <=320mm |  | 22.6193 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 97.8557 | 1
875 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 10.1225 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 174.9319 | 2
876 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_WEST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 9.5551 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 208.4837 | 2
877 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-EASTERN-POLYURETHANE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | 1921_1940 | B08_1920 | DIAM_LT_320 | <=320mm |  | 7.2869 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 273.3782 | 3
878 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-NORTHERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_1 | 1921_1940 | B08_1920 | DIAM_LT_320 | <=320mm |  | 23.5656 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 103.3187 | 1
879 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-NORTHERN-CEMENT_MORTAR-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1921_1940 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 8.8655 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 174.7677 | 2
880 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-NORTHERN-EPOXY_RESIN-(120,160]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-LLANDUDNO MAESDU ROAD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1921_1940 | B08_1920 | DIAM_LT_320 | <=320mm | (120,160] | 0.75157 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 2061.5446 | 5
881 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1921_1940 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 7.3036 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 212.1417 | 2
882 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-WESTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_1 | 1921_1940 | B08_1920 | DIAM_LT_320 | <=320mm |  | 18.7127 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 118.2849 | 1
883 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-WESTERN-CEMENT_MORTAR-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B08_1920 | DIAM_LT_320 | <=320mm | (120,160] | 7.4964 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 236.2117 | 2
884 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-WESTERN-CEMENT_MORTAR-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 7.7075 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 258.4616 | 3
885 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-WESTERN-EPOXY_RESIN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | 1921_1940 | B08_1920 | DIAM_LT_320 | <=320mm |  | 10.4474 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 169.491 | 2
886 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-PENCOED__BRIDGEND_VALLEYS-CEFN HIRGOED TO LLANGEINOR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1921_1940 | B08_1920 | DIAM_LT_320 | <=320mm | (120,160] | 1.3802 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 1283.0012 | 5
887 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-WESTERN-NONE-(160,320]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B08_1920 | DIAM_LT_320 | <=320mm | (160,320] | 36.0808 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 49.0771 | 1
888 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 15.725 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 126.683 | 2
889 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-LLANELLI_FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B08_1920 | DIAM_LT_320 | <=320mm | (70,120] | 3.5616 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 435.0311 | 3
890 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm |  | 11.4931 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 154.0699 | 2
891 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-EPOXY_RESIN-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 11.7195 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 207.7543 | 2
892 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (120,160] | 10.2489 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 194.3699 | 2
893 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (120,160] | 16.0524 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 137.888 | 2
894 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(160,320] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (160,320] | 34.6605 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 51.0882 | 1
895 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 7.1822 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 215.7287 | 2
896 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-CYNON-ABERDARE_HIRWAUN__PONSTICILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 12.3965 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 267.8297 | 3
897 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-CYNON-MERTHYR__ABERCYNON-CWMDARE AND BRYNNAU FARM-CWMDARE LESS BRYNAU FARM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 2.4358 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 726.9641 | 4
898 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 4.6067 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 384.3839 | 3
899 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 4.0552 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 382.0807 | 3
900 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 20.2435 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 142.1426 | 2
901 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__RUMNEY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 4.5912 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 337.4709 | 3
902 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__RUMNEY-LLANRUMNEY AVENUE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 3.5991 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 615.0002 | 4
903 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 21.9722 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 141.0329 | 2
904 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 19.6493 | 4.2055 | 2.5 | 68.22% | +/- 50% | OVER | 214.0285 | 2
905 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-POLYURETHANE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (120,160] | 10.1604 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 217.8479 | 2
906 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-POLYURETHANE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 13.9102 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 222.772 | 2
907 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-POLYURETHANE-(70,120]-PONTSTICILL_LOW_LEVEL-MERTHYR__ABERCYNON-TWYNRODYN BULK-SUMMERHILL PLACE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 3.1333 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 635.7872 | 4
908 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-POLYURETHANE-(70,120]-RHONDDA-MAERDY__PORTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 2.5719 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 602.4387 | 4
909 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_HEATH_&_LLANISHEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 10.7329 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 144.3601 | 2
910 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-EASTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm |  | 34.5136 | 4.4269 | 2.5 | 77.07% | +/- 50% | OVER | 128.264 | 2
911 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-EASTERN-EPOXY_RESIN-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 17.0597 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 194.619 | 2
912 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-EASTERN-EPOXY_RESIN-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-TALYWAIN-TALYWAIN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 3.2536 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 680.3079 | 4
913 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (120,160] | 9.0342 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 196.0034 | 2
914 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 14.1309 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 109.6463 | 1
915 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 7.3204 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 302.3638 | 3
916 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN-LLANDERFEL-HENLLYS 4 INCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 2.8259 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 626.6032 | 4
917 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 11.9058 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 130.1379 | 2
918 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_WEST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 14.1971 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 155.9075 | 2
919 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(70,120]-TALYBONT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 2.5717 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 774.6089 | 4
920 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-NORTHERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm |  | 33.5636 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 98.921 | 1
921 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-NORTHERN-CEMENT_MORTAR-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 38.2678 | 4.4269 | 2.5 | 77.07% | +/- 50% | OVER | 115.681 | 1
922 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-NORTHERN-EPOXY_RESIN-(70,120]-CLWYD_COASTAL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 5.942 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 298.0067 | 3
923 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (120,160] | 20.594 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 85.9834 | 1
924 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 15.389 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 143.8321 | 2
925 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-FLINT__CONNAHS_QUAY_BRETTON-ASTON 9 INCH-ASTON FROM PLOUGHINN. | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 2.9052 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 609.5087 | 4
926 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 28.6512 | 5.9763 | 2.5 | 139.1% | +/- 50% | OVER | 208.5868 | 2
927 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 6.2294 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 355.3204 | 3
928 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 16.9348 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 169.9137 | 2
929 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-BANGOR MAESGEIRCHEN-MAESGERCHEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 3.2159 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 481.7934 | 3
930 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-WESTERN-CEMENT_MORTAR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm |  | 17.3298 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 127.7241 | 2
931 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-WESTERN-EPOXY_RESIN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm |  | 11.3094 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 137.001 | 2
932 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-WESTERN-EPOXY_RESIN-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (120,160] | 11.5507 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 172.4639 | 2
933 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-WESTERN-EPOXY_RESIN-(70,120]-MID_-_SOUTH_CEREDIGION | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 7.0944 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 218.3983 | 2
934 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY-SIGGINGSTONE 12INCH OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 2.0893 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 953.4862 | 4
935 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm |  | 28.0427 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 71.0377 | 1
936 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-WESTERN-NONE-(120,160]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (120,160] | 10.8108 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 163.7938 | 2
937 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 11.6135 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 171.5319 | 2
938 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-WESTERN-POLYURETHANE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm | (70,120] | 6.163 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 359.1453 | 3
939 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm |  | 30.3184 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 73.0062 | 1
940 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-CENTRAL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm |  | 7.6535 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 318.1244 | 3
941 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm |  | 9.1564 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 169.2155 | 2
942 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-CENTRAL-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 9.1402 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 363.2464 | 3
943 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RHYMNEY__BARGOED-RHYMNEY SOUTH-ABERTYSSWG | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 0.59805 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 4071.1603 | 5
944 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-PONTYPRIDD_PONTSTICILL_HIGH-RHYDYFELIN LOW LEVEL BULK-RHYDYFELIN L.L. BULK | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 3.9627 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 390.9972 | 3
945 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-RHYMNEY__BARGOED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 2.9924 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 517.7761 | 4
946 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-CENTRAL-NONE-(70,120]-RHONDDA-PONTYPRIDD_PONTSTICILL_HIGH-GLYNCOCH HIGH-GLYNCOCH HIGH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 5.1739 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 641.7113 | 4
947 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH__BARRY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 2.4748 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 626.075 | 4
948 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-CENTRAL-POLYURETHANE-(70,120]-PONTSTICILL_LOW_LEVEL-CAERPHILLY-GWERNAU 12INCH CAERPHILLY FLOW-CAERPHILLY NORTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 5.9064 | 3.5415 | 2.5 | 41.66% | +/- 50% | PASS | 599.6 | 4
949 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-NORTHERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm |  | 21.7808 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 71.136 | 1
950 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-NORTHERN-CEMENT_MORTAR-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 12.0852 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 274.7286 | 3
951 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 17.1167 | 3.5415 | 2.5 | 41.66% | +/- 50% | PASS | 206.9023 | 2
952 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-GOSEN TYN Y FRITH-T1 TO RHYD Y FOEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 5.3959 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 328.1653 | 3
953 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-CEMENT_MORTAR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm |  | 13.5937 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 146.5446 | 2
954 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-EPOXY_RESIN-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (120,160] | 10.8045 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 266.3205 | 3
955 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-EPOXY_RESIN-(70,120]-MID_-_SOUTH_CEREDIGION | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 7.1098 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 249.058 | 2
956 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-EPOXY_RESIN-(70,120]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 7.528 | 4.6482 | 2.5 | 85.93% | +/- 50% | OVER | 617.4586 | 4
957 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 6.6628 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 298.9865 | 3
958 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 17.6408 | 4.8695 | 2.5 | 94.78% | +/- 50% | OVER | 276.0379 | 3
959 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(120,160]-PEMBROKESHIRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (120,160] | 4.9396 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 358.4775 | 3
960 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (120,160] | 10.4759 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 169.0309 | 2
961 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (120,160] | 5.9475 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 334.9442 | 3
962 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-PEMBROKESHIRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 4.8993 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 361.4294 | 3
963 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 7.1227 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 310.7573 | 3
964 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 5.72 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 270.8729 | 3
965 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY-LLANGEWYDD-LLANGEWYDD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 3.911 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 452.7594 | 3
966 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY-NEWTON NOTTAGE-NEWTON NOTTAGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 3.1216 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 709.0786 | 4
967 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY-NOTTAGE MAIN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 4.4018 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 452.5646 | 3
968 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PENCOED__BRIDGEND_VALLEYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 14.6348 | 4.4269 | 2.5 | 77.07% | +/- 50% | OVER | 302.4892 | 3
969 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PORT_TALBOT_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 11.5872 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 248.3314 | 2
970 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PORT_TALBOT_FELINDRE__CRAY-TOLLGATE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 3.6629 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 543.856 | 4
971 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKEWEN__LLANDARCY_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 19.8573 | 4.2055 | 2.5 | 68.22% | +/- 50% | OVER | 211.7868 | 2
972 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKEWEN__LLANDARCY_FELINDRE__CRAY-MAES RHEDYN AND LODGE DRIVE-LODGE DRIVE BAGLAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 1.4943 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 1036.9023 | 5
973 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-POLYURETHANE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 4.1851 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 370.2173 | 3
974 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-POLYURETHANE-(70,120]-PEMBROKESHIRE-BOLTON_HILL-ROSEPOOL-FOXHILL RES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 1.1812 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 1499.0989 | 5
975 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-POLYURETHANE-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 8.2965 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 400.1877 | 3
976 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | FERROUS_1 | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm |  | 27.9577 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 71.2535 | 1
977 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-CENTRAL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_1 | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm |  | 9.4197 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 234.9792 | 2
978 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-CENTRAL-EPOXY_RESIN-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 2.8892 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 689.4988 | 4
979 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 11.1844 | 3.9842 | 2.5 | 59.37% | +/- 50% | OVER | 356.2246 | 3
980 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 4.4759 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 642.8833 | 4
981 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-EASTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm |  | 16.3283 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 108.4461 | 1
982 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 8.2637 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 241.0653 | 2
983 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 7.1194 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 435.2638 | 3
984 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_WEST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 7.5705 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 409.3253 | 3
985 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-NORTHERN-CEMENT_MORTAR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm |  | 17.8376 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 111.6788 | 1
986 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-NORTHERN-EPOXY_RESIN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm |  | 7.6509 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 202.5115 | 2
987 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 3.1538 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 561.4701 | 4
988 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 8.7561 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 176.951 | 2
989 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 3.0362 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 583.2126 | 4
990 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 8.5117 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 286.0493 | 3
991 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_1 | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm |  | 34.7339 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 57.3527 | 1
992 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-CEMENT_MORTAR-(70,120]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 5.5719 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 317.7963 | 3
993 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-EPOXY_RESIN-(70,120]-PEMBROKESHIRE-PRESELI_SUPPLY-PRESELI DOLWEN-EITHBED OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 7.2533 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 335.6785 | 3
994 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 19.6663 | 4.4269 | 2.5 | 77.07% | +/- 50% | OVER | 225.0984 | 2
995 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY-NEWTON NOTTAGE-NEWTON NOTTAGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 5.7028 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 426.9429 | 3
996 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm |  | 34.0653 | 3.5415 | 2.5 | 41.66% | +/- 50% | PASS | 103.9617 | 1
997 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (120,160] | 22.8833 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 106.3995 | 1
998 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL-NORCHARD BEACON SR OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 2.4506 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 632.2577 | 4
999 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL-STEPHENS GREEN SR OUTLET-JAMESTON YOUTH CLUB | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 2.9955 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 591.1366 | 4
1000 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PENDINE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 5.5558 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 278.8816 | 3
1001 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PENDINE-BRANDY HILL TO ST. CLEARS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 6.1404 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 396.5165 | 3
1002 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PENDINE-THREE LORDS OUTLET-THREE LORDS (BROADWAY/LAUGHARN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 1.8145 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 853.8795 | 4
1003 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 28.8422 | 3.7628 | 2.5 | 50.51% | +/- 50% | OVER | 130.4625 | 2
1004 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 5.2172 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 296.9786 | 3
1005 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-LLANELLI_FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 4.6882 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 519.3395 | 4
1006 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PENCOED__BRIDGEND_VALLEYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 6.8788 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 353.9552 | 3
1007 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKEWEN__LLANDARCY_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 5.7288 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 270.4566 | 3
1008 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-POLYURETHANE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 5.3936 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 369.3432 | 3
1009 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-POLYURETHANE-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 3.1503 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 632.3498 | 4
1010 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm |  | 5.7265 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 386.5214 | 3
1011 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-EPOXY_RESIN-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_HEATH_&_LLANISHEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 5.4099 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 409.1416 | 3
1012 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm |  | 20.9275 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 84.6133 | 1
1013 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 10.7075 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 144.7028 | 2
1014 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 11.5317 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 191.9437 | 2
1015 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 15.4108 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 157.9917 | 2
1016 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-CYNON-MERTHYR__ABERCYNON-PENYWAUN / CEMETERY ROAD-PENYWAUN/CEMETERY RD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 6.7936 | 3.7628 | 2.5 | 50.51% | +/- 50% | OVER | 553.8764 | 4
1017 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-MERTHYR__ABERCYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 2.2216 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 797.0489 | 4
1018 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-MERTHYR__ABERCYNON-GALON UCHAF ESTATE-GALON UCHAF ESTATE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 7.3947 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 329.2602 | 3
1019 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-MERTHYR__ABERCYNON-GUERNOS EAST-GURNOS EAST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 6.0302 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 256.9406 | 3
1020 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 6.4172 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 241.4457 | 2
1021 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-MERTHYR__ABERCYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 4.977 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 311.3139 | 3
1022 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-PONTYPRIDD_PONTSTICILL_HIGH-RHYDYFELIN LOW LEVEL BULK-RHYDYFELIN L.L. BULK | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 5.1106 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 346.4838 | 3
1023 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-VALE_OF_GLAM__RHONDDA_VALLEYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 2.9162 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 531.3002 | 4
1024 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-RHONDDA-MAERDY__PORTH-CYMMER | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 2.7997 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 553.4171 | 4
1025 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-RHONDDA-MAERDY__PORTH-MAERDY HP OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 3.8701 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 457.5389 | 3
1026 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 15.5193 | 4.6482 | 2.5 | 85.93% | +/- 50% | OVER | 299.5106 | 3
1027 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_EAST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 7.5165 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 323.9237 | 3
1028 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_EAST-LLANRUMNEY PUMPS-LLANRUMNEY PUMP | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 4.9025 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 496.6386 | 3
1029 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 8.3612 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 291.1994 | 3
1030 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF-PENTREBANE NORTH-PENTREBANE NORTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 3.6876 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 420.1642 | 3
1031 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH__BARRY-LOWER PENARTH PRV-AREA FED BY SSS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 1.263 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 1401.985 | 5
1032 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH__BARRY-REDLANDS ROAD SOUTH-REDLANDS ROAD SOUTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 2.6388 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 671.0506 | 4
1033 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-POLYURETHANE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 5.3276 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 332.3718 | 3
1034 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-POLYURETHANE-(70,120]-PONTSTICILL_LOW_LEVEL-MERTHYR__ABERCYNON-TWYNRODYN BULK-SUMMERHILL PLACE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 2.0923 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 1269.4624 | 5
1035 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-POLYURETHANE-(70,120]-PONTSTICILL_LOW_LEVEL-PONTYPRIDD_PONTSTICILL_HIGH-RHYDYFELIN LOW LEVEL BULK-RHYDYFELIN SOUTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 1.7996 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 860.9671 | 4
1036 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 3.7195 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 416.556 | 3
1037 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_HEATH_&_LLANISHEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 7.2435 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 397.2458 | 3
1038 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_HEATH_&_LLANISHEN-LLANDENNIS ROAD-LLANDENNIS ROAD 10 INCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 5.2671 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 546.309 | 4
1039 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm |  | 42.6733 | 3.7628 | 2.5 | 50.51% | +/- 50% | OVER | 88.1776 | 1
1040 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-EPOXY_RESIN-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 6.9141 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 256.1055 | 3
1041 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-EPOXY_RESIN-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 18.1363 | 4.6482 | 2.5 | 85.93% | +/- 50% | OVER | 256.293 | 3
1042 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-EPOXY_RESIN-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL-WEOBLEY NORTH-WEOBLEY RES NORTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 2.7953 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 871.0256 | 4
1043 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-EPOXY_RESIN-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 12.3668 | 3.9842 | 2.5 | 59.37% | +/- 50% | OVER | 322.1656 | 3
1044 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-EPOXY_RESIN-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 9.3 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 333.2029 | 3
1045 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-EPOXY_RESIN-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-CEFN PENDEGAR REDUCED DMA-BRYN DERI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 4.1982 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 369.0614 | 3
1046 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-EPOXY_RESIN-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-CEFN PENDEGAR REDUCED DMA-LLANTILLIO | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 7.4396 | 3.5415 | 2.5 | 41.66% | +/- 50% | PASS | 476.0326 | 3
1047 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 9.5787 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 277.2941 | 3
1048 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(0,70]-TALYBONT-ABERGAVENNY__CWMTILLERY-LITTLE MILL TO USK | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 0.7691 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 2014.5747 | 5
1049 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 30.5587 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 72.4319 | 1
1050 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(120,160]-MONMOUTH-TRELLECH__MAYHILL__FYNNON_GAER-TRELLECK-FARR HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 8.1374 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 190.405 | 2
1051 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(160,320] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (160,320] | 33.8449 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 78.4791 | 1
1052 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 18.8512 | 4.4269 | 2.5 | 77.07% | +/- 50% | OVER | 234.8313 | 2
1053 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 8.8845 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 249.1335 | 2
1054 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-DUNFIELD_CROSSWAYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 6.2137 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 320.5969 | 3
1055 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-MONMOUTH-TRELLECH__MAYHILL__FYNNON_GAER-TRELLECK | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 15.2062 | 4.6482 | 2.5 | 85.93% | +/- 50% | OVER | 305.6783 | 3
1056 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-MONMOUTH-TRELLECH__MAYHILL__FYNNON_GAER-TRELLECK-CATBROOK | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 4.2826 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 361.7854 | 3
1057 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-MONMOUTH-TRELLECH__MAYHILL__FYNNON_GAER-TRELLECK-FARR HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 4.1417 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 587.8737 | 4
1058 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-MONMOUTH-TRELLECH__MAYHILL__FYNNON_GAER-TRELLECK-NEW MILLS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 3.5315 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 689.4403 | 4
1059 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-MONMOUTH-TRELLECH__MAYHILL__FYNNON_GAER-TRELLECK-PENALLT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 6.9887 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 348.386 | 3
1060 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 7.2701 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 213.1198 | 2
1061 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 4.7583 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 418.6519 | 3
1062 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 10.3692 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 213.461 | 2
1063 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN-SLUVAD A-LLANGIBBY VILLAGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 3.0538 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 507.3637 | 4
1064 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 6.1442 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 252.1729 | 3
1065 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT-ST JULIANS ROAD-FIRBANK AVENUE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 3.6224 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 672.1498 | 4
1066 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 29.0351 | 6.8616 | 2.5 | 174.5% | +/- 50% | OVER | 236.3218 | 2
1067 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-LITTLE MILL TO USK-GWEHELOG SUPPLY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 4.387 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 756.8188 | 4
1068 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-LITTLE MILL TO USK-USK-LLANGIBBY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 4.2554 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 364.0997 | 3
1069 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-POLYURETHANE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 13.9907 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 237.3113 | 2
1070 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-POLYURETHANE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 7.6613 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 317.8007 | 3
1071 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN-LLANYRAVON-LLANYRAVON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 6.3288 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 489.6378 | 3
1072 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm |  | 62.7377 | 4.4269 | 2.5 | 77.07% | +/- 50% | OVER | 70.5614 | 1
1073 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-CEMENT_MORTAR-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 20.3503 | 3.5415 | 2.5 | 41.66% | +/- 50% | PASS | 174.0259 | 2
1074 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-CEMENT_MORTAR-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 22.2482 | 4.8695 | 2.5 | 94.78% | +/- 50% | OVER | 218.8731 | 2
1075 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-CEMENT_MORTAR-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-GWALCHMAI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 8.6569 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 230.1157 | 2
1076 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-CEMENT_MORTAR-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-MONA TO HOLLAND ARMS-PENTRE BERW TO LLANGAFFO | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 3.8419 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 403.2922 | 3
1077 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-CEMENT_MORTAR-(70,120]-NORTH_ERYRI_/_YNYS_MON-SOUTH_ANGLESEY_CWELLYN__MYNYDD-PENMYNYDD CADNANT GAERWEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 2.8501 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 621.2956 | 4
1078 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-EPOXY_RESIN-(160,320] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (160,320] | 23.5932 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 84.4347 | 1
1079 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-EPOXY_RESIN-(160,320]-NORTH_ERYRI_/_YNYS_MON-EAST_ANGLESEY_CEFNI-LLANDYFRYDOG TO PENSARN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (160,320] | 7.7861 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 255.8503 | 3
1080 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-EPOXY_RESIN-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 9.0651 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 268.5886 | 3
1081 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-EPOXY_RESIN-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-BYLCHAU HIGH-CEFN LLWYDHENLLAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 2.8247 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 783.5976 | 4
1082 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-EPOXY_RESIN-(70,120]-CLWYD_COASTAL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 10.2682 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 172.4494 | 2
1083 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-EPOXY_RESIN-(70,120]-NORTH_ERYRI_/_YNYS_MON-EAST_ANGLESEY_CEFNI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 1.7424 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 889.2294 | 4
1084 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 8.2456 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 268.4374 | 3
1085 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 20.0769 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 88.1979 | 1
1086 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(120,160]-NORTH_ERYRI_/_YNYS_MON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 6.9966 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 221.4519 | 2
1087 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 9.8795 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 291.2552 | 3
1088 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-FLINT__CONNAHS_QUAY_BRETTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 3.1668 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 559.151 | 4
1089 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON-RHOSESMOR BERTH DDU | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 2.6603 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 582.4091 | 4
1090 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 22.0481 | 5.7549 | 2.5 | 130.2% | +/- 50% | OVER | 261.0161 | 3
1091 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT VALLEY GAP | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 9.9379 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 267.2704 | 3
1092 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-PENRHYNDEUDRAETH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 1.2302 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 1619.3256 | 5
1093 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 16.5905 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 160.0989 | 2
1094 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 6.4331 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 344.0711 | 3
1095 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-EAST_ANGLESEY_CEFNI-RHOSYBOL TO COEDEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 1.9364 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 1028.7612 | 5
1096 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 25.2714 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 96.345 | 1
1097 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-CAERGEILIOG SCHOOL 150-REFAIL CROSSROADS TO RHOSCOLY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 3.5678 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 434.275 | 3
1098 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-COEDEN TO LLANFAETHLU-LLANRHUDDLAD TO RHYDWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 2.7922 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 792.728 | 4
1099 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-COEDEN TO LLANFAETHLU-RHYDWYN VILLAGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 1.405 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 1890.5286 | 5
1100 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-MONA TO HOLLAND ARMS-CEFN CWMWD TO BETHEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 9.5703 | 4.4269 | 2.5 | 77.07% | +/- 50% | OVER | 462.5615 | 3
1101 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-SOUTH_ANGLESEY_CWELLYN__MYNYDD-FELIN ENGAN LLANFAIR PG-FELIN ENGAN TO LLANFAIRPWLL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 2.1678 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 816.8294 | 4
1102 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-POLYURETHANE-(70,120]-CLWYD_COASTAL-ABERGELE__RHYL_GLASCOED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 11.0803 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 279.6672 | 3
1103 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-CEMENT_MORTAR-(120,160]-PEMBROKESHIRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 10.6716 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 186.6712 | 2
1104 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-CEMENT_MORTAR-(120,160]-PEMBROKESHIRE-PRESELI_SUPPLY-MOUNTAIN TREFFGARNE AND RUDBAXTON-PLUMSTONE TO TREFFGARNE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 5.2817 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 335.2575 | 3
1105 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-CEMENT_MORTAR-(70,120]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 6.7603 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 392.9015 | 3
1106 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-EPOXY_RESIN-(120,160]-TYWI_C.U._AREA-CAPEL_DEWI-EBENEZER SR OUTLETS-LLANSTEPHAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 2.5094 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 793.8504 | 4
1107 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-EPOXY_RESIN-(70,120]-PEMBROKESHIRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 4.3699 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 354.5627 | 3
1108 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 15.9237 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 194.6027 | 2
1109 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm |  | 36.3621 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 54.7846 | 1
1110 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 8.3169 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 212.9102 | 2
1111 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 4.0593 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 436.223 | 3
1112 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 2.3832 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 928.7708 | 4
1113 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PENDINE-BRANDY HILL TO CROSSHANDS-PONT Y FENNI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 0.88876 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 1743.3198 | 5
1114 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 14.7209 | 4.2055 | 2.5 | 68.22% | +/- 50% | OVER | 285.6825 | 3
1115 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKEWEN__LLANDARCY_FELINDRE__CRAY-MAES RHEDYN AND LODGE DRIVE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 1.0648 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 1455.1702 | 5
1116 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 2.2951 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 675.0939 | 4
1117 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-POLYURETHANE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm |  | 12.5632 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 123.3284 | 1
1118 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-POLYURETHANE-(70,120]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 2.5296 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 787.5177 | 4
1119 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-POLYURETHANE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-TROEDYRHIW TO MAESTWYNOG-POST GWYN FFARMERS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 2.4545 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 1082.1217 | 5
1120 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN | FERROUS_1 |  |  | DIAM_LT_320 | <=320mm |  | 24.2962 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 91.1017 | 1
1121 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-EPOXY_RESIN-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 4.0244 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 385.0038 | 3
1122 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-EPOXY_RESIN-(70,120]-CYNON-MERTHYR__ABERCYNON-PENLOCKS 19INCH-HAWTHORN TERRACE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 0.80307 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 2204.9654 | 5
1123 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-EPOXY_RESIN-(70,120]-CYNON-PENDERYN__PONTSTICILL-PERTHCELYN-PERTHCELYN PUMPS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 0.91825 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 1687.3411 | 5
1124 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-EPOXY_RESIN-(70,120]-PONTSTICILL_LOW_LEVEL-RHYMNEY__BARGOED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 5.9443 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 297.8912 | 3
1125 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 11.4959 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 211.7945 | 2
1126 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(70,120]-CYNON-ABERDARE_HIRWAUN__PONSTICILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 3.7308 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 415.2959 | 3
1127 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-MERTHYR__ABERCYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 7.5385 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 293.6169 | 3
1128 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RHYMNEY__BARGOED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 3.2173 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 481.5903 | 3
1129 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 12.5409 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 247.096 | 2
1130 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-RHYMNEY__BARGOED-CEFN FOREST NORTH-BRITTANIA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 1.7853 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 867.8861 | 4
1131 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(70,120]-RHONDDA-MAERDY__PORTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 4.7418 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 513.4721 | 4
1132 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 8.5221 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 389.5909 | 3
1133 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-POLYURETHANE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 3.0866 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 501.9795 | 4
1134 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-POLYURETHANE-(70,120]-PONTSTICILL_LOW_LEVEL-MERTHYR__ABERCYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 3.1788 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 487.4173 | 3
1135 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-EASTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_1 | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm |  | 18.0678 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 98.0055 | 1
1136 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-EASTERN-EPOXY_RESIN-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 11.9118 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 222.9824 | 2
1137 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-EASTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm |  | 16.6467 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 119.6686 | 1
1138 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 14.7763 | 4.6482 | 2.5 | 85.93% | +/- 50% | OVER | 314.5703 | 3
1139 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-DUNFIELD_CROSSWAYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 6.6057 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 234.5533 | 2
1140 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 4.7219 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 328.1311 | 3
1141 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 2.0495 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 863.9962 | 4
1142 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN-MALPAS ROAD HIGH PRESSURE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 0.94237 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 1879.0306 | 5
1143 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-EASTERN-POLYURETHANE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RASSAU__SIRHOWY_VALLEY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 5.1876 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 384.0088 | 3
1144 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-EASTERN-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_SW__RISCA__ABERCARN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 8.2743 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 401.2586 | 3
1145 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-NORTHERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_1 | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm |  | 15.7391 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 126.5689 | 2
1146 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 7.6398 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 202.8065 | 2
1147 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-WESTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_1 | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm |  | 7.5095 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 206.3258 | 2
1148 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-WESTERN-EPOXY_RESIN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm |  | 9.0552 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 195.55 | 2
1149 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 5.3327 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 332.0521 | 3
1150 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 8.4678 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 313.6722 | 3
1151 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-CENTRAL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm |  | 28.3183 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 62.53 | 1
1152 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-CENTRAL-EPOXY_RESIN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm |  | 4.5294 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 342.074 | 3
1153 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 3.151 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 491.7206 | 3
1154 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 13.9286 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 143.021 | 2
1155 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-VALE_OF_GLAM__RHONDDA_VALLEYS-ALFRED STREET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 2.0028 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 994.6424 | 4
1156 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-VALE_OF_GLAM__RHONDDA_VALLEYS-LLANTRISANT TANK 12INCH PONTYCLUN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 2.9221 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 530.2286 | 4
1157 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 2.4122 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 825.8236 | 4
1158 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 2.4568 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 630.6589 | 4
1159 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH__BARRY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 3.5533 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 436.0433 | 3
1160 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm |  | 52.2135 | 3.9842 | 2.5 | 59.37% | +/- 50% | OVER | 76.3053 | 1
1161 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-BITUMEN-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 8.4408 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 236.0074 | 2
1162 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-BITUMEN-(70,120]-HEREFORD_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 7.9394 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 306.6705 | 3
1163 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-BITUMEN-(70,120]-VOWCHURCH-VOWCHURCH-BRAMPTON SR-WALTERSTONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 5.9769 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 259.2307 | 3
1164 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-BITUMEN-(70,120]-WHITBOURNE-WHITBOURNE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 1.5242 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 1161.7673 | 5
1165 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-EPOXY_RESIN-(120,160]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 7.0986 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 218.2686 | 2
1166 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-EPOXY_RESIN-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 11.6705 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 265.5239 | 3
1167 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-EPOXY_RESIN-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 22.0706 | 5.5336 | 2.5 | 121.3% | +/- 50% | OVER | 250.7219 | 3
1168 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-EPOXY_RESIN-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL-MALVERN RD-LEDBURY RES MALVERN RD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 0.51598 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 3002.8483 | 5
1169 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-EPOXY_RESIN-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL-WEOBLEY SOUTH-NORTON PRV | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 11.0923 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 159.6373 | 2
1170 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-EPOXY_RESIN-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL-WEOBLEY SOUTH-NORTON WOOD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 8.8654 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 324.5724 | 3
1171 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-EPOXY_RESIN-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL-WEOBLEY SOUTH-REDLION PUB BREDWARDINE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 17.302 | 4.6482 | 2.5 | 85.93% | +/- 50% | OVER | 268.6509 | 3
1172 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-EPOXY_RESIN-(70,120]-ROSS-ON-WYE-ROSS-ON-WYE_MITCHELDEAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 4.0275 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 384.7051 | 3
1173 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-EPOXY_RESIN-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 1.8161 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 1096.8979 | 5
1174 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 12.8034 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 242.0293 | 2
1175 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 40.1943 | 7.083 | 2.5 | 183.3% | +/- 50% | OVER | 176.2183 | 2
1176 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(120,160]-HEREFORD_C.U._AREA-DUNFIELD_CROSSWAYS-CROSSWAYS SOUTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 14.4313 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 138.0392 | 2
1177 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 6.0447 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 329.5599 | 3
1178 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 5.9755 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 296.3343 | 3
1179 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 8.0493 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 247.4866 | 2
1180 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(160,320]-HEREFORD_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (160,320] | 13.4106 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 132.0401 | 2
1181 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 29.3279 | 5.7549 | 2.5 | 130.2% | +/- 50% | OVER | 196.2264 | 2
1182 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-DUNFIELD_CROSSWAYS-CROSSWAYS NORTH AND HIGH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 20.3696 | 4.4269 | 2.5 | 77.07% | +/- 50% | OVER | 217.3264 | 2
1183 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-DUNFIELD_CROSSWAYS-CROSSWAYS NORTH AND HIGH-BRILLEY SCHOOL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 10.802 | 3.5415 | 2.5 | 41.66% | +/- 50% | PASS | 327.8531 | 3
1184 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-DUNFIELD_CROSSWAYS-CROSSWAYS NORTH AND HIGH-KINGSWOOD(CROSSWAYS HIGH) | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 2.1412 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 1033.7532 | 5
1185 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-DUNFIELD_CROSSWAYS-CROSSWAYS NORTH AND HIGH-PHONEBOX BRILLEY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 5.664 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 351.7079 | 3
1186 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-DUNFIELD_CROSSWAYS-CROSSWAYS NORTH AND HIGH-THE SHAWL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 5.8569 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 566.8725 | 4
1187 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-DUNFIELD_CROSSWAYS-CROSSWAYS SOUTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 35.888 | 4.6482 | 2.5 | 85.93% | +/- 50% | OVER | 129.5194 | 2
1188 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-DUNFIELD_CROSSWAYS-CROSSWAYS SOUTH-SARNESFIELD JUNCTION | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 2.9518 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 599.8922 | 4
1189 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 8.2346 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 241.9169 | 2
1190 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL-BEWDLEY RES TO WOEBLEY RES TDMA-AREA FEED BY 1T810310 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 1.4414 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 1074.9464 | 5
1191 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL-WEOBLEY SOUTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 3.8274 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 462.6466 | 3
1192 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__SOUTH_BROOMY_HILL_ | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 4.609 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 336.1682 | 3
1193 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 8.2054 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 215.8027 | 2
1194 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 8.051 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 357.4016 | 3
1195 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 17.5735 | 5.0909 | 2.5 | 103.6% | +/- 50% | OVER | 289.6906 | 3
1196 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN-LLANDERFEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 4.9217 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 449.7266 | 3
1197 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN-MALPAS ROAD HIGH PRESSURE-WHITTLE DRIVE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 1.389 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 1593.4903 | 5
1198 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 13.3063 | 3.9842 | 2.5 | 59.37% | +/- 50% | OVER | 299.4202 | 3
1199 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT-RINGWOOD 1 AND 2 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 3.2273 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 480.0898 | 3
1200 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 6.5387 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 473.9174 | 3
1201 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-CHAIN ROAD DAN Y DERRY-CHAIN ROAD(UNDERHILL) | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 3.5189 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 503.2121 | 4
1202 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-VOWCHURCH-VOWCHURCH-BRAMPTON SR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 24.9547 | 3.5415 | 2.5 | 41.66% | +/- 50% | PASS | 141.9165 | 2
1203 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-VOWCHURCH-VOWCHURCH-BRAMPTON SR-MYNYDD FERDDYN (LONGTOWN) | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 1.3443 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 1152.554 | 5
1204 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-VOWCHURCH-VOWCHURCH-BRAMPTON SR-SARAS CROSS (LONGTOWN) | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 5.4155 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 326.9776 | 3
1205 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-WHITBOURNE-WHITBOURNE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 8.3185 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 319.3007 | 3
1206 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-WHITBOURNE-WHITBOURNE-RIDGEWAY STIFFORDS BRIDGE-STIFFORDS BRIDGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 3.105 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 570.2895 | 4
1207 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-WHITBOURNE-WHITBOURNE-WARRENWOOD-UPPER SAPEY METER | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 0.6001 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 2950.7468 | 5
1208 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-POLYURETHANE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm |  | 12.6937 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 122.0607 | 1
1209 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-POLYURETHANE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 9.7679 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 203.9417 | 2
1210 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 6.8497 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 387.7732 | 3
1211 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN-BETTWS EAST-BETTWS EAST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 4.0791 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 596.8951 | 4
1212 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-POLYURETHANE-(70,120]-TALYBONT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 2.5553 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 866.2155 | 4
1213 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-NORTHERN-EPOXY_RESIN-(70,120]-CLWYD_COASTAL-PRESTATYN_GLASCOED__TRECASTELL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 7.3783 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 209.994 | 2
1214 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-NORTHERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm |  | 17.5338 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 113.6141 | 1
1215 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 10.1374 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 262.0117 | 3
1216 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 13.1095 | 3.7628 | 2.5 | 50.51% | +/- 50% | OVER | 287.0296 | 3
1217 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-WESTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm |  | 35.2546 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 69.0625 | 1
1218 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 8.9721 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 296.0425 | 3
1219 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 6.6147 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 234.2353 | 2
1220 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SKEWEN__LLANDARCY_FELINDRE__CRAY-EAST SWANSEA DOCKS-BURROWS ENTRANCE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 0.32472 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 6816.3214 | 5
1221 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 19.4945 | 6.8616 | 2.5 | 174.5% | +/- 50% | OVER | 351.9776 | 3
1222 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PORT_TALBOT_FELINDRE__CRAY-TY CANOL PUMPED OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 3.4355 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 450.9984 | 3
1223 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-CENTRAL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_1 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm |  | 18.5816 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 154.8551 | 2
1224 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 11.7806 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 131.5209 | 2
1225 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(70,120]-CYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 4.8768 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 317.708 | 3
1226 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-MERTHYR__ABERCYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 16.334 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 189.7144 | 2
1227 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-MERTHYR__ABERCYNON-PONSTICILL AND VAYNOR-TREFECHAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 3.6236 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 732.9952 | 4
1228 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 18.2924 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 181.5043 | 2
1229 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(70,120]-RHONDDA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 8.1734 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 352.0531 | 3
1230 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 14.9489 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 192.4867 | 2
1231 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-CENTRAL-POLYURETHANE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 2.8853 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 537.0065 | 4
1232 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-CENTRAL-POLYURETHANE-(70,120]-CYNON-ABERDARE_HIRWAUN__PONSTICILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 4.3368 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 357.2661 | 3
1233 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-CENTRAL-POLYURETHANE-(70,120]-PONTSTICILL_LOW_LEVEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 5.1028 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 303.6348 | 3
1234 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-EASTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_1 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm |  | 41.8074 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 37.0604 | 1
1235 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-EASTERN-EPOXY_RESIN-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 11.7602 | 4.8695 | 2.5 | 94.78% | +/- 50% | OVER | 414.0692 | 3
1236 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-EASTERN-EPOXY_RESIN-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 7.6797 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 201.7528 | 2
1237 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 12.8048 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 155.5729 | 2
1238 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 14.8581 | 4.2055 | 2.5 | 68.22% | +/- 50% | OVER | 283.0449 | 3
1239 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-BRECON_/_PORTIS-BRECON_BOREHOLES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 3.1321 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 494.6909 | 3
1240 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 14.0843 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 204.3031 | 2
1241 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 2.358 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 657.0887 | 4
1242 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 5.6146 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 551.9162 | 4
1243 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-WHITBOURNE-WHITBOURNE-WARRENWOOD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 4.4189 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 651.1641 | 4
1244 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-EASTERN-POLYURETHANE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 7.3755 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 330.114 | 3
1245 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-EASTERN-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 5.2726 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 335.8389 | 3
1246 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-NORTHERN-EPOXY_RESIN-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 1.5862 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 1116.3261 | 5
1247 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-NORTHERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm |  | 6.8324 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 291.565 | 3
1248 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-ALWEN_/_DEE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 3.9297 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 450.6038 | 3
1249 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 2.614 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 677.4146 | 4
1250 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 6.0327 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 256.833 | 3
1251 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-BRYN GWENALLT-CARMEL BOOSTER | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 0.86996 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 2544.2914 | 5
1252 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-WESTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_1 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm |  | 27.9845 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 102.8232 | 1
1253 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-WESTERN-EPOXY_RESIN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_1 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm |  | 6.7799 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 228.5296 | 2
1254 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 5.3977 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 369.0619 | 3
1255 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 10.171 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 217.6214 | 2
1256 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 16.2487 | 4.4269 | 2.5 | 77.07% | +/- 50% | OVER | 272.4431 | 3
1257 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 6.1843 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 393.7004 | 3
1258 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY-NOTTAGE MAIN-FULMAR ROAD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 3.9957 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 553.9466 | 4
1259 | DIAM_LT_320-FERROUS_2-<=320mm | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY | FERROUS_2 |  |  | DIAM_LT_320 | <=320mm |  | 62.4075 | 1.9277 | 2.5 | -22.89% | +/- 50% | PASS | 30.8883 | 1
1260 | DIAM_LT_320-FERROUS_2-<=320mm-B11_1950-1941_1960-WESTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_2 | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm |  | 78.6264 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 28.1512 | 1
1261 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm |  | 43.4313 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 40.7711 | 1
1262 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-CENTRAL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm |  | 36.5938 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 48.3891 | 1
1263 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-CENTRAL-CEMENT_MORTAR-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 14.034 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 110.4033 | 1
1264 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(160,320]-PONTSTICILL_LOW_LEVEL-VALE_OF_GLAM__RHONDDA_VALLEYS-12 LLANILID OUTLET TDMA-AREA FED BY SUB SUPPLY SYSTEM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (160,320] | 1.3837 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 1599.6723 | 5
1265 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 34.3908 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 96.5415 | 1
1266 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-CEMENT_MORTAR-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 5.7834 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 420.9912 | 3
1267 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-CEMENT_MORTAR-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 3.8437 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 403.0983 | 3
1268 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-CEMENT_MORTAR-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 6.6567 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 299.2586 | 3
1269 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-EPOXY_RESIN-(120,160]-TALYBONT-ABERGAVENNY__CWMTILLERY-8116-CONFIRMED OUTSIDE OF SDMAS-PANT FARM OUTLET TO CROSS ASH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 1.9173 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 923.5602 | 4
1270 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-EPOXY_RESIN-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 13.9187 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 159.0252 | 2
1271 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 17.5421 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 189.2672 | 2
1272 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 14.1993 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 155.8824 | 2
1273 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(160,320] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (160,320] | 26.0128 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 68.072 | 1
1274 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(160,320]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (160,320] | 9.624 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 183.9915 | 2
1275 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(160,320]-WHITBOURNE-WHITBOURNE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (160,320] | 2.2664 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 1074.2983 | 5
1276 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 41.4749 | 5.0909 | 2.5 | 103.6% | +/- 50% | OVER | 122.7462 | 1
1277 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 8.4515 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 314.277 | 3
1278 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 4.8547 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 410.3388 | 3
1279 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN-THORNHILL-THORNHILL ROAD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 4.2817 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 723.7335 | 4
1280 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 8.024 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 220.6806 | 2
1281 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-WHITBOURNE-WHITBOURNE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 5.0619 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 306.0919 | 3
1282 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-POLYURETHANE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm |  | 20.7452 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 74.687 | 1
1283 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-NORTHERN-CEMENT_MORTAR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm |  | 45.4796 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 43.8018 | 1
1284 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-NORTHERN-CEMENT_MORTAR-(160,320]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT VALLEY TRUNK-AREA FED BY S/SUPPLY 3SC20M18 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (160,320] | 2.8543 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 697.9238 | 4
1285 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-NORTHERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm |  | 20.0475 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 88.3272 | 1
1286 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 25.1317 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 88.073 | 1
1287 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 31.2392 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 63.7687 | 1
1288 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-WESTERN-CEMENT_MORTAR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm |  | 56.6301 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 46.9028 | 1
1289 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-WESTERN-CEMENT_MORTAR-(160,320]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (160,320] | 57.3505 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 27.0163 | 1
1290 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 15.4688 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 157.3986 | 2
1291 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(120,160]-PEMBROKESHIRE-PENDINE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 7.0866 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 218.6375 | 2
1292 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(160,320] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (160,320] | 43.5157 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 50.8651 | 1
1293 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 13.4444 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 164.6359 | 2
1294 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1961_1980-CENTRAL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_2 | 1961_1980 | B14_1980 | DIAM_LT_320 | <=320mm |  | 37.2625 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 53.4608 | 1
1295 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1961_1980-CENTRAL-CEMENT_MORTAR-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1961_1980 | B14_1980 | DIAM_LT_320 | <=320mm | (70,120] | 66.866 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 39.7229 | 1
1296 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1961_1980-EASTERN-CEMENT_MORTAR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_2 | 1961_1980 | B14_1980 | DIAM_LT_320 | <=320mm |  | 17.4504 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 88.789 | 1
1297 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1961_1980-EASTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_2 | 1961_1980 | B14_1980 | DIAM_LT_320 | <=320mm |  | 11.2086 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 138.2337 | 2
1298 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | FERROUS_2 | 1981_2000 | B14_1980 | DIAM_LT_320 | <=320mm |  | 58.3389 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 26.5586 | 1
1299 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-CENTRAL-CEMENT_MORTAR-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1981_2000 | B14_1980 | DIAM_LT_320 | <=320mm | (120,160] | 47.2749 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 42.1383 | 1
1300 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-CENTRAL-CEMENT_MORTAR-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1981_2000 | B14_1980 | DIAM_LT_320 | <=320mm | (70,120] | 46.2273 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 62.2459 | 1
1301 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-CENTRAL-CEMENT_MORTAR-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_2 | 1981_2000 | B14_1980 | DIAM_LT_320 | <=320mm | (70,120] | 95.509 | 3.9842 | 2.5 | 59.37% | +/- 50% | OVER | 41.7151 | 1
1302 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-EASTERN-CEMENT_MORTAR-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1981_2000 | B14_1980 | DIAM_LT_320 | <=320mm | (120,160] | 40.1473 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 82.699 | 1
1303 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-EASTERN-CEMENT_MORTAR-(160,320] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1981_2000 | B14_1980 | DIAM_LT_320 | <=320mm | (160,320] | 82.9268 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 32.0296 | 1
1304 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-EASTERN-CEMENT_MORTAR-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1981_2000 | B14_1980 | DIAM_LT_320 | <=320mm | (70,120] | 34.0614 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 71.4818 | 1
1305 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-EASTERN-CEMENT_MORTAR-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_2 | 1981_2000 | B14_1980 | DIAM_LT_320 | <=320mm | (70,120] | 27.2936 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 113.5357 | 1
1306 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-EASTERN-CEMENT_MORTAR-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_2 | 1981_2000 | B14_1980 | DIAM_LT_320 | <=320mm | (70,120] | 21.4018 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 103.4226 | 1
1307 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-EASTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_2 | 1981_2000 | B14_1980 | DIAM_LT_320 | <=320mm |  | 77.0763 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 31.5891 | 1
1308 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-NORTHERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_2 | 1981_2000 | B14_1980 | DIAM_LT_320 | <=320mm |  | 105.38 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 14.703 | 1
1309 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-WESTERN-CEMENT_MORTAR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_2 | 1981_2000 | B14_1980 | DIAM_LT_320 | <=320mm |  | 61.5452 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 28.7714 | 1
1310 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-WESTERN-CEMENT_MORTAR-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_2 | 1981_2000 | B14_1980 | DIAM_LT_320 | <=320mm | (120,160] | 29.4948 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 112.5669 | 1
1311 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-WESTERN-CEMENT_MORTAR-(120,160]-TYWI_C.U._AREA-DAFEN__FELINDRE-FRAMPTON OUTLET RED DMA-PRINCESS STREET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_2 | 1981_2000 | B14_1980 | DIAM_LT_320 | <=320mm | (120,160] | 0.2621 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 7600.3595 | 5
1312 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-WESTERN-CEMENT_MORTAR-(160,320]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_2 | 1981_2000 | B14_1980 | DIAM_LT_320 | <=320mm | (160,320] | 55.0406 | 4.8695 | 2.5 | 94.78% | +/- 50% | OVER | 88.4719 | 1
1313 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-WESTERN-CEMENT_MORTAR-(160,320]-TYWI_C.U._AREA-PENCOED__BRIDGEND_VALLEYS-CEFN HIRGOED TO LLANGEINOR-TYN-Y-WAUN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_2 | 1981_2000 | B14_1980 | DIAM_LT_320 | <=320mm | (160,320] | 0.67383 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 2299.4088 | 5
1314 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-WESTERN-CEMENT_MORTAR-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_2 | 1981_2000 | B14_1980 | DIAM_LT_320 | <=320mm | (70,120] | 26.332 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 92.4644 | 1
1315 | DIAM_LT_320-FERROUS_2-<=320mm-B15_1990-1981_2000 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | FERROUS_2 | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm |  | 222.9507 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 9.9279 | 1
1316 | DIAM_LT_320-FERROUS_2-<=320mm-B15_1990-1981_2000-CENTRAL-CEMENT_MORTAR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_2 | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm |  | 105.7431 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 18.8389 | 1
1317 | DIAM_LT_320-FERROUS_2-<=320mm-B15_1990-1981_2000-CENTRAL-CEMENT_MORTAR-(160,320]-CYNON-PENDERYN__PONTSTICILL-RHIGOS VILLAGE 8IN & 10IN OUTLETS-HIRWAUN INDUSTRIAL ESTATE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_2 | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (160,320] | 2.06 | 3.7628 | 2.5 | 50.51% | +/- 50% | OVER | 1826.6325 | 5
1318 | DIAM_LT_320-FERROUS_2-<=320mm-B15_1990-1981_2000-EASTERN-CEMENT_MORTAR-(160,320] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (160,320] | 56.4909 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 27.4274 | 1
1319 | DIAM_LT_320-FERROUS_2-<=320mm-B15_1990-1981_2000-EASTERN-CEMENT_MORTAR-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (70,120] | 25.632 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 60.4479 | 1
1320 | DIAM_LT_320-FERROUS_2-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (70,120] | 7.4889 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 266.004 | 3
1321 | DIAM_LT_320-FERROUS_2-<=320mm-B15_1990-1981_2000-NORTHERN-CEMENT_MORTAR-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (70,120] | 40.982 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 37.8069 | 1
1322 | DIAM_LT_320-FERROUS_2-<=320mm-B15_1990-1981_2000-WESTERN-CEMENT_MORTAR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | FERROUS_2 | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm |  | 183.5565 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 10.8527 | 1
1323 | DIAM_LT_320-FERROUS_2-<=320mm-B16_2000-2001_2020 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | FERROUS_2 | 2001_2020 | B16_2000 | DIAM_LT_320 | <=320mm |  | 94.9469 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 27.9747 | 1
1324 | DIAM_LT_320-FERROUS_2-<=320mm-B16_2000-2001_2020-CENTRAL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | FERROUS_2 | 2001_2020 | B16_2000 | DIAM_LT_320 | <=320mm |  | 47.5942 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 46.5063 | 1
1325 | DIAM_LT_320-FERROUS_2-<=320mm-B16_2000-2001_2020-WESTERN-EPOXY_RESIN-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 2001_2020 | B16_2000 | DIAM_LT_320 | <=320mm | (120,160] | 15.9136 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 125.1809 | 2
1326 | DIAM_LT_320-FERROUS_2-<=320mm-B16_2000-2001_2020-WESTERN-EPOXY_RESIN-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 2001_2020 | B16_2000 | DIAM_LT_320 | <=320mm | (70,120] | 14.6353 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 120.991 | 1
1327 | DIAM_LT_320-FERROUS_2-<=320mm-B17_2010-2001_2020 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | FERROUS_2 | 2001_2020 | B17_2010 | DIAM_LT_320 | <=320mm |  | 52.7717 | 2.7389 | 2.5 | 9.556% | +/- 50% | PASS | 51.9008 | 1
1328 | DIAM_LT_320-OTHER-<=320mm-B12_1960 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN | OTHER |  |  | DIAM_LT_320 | <=320mm | (0,70] | 0.2377 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 6518.2684 | 5
1329 | DIAM_LT_320-PLASTIC_PE-<=320mm | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY | PLASTIC_PE |  |  | DIAM_LT_320 | <=320mm |  | 158.6537 | 3.4398 | 2.5 | 37.59% | +/- 50% | PASS | 21.6811 | 1
1330 | DIAM_LT_320-PLASTIC_PE-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (0,70] | 17.6289 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 87.8898 | 1
1331 | DIAM_LT_320-PLASTIC_PE-<=320mm-B14_1980-1981_2000 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | PLASTIC_PE | 1981_2000 | B14_1980 | DIAM_LT_320 | <=320mm |  | 123.6303 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 25.065 | 1
1332 | DIAM_LT_320-PLASTIC_PE-<=320mm-B14_1980-1981_2000-EASTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 1981_2000 | B14_1980 | DIAM_LT_320 | <=320mm | (120,160] | 91.7673 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 26.532 | 1
1333 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | PLASTIC_PE | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm |  | 63.2957 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 24.4788 | 1
1334 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-CENTRAL-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (120,160] | 71.502 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 24.765 | 1
1335 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (120,160] | 183.4648 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 13.2711 | 1
1336 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-PENARTH__BARRY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PE | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (120,160] | 12.6912 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 122.0845 | 1
1337 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-CENTRAL-NONE-(160,320] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (160,320] | 55.4374 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 35.934 | 1
1338 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (70,120] | 30.8484 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 86.1022 | 1
1339 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (0,70] | 80.8626 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 27.3727 | 1
1340 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (120,160] | 219.959 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 14.0881 | 1
1341 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (120,160] | 73.9578 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 29.9283 | 1
1342 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PE | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (120,160] | 38.5794 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 57.3734 | 1
1343 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(120,160]-TALYBONT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (120,160] | 16.9566 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 91.3744 | 1
1344 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(120,160]-TALYBONT-ABERGAVENNY__CWMTILLERY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PE | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (120,160] | 107.8409 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 30.7874 | 1
1345 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(160,320] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (160,320] | 78.4374 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 28.219 | 1
1346 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(160,320]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (160,320] | 42.876 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 41.2992 | 1
1347 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(160,320]-TALYBONT-ABERGAVENNY__CWMTILLERY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PE | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (160,320] | 24.8863 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 71.1533 | 1
1348 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (70,120] | 108.6284 | 3.7628 | 2.5 | 50.51% | +/- 50% | OVER | 34.6394 | 1
1349 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (70,120] | 93.8772 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 25.9357 | 1
1350 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (70,120] | 61.1432 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 50.6811 | 1
1351 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-NORTHERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | PLASTIC_PE | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm |  | 272.8248 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 9.7356 | 1
1352 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-NORTHERN-NONE-(160,320] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (160,320] | 120.8574 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 14.6515 | 1
1353 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (70,120] | 103.6776 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 17.0793 | 1
1354 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-NORTHERN-NONE-(70,120]-ALWEN_/_DEE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (70,120] | 103.112 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 15.0264 | 1
1355 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | PLASTIC_PE | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm |  | 139.651 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 11.0948 | 1
1356 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-WESTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (0,70] | 57.7485 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 26.8301 | 1
1357 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-WESTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (120,160] | 97.016 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 18.2521 | 1
1358 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN | PLASTIC_PE |  |  | DIAM_LT_320 | <=320mm |  | 63.6539 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 24.341 | 1
1359 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | PLASTIC_PE | 2001_2020 | B16_2000 | DIAM_LT_320 | <=320mm |  | 96.4789 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 27.5305 | 1
1360 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 2001_2020 | B16_2000 | DIAM_LT_320 | <=320mm | (120,160] | 31.9318 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 69.3174 | 1
1361 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-CENTRAL-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 2001_2020 | B16_2000 | DIAM_LT_320 | <=320mm | (70,120] | 57.8231 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 45.9352 | 1
1362 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 2001_2020 | B16_2000 | DIAM_LT_320 | <=320mm | (70,120] | 82.3161 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 40.334 | 1
1363 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 2001_2020 | B16_2000 | DIAM_LT_320 | <=320mm | (70,120] | 107.1434 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 24.7903 | 1
1364 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-EASTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 2001_2020 | B16_2000 | DIAM_LT_320 | <=320mm | (0,70] | 127.7897 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 20.785 | 1
1365 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-EASTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 2001_2020 | B16_2000 | DIAM_LT_320 | <=320mm | (120,160] | 200.9577 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 15.4202 | 1
1366 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 2001_2020 | B16_2000 | DIAM_LT_320 | <=320mm | (120,160] | 27.3571 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 64.7269 | 1
1367 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-EASTERN-NONE-(160,320]-HEREFORD_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 2001_2020 | B16_2000 | DIAM_LT_320 | <=320mm | (160,320] | 49.9136 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 31.0416 | 1
1368 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 2001_2020 | B16_2000 | DIAM_LT_320 | <=320mm | (70,120] | 318.6634 | 4.8695 | 2.5 | 94.78% | +/- 50% | OVER | 15.2811 | 1
1369 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 2001_2020 | B16_2000 | DIAM_LT_320 | <=320mm | (70,120] | 110.2674 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 16.0586 | 1
1370 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PE | 2001_2020 | B16_2000 | DIAM_LT_320 | <=320mm | (70,120] | 139.885 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 12.6586 | 1
1371 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 2001_2020 | B16_2000 | DIAM_LT_320 | <=320mm | (70,120] | 88.6929 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 29.9473 | 1
1372 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PE | 2001_2020 | B16_2000 | DIAM_LT_320 | <=320mm | (70,120] | 115.4523 | 3.5415 | 2.5 | 41.66% | +/- 50% | PASS | 30.6749 | 1
1373 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-CROSS ASH-CROSS ASH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PE | 2001_2020 | B16_2000 | DIAM_LT_320 | <=320mm | (70,120] | 9.2551 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 191.3261 | 2
1374 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-NORTHERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | PLASTIC_PE | 2001_2020 | B16_2000 | DIAM_LT_320 | <=320mm |  | 209.9392 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 9.4889 | 1
1375 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 2001_2020 | B16_2000 | DIAM_LT_320 | <=320mm | (70,120] | 280.7902 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 10.2477 | 1
1376 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | PLASTIC_PE | 2001_2020 | B16_2000 | DIAM_LT_320 | <=320mm |  | 141.262 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 17.2359 | 1
1377 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 2001_2020 | B16_2000 | DIAM_LT_320 | <=320mm | (0,70] | 32.1731 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 48.1582 | 1
1378 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-WESTERN-NONE-(0,70]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 2001_2020 | B16_2000 | DIAM_LT_320 | <=320mm | (0,70] | 51.0261 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 47.7162 | 1
1379 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-WESTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 2001_2020 | B16_2000 | DIAM_LT_320 | <=320mm | (120,160] | 174.1763 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 16.5204 | 1
1380 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-WESTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 2001_2020 | B16_2000 | DIAM_LT_320 | <=320mm | (70,120] | 113.3497 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 13.6692 | 1
1381 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PE | 2001_2020 | B16_2000 | DIAM_LT_320 | <=320mm | (70,120] | 91.4897 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 16.9352 | 1
1382 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PE | 2001_2020 | B16_2000 | DIAM_LT_320 | <=320mm | (70,120] | 249.1136 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 11.5508 | 1
1383 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PRESELI_SUPPLY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PE | 2001_2020 | B16_2000 | DIAM_LT_320 | <=320mm | (70,120] | 88.3699 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 22.5426 | 1
1384 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 2001_2020 | B16_2000 | DIAM_LT_320 | <=320mm | (70,120] | 346.2703 | 5.5336 | 2.5 | 121.3% | +/- 50% | OVER | 15.9805 | 1
1385 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PE | 2001_2020 | B16_2000 | DIAM_LT_320 | <=320mm | (70,120] | 144.8952 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 16.8037 | 1
1386 | DIAM_LT_320-PLASTIC_PE-<=320mm-B17_2010-2001_2020-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | PLASTIC_PE | 2001_2020 | B17_2010 | DIAM_LT_320 | <=320mm |  | 49.6067 | 2.0212 | 2.5 | -19.15% | +/- 50% | PASS | 40.7454 | 1
1387 | DIAM_LT_320-PLASTIC_PE-<=320mm-B17_2010-2001_2020-CENTRAL-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 2001_2020 | B17_2010 | DIAM_LT_320 | <=320mm | (70,120] | 98.4205 | 2.0526 | 2.5 | -17.9% | +/- 50% | PASS | 20.8553 | 1
1388 | DIAM_LT_320-PLASTIC_PE-<=320mm-B17_2010-2001_2020-EASTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | PLASTIC_PE | 2001_2020 | B17_2010 | DIAM_LT_320 | <=320mm |  | 194.471 | 1.5769 | 2.5 | -36.92% | +/- 50% | PASS | 8.1086 | 1
1389 | DIAM_LT_320-PLASTIC_PE-<=320mm-B17_2010-2001_2020-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 2001_2020 | B17_2010 | DIAM_LT_320 | <=320mm | (70,120] | 219.3154 | 4.1458 | 2.5 | 65.83% | +/- 50% | OVER | 18.9034 | 1
1390 | DIAM_LT_320-PLASTIC_PE-<=320mm-B17_2010-2001_2020-NORTHERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | PLASTIC_PE | 2001_2020 | B17_2010 | DIAM_LT_320 | <=320mm |  | 159.473 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 15.2676 | 1
1391 | DIAM_LT_320-PLASTIC_PE-<=320mm-B17_2010-2001_2020-NORTHERN-NONE-(0,70]-ALWEN_/_DEE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 2001_2020 | B17_2010 | DIAM_LT_320 | <=320mm | (0,70] | 16.8724 | 1.7729 | 2.5 | -29.08% | +/- 50% | PASS | 105.0787 | 1
1392 | DIAM_LT_320-PLASTIC_PE-<=320mm-B17_2010-2001_2020-NORTHERN-NONE-(0,70]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PE | 2001_2020 | B17_2010 | DIAM_LT_320 | <=320mm | (0,70] | 14.1527 | 1.5649 | 2.5 | -37.41% | +/- 50% | PASS | 110.5703 | 1
1393 | DIAM_LT_320-PLASTIC_PE-<=320mm-B17_2010-2001_2020-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 2001_2020 | B17_2010 | DIAM_LT_320 | <=320mm | (70,120] | 199.5654 | 1.7763 | 2.5 | -28.95% | +/- 50% | PASS | 8.9011 | 1
1394 | DIAM_LT_320-PLASTIC_PE-<=320mm-B17_2010-2001_2020-WESTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 2001_2020 | B17_2010 | DIAM_LT_320 | <=320mm | (0,70] | 74.3294 | 2.3718 | 2.5 | -5.129% | +/- 50% | PASS | 31.9089 | 1
1395 | DIAM_LT_320-PLASTIC_PE-<=320mm-B17_2010-2001_2020-WESTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 2001_2020 | B17_2010 | DIAM_LT_320 | <=320mm | (70,120] | 125.9134 | 2.2255 | 2.5 | -10.98% | +/- 50% | PASS | 17.6751 | 1
1396 | DIAM_LT_320-PLASTIC_PE-<=320mm-B17_2010-2001_2020-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 2001_2020 | B17_2010 | DIAM_LT_320 | <=320mm | (70,120] | 130.4877 | 2.5527 | 2.5 | 2.107% | +/- 50% | PASS | 19.5627 | 1
1397 | DIAM_LT_320-PLASTIC_PE-<=320mm-B18_2020-2021_ONWARDS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | PLASTIC_PE | 2021_ONWARDS | B18_2020 | DIAM_LT_320 | <=320mm |  | 50.2376 | 2.3314 | 2.5 | -6.745% | +/- 50% | PASS | 46.407 | 1
1398 | DIAM_LT_320-PLASTIC_PE-<=320mm-B18_2020-2021_ONWARDS-NORTHERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 2021_ONWARDS | B18_2020 | DIAM_LT_320 | <=320mm | (0,70] | 2.4863 | 2.2968 | 2.5 | -8.126% | +/- 50% | PASS | 923.7956 | 4
1399 | DIAM_LT_320-PLASTIC_PE-<=320mm-B18_2020-2021_ONWARDS-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 2021_ONWARDS | B18_2020 | DIAM_LT_320 | <=320mm | (70,120] | 18.6445 | 2.0387 | 2.5 | -18.45% | +/- 50% | PASS | 109.3481 | 1
1400 | DIAM_LT_320-PLASTIC_PVC-<=320mm | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY | PLASTIC_PVC |  |  | DIAM_LT_320 | <=320mm |  | 30.0647 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 66.26 | 1
1401 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1921_1940 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | PLASTIC_PVC | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm |  | 8.8888 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 174.3091 | 2
1402 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1921_1940-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | PLASTIC_PVC | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm |  | 6.9357 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 223.3936 | 2
1403 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 18.8064 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 105.9259 | 1
1404 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-PEMBROKESHIRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1921_1940 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 15.7861 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 98.1497 | 1
1405 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | PLASTIC_PVC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm |  | 12.5951 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 210.8844 | 2
1406 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 5.7288 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 386.3703 | 3
1407 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | PLASTIC_PVC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm |  | 45.9958 | 3.7628 | 2.5 | 50.51% | +/- 50% | OVER | 81.8082 | 1
1408 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (0,70] | 6.3373 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 244.4877 | 2
1409 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-BETTWS LLANGYBI AND LLANDDEWI BREFI-BETTWS BLEDRWS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (0,70] | 0.56634 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 5471.6476 | 5
1410 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (0,70] | 5.9911 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 258.6158 | 3
1411 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(120,160]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (120,160] | 15.5997 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 198.6448 | 2
1412 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(120,160]-PEMBROKESHIRE-BOLTON_HILL-PLUMSTONE TO BRAWDY-CUFFERN/SIMPSON CROSS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (120,160] | 5.4483 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 325.0063 | 3
1413 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(120,160]-PEMBROKESHIRE-BOLTON_HILL-ROSEPOOL-ROSEPOOL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (120,160] | 1.3797 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 1604.2315 | 5
1414 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(120,160]-PEMBROKESHIRE-PRESELI_SUPPLY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (120,160] | 4.7199 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 468.9613 | 3
1415 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (120,160] | 22.3889 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 128.5219 | 2
1416 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 23.4716 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 75.4421 | 1
1417 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 14.4671 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 107.0984 | 1
1418 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 52.5275 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 42.1385 | 1
1419 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PENDINE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 10.5321 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 168.1275 | 2
1420 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PRESELI_SUPPLY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 19.841 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 78.0907 | 1
1421 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1941_1960 | B10_1940 | DIAM_LT_320 | <=320mm | (70,120] | 70.404 | 6.6403 | 2.5 | 165.6% | +/- 50% | OVER | 94.3169 | 1
1422 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | PLASTIC_PVC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm |  | 21.1322 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 83.7935 | 1
1423 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 5.1008 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 347.1524 | 3
1424 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 8.0783 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 191.7979 | 2
1425 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 13.2676 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 116.7806 | 1
1426 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-ELAN_/_BUILTH-ELAN-NEUADD NORTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | PLASTIC_PVC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 8.2851 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 347.3032 | 3
1427 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-PILLETH-PILLETH_KNIGHTON__BLEDDFA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 2.5068 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 706.3668 | 4
1428 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 5.1041 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 346.9227 | 3
1429 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-TALYBONT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 6.8251 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 227.0147 | 2
1430 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(120,160]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-GOSEN TYN Y FRITH-GOSEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (120,160] | 3.1016 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 499.5492 | 3
1431 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 13.5675 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 114.1997 | 1
1432 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-GOSEN TYN Y FRITH-GOSEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 5.8745 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 263.7509 | 3
1433 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | PLASTIC_PVC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm |  | 14.7815 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 194.666 | 2
1434 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-PENWCH SERVICE RES OUTLET-BETHANIA TREFENTER | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (0,70] | 4.3223 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 409.6738 | 3
1435 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 32.8094 | 3.7628 | 2.5 | 50.51% | +/- 50% | OVER | 114.6875 | 1
1436 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-BETTWS LLANGYBI AND LLANDDEWI BREFI-LANGYBI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 6.2494 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 283.3476 | 3
1437 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-PENWCH SERVICE RES OUTLET-BETHANIA TREFENTER | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 13.1197 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 236.1947 | 2
1438 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAPEL_DEWI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 6.9042 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 288.5319 | 3
1439 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1941_1960 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | PLASTIC_PVC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm |  | 15.8616 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 167.4561 | 2
1440 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 8.0391 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 220.2659 | 2
1441 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 3.9506 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 448.2204 | 3
1442 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH-STUMPY EAST NO. 2 OUTLET-HOLTON ROAD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 1.3918 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 1272.2309 | 5
1443 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1941_1960-EASTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | PLASTIC_PVC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm |  | 21.2245 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 73.0006 | 1
1444 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 11.9868 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 147.7249 | 2
1445 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1941_1960-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | PLASTIC_PVC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm |  | 16.3005 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 135.7889 | 2
1446 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(120,160]-PEMBROKESHIRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 24.0017 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 73.7758 | 1
1447 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 62.8585 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 49.298 | 1
1448 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PENDINE-CROSSHANDS RES OUTLETS-X HANDS RES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 26.252 | 3.5415 | 2.5 | 41.66% | +/- 50% | PASS | 134.9034 | 2
1449 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAPEL_DEWI-MAENIEUAN OUTLETS-MADOX TO TRELECH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1941_1960 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 12.0307 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 128.7871 | 2
1450 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm |  | 9.5619 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 185.1873 | 2
1451 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 2.9316 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 528.5137 | 4
1452 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 6.4101 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 276.2442 | 3
1453 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__RUMNEY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 4.423 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 450.396 | 3
1454 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__RUMNEY-LLANRUMNEY AVENUE-NEWPORT ROAD RUMNEY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 0.42346 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 3658.9123 | 5
1455 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_EAST-COED Y GORAS-COED Y GORES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 1.8704 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 1301.7321 | 5
1456 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_EAST-TY DRAW ROAD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 4.4997 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 393.5234 | 3
1457 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_HEATH_&_LLANISHEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 8.0149 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 414.2483 | 3
1458 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 16.5119 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 201.0756 | 2
1459 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_EAST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 14.3902 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 123.0522 | 1
1460 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_EAST-COED Y GORAS-COED Y GORES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 3.0327 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 656.8689 | 4
1461 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_EAST-NORTH PENTWYN SOUTH-NORTH PENTWYN SOUTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 4.116 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 376.436 | 3
1462 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 4.1785 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 476.7499 | 3
1463 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_HEATH_&_LLANISHEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 9.5279 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 302.0037 | 3
1464 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_HEATH_&_LLANISHEN-WERN GOCH ROAD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 8.6009 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 257.3472 | 3
1465 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 11.6198 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 228.5857 | 2
1466 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm |  | 31.7224 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 55.82 | 1
1467 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(0,70]-TALYBONT-ABERGAVENNY__CWMTILLERY-PONTYPOOL TDMA-AREA FED BY SUB SUPPLY SYSTEM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 2.7064 | 3.7628 | 2.5 | 50.51% | +/- 50% | OVER | 1390.3393 | 5
1468 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(120,160]-TALYBONT-ABERGAVENNY__CWMTILLERY-BUNKERS-HILLSIDE NO.1 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 1.2101 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 1280.4375 | 5
1469 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(120,160]-WHITBOURNE-WHITBOURNE-LEYSTERS 8INCH-POLE FARM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 0.88762 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 1994.9435 | 5
1470 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 54.8185 | 5.9763 | 2.5 | 139.1% | +/- 50% | OVER | 109.0189 | 1
1471 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-ELAN_/_BUILTH-BUILTH-BUILTH WELLS-BUILTH TO ABERDW | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 7.6629 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 404.3878 | 3
1472 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-ELAN_/_BUILTH-ELAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 13.0607 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 118.6311 | 1
1473 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 8.6012 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 231.6057 | 2
1474 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL-WEOBLEY NORTH-DILWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 1.2778 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 1559.0283 | 5
1475 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__SOUTH_BROOMY_HILL_ | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 11.5111 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 134.6009 | 2
1476 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 11.3218 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 156.4009 | 2
1477 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_SW__RISCA__ABERCARN-RHIWDERIN TO DUFFRYN SR OUT TDMA-RHIWDERIN TO DUFFRYN S.R. | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 1.6884 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 1442.0822 | 5
1478 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-CEFN PENDEGAR REDUCED DMA-CEFN PENDEGAR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 2.7659 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 960.3169 | 4
1479 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-CROSS ASH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 6.9629 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 222.5226 | 2
1480 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-USK MARKET ST AND DAVINGTON HOUSE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 2.9089 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 684.8327 | 4
1481 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-USK MARKET ST AND DAVINGTON HOUSE-GWERNESNEY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 5.1911 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 639.5896 | 4
1482 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 20.0599 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 99.3066 | 1
1483 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 16.0013 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 110.6623 | 1
1484 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(120,160]-NORTH_ERYRI_/_YNYS_MON-EAST_ANGLESEY_CEFNI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 16.5842 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 120.1196 | 1
1485 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(160,320]-NORTH_ERYRI_/_YNYS_MON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (160,320] | 3.9993 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 387.4169 | 3
1486 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 33.5952 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 85.6508 | 1
1487 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-CLWYD_COASTAL-ABERGELE__RHYL_GLASCOED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 23.6503 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 84.2309 | 1
1488 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-CLWYD_COASTAL-PRESTATYN_GLASCOED__TRECASTELL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 13.7104 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 129.1537 | 2
1489 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-EAST_ANGLESEY_CEFNI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 41.7554 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 63.6113 | 1
1490 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 39.1894 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 39.5361 | 1
1491 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-COEDEN TO LLANFAETHLU-RHYDWYN BOOSTER | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 3.5318 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 689.3812 | 4
1492 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm |  | 15.9112 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 125.1998 | 2
1493 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (0,70] | 8.8769 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 174.5434 | 2
1494 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-PEMBROKESHIRE-BOLTON_HILL-BRAWDY ST DAVIDS-ST DAVIDS LOW PRES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (120,160] | 2.0577 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 968.1347 | 4
1495 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-HAFOD LLECHRYD-LECHRYD VILLIAGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 3.115 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 781.64 | 4
1496 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 16.8454 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 131.3968 | 2
1497 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 51.9944 | 3.7628 | 2.5 | 50.51% | +/- 50% | OVER | 72.3698 | 1
1498 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAPEL_DEWI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm | (70,120] | 17.595 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 150.9586 | 2
1499 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm |  | 8.477 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 208.8887 | 2
1500 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 8.8347 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 275.5921 | 3
1501 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-PENARTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 2.3452 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 943.8199 | 4
1502 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 8.096 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 273.3966 | 3
1503 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 12.885 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 188.9613 | 2
1504 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 10.42 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 169.9366 | 2
1505 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(0,70]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RASSAU__SIRHOWY_VALLEY-TY FRY SR-TY FRY OUTLET TO BLACKWOOD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (0,70] | 0.17062 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 10378.2153 | 5
1506 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 17.4756 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 189.9874 | 2
1507 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(120,160]-HEREFORD_C.U._AREA-HEREFORD__SOUTH_BROOMY_HILL_ | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 6.7581 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 360.2722 | 3
1508 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(120,160]-VOWCHURCH-VOWCHURCH-KINGSTONE SR-CLEHONGER | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 2.6616 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 582.1293 | 4
1509 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(160,320]-BRECON_/_PORTIS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (160,320] | 1.375 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 1287.8129 | 5
1510 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(160,320]-ELAN_/_BUILTH-ELAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (160,320] | 3.5806 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 432.7235 | 3
1511 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 39.8578 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 83.2996 | 1
1512 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-ELAN_/_BUILTH-ELAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 27.6563 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 56.0234 | 1
1513 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-ELAN_/_BUILTH-ELAN-ELAN-BWLCH-Y-SARNAU S.R. | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 1.82 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 851.3004 | 4
1514 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-ELAN_/_BUILTH-ELAN-NEUADD SOUTH-HOWEY-BUILTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 3.5676 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 496.3448 | 3
1515 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 24.0168 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 64.5132 | 1
1516 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 13.2373 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 133.7696 | 2
1517 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-LLYSWEN-LLYSWEN-HAY ON WYE-DORSTONE OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 1.3618 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 1137.7857 | 5
1518 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-LLYSWEN-LLYSWEN-LLYSWEN TO LLANSTEPHAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 17.7308 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 124.835 | 1
1519 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-PILLETH-PILLETH_KNIGHTON__BLEDDFA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 10.258 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 215.7759 | 2
1520 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-PILLETH-PILLETH_KNIGHTON__BLEDDFA-BEGGARS BUSH TO KNOWLE HILL TDMA-KINNERTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 5.4534 | 3.9842 | 2.5 | 59.37% | +/- 50% | OVER | 730.5888 | 4
1521 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-PILLETH-PILLETH_KNIGHTON__BLEDDFA-WHITTON BEGGARS BUSH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 13.9832 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 174.1207 | 2
1522 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-PILLETH-PILLETH_KNIGHTON__BLEDDFA-WOODHOUSE-KNIGHTON-KNUCKLAS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 1.5122 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 1170.9565 | 5
1523 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-USK MARKET ST AND DAVINGTON HOUSE-LLANDENNY MAIN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 2.7708 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 798.8361 | 4
1524 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-WHITBOURNE-WHITBOURNE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 14.4172 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 138.1739 | 2
1525 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-WHITBOURNE-WHITBOURNE-WARRENWOOD-STOKE LACY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 11.9691 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 147.943 | 2
1526 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (0,70] | 35.262 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 69.0479 | 1
1527 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(0,70]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (0,70] | 27.9716 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 71.2181 | 1
1528 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(0,70]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-CERRIG-BRYN GLAS SRV O/LET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (0,70] | 3.0293 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 511.4788 | 4
1529 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(0,70]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT & GORSWEN MINOR-EGLWYSBACH 85 LLYN CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (0,70] | 1.8691 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 1657.9436 | 5
1530 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 29.4033 | 3.5415 | 2.5 | 41.66% | +/- 50% | PASS | 120.4453 | 1
1531 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 13.5904 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 162.8665 | 2
1532 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160]-LLEYNHARLECH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 7.6377 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 202.8633 | 2
1533 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160]-NORTH_ERYRI_/_YNYS_MON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 30.3214 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 65.6991 | 1
1534 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(160,320] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (160,320] | 8.9367 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 272.447 | 3
1535 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(160,320]-ALWEN_/_DEE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (160,320] | 7.3981 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 329.1063 | 3
1536 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(160,320]-ALWEN_/_DEE-DENBIGH_ALWEN-MEIFOD-1104 FOELAS (G10) | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (160,320] | 3.1007 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 571.0806 | 4
1537 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(160,320]-ALWEN_/_DEE-FLINT__CONNAHS_QUAY_BRETTON-ASTON 9 INCH-ASTON FROM PLOUGHINN. | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (160,320] | 0.807 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 2468.5083 | 5
1538 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(160,320]-ALWEN_/_DEE-FLINT__CONNAHS_QUAY_BRETTON-HAWARDEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (160,320] | 3.2616 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 678.628 | 4
1539 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(160,320]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (160,320] | 15.9202 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 125.129 | 2
1540 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(160,320]-NORTH_ERYRI_/_YNYS_MON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (160,320] | 4.0195 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 495.6052 | 3
1541 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(160,320]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (160,320] | 10.8497 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 183.6072 | 2
1542 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 29.5693 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 82.3411 | 1
1543 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 39.6473 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 39.0796 | 1
1544 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-ALWEN TO BWLCH TRUNK | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 5.4803 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 282.7223 | 3
1545 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 22.8349 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 106.6251 | 1
1546 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-BLAENAU_FFESTINIOG-BLAENAU_GARREGLWYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 16.1228 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 96.0999 | 1
1547 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-CLWYD_COASTAL-ABERGELE__RHYL_GLASCOED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 46.7691 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 42.594 | 1
1548 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-CLWYD_COASTAL-PRESTATYN_GLASCOED__TRECASTELL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 11.4741 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 154.3258 | 2
1549 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-CLWYD_COASTAL-PRESTATYN_GLASCOED__TRECASTELL-DYSERTH-0805 DYSERTHGRAVITY (R80) | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 0.75678 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 2047.3531 | 5
1550 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 20.164 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 98.7942 | 1
1551 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-CERRIG | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 4.0995 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 377.9448 | 3
1552 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-LLYSFAEN-0059 BRYN Y PIN(R00) | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 10.1042 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 197.1547 | 2
1553 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 17.4503 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 114.1575 | 1
1554 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-PENRHYNDEUDRAETH-PENRHYD LLANFROTHEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 0.82214 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 2153.8166 | 5
1555 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 30.3623 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 65.6105 | 1
1556 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-EAST_ANGLESEY_CEFNI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 37.6667 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 41.1345 | 1
1557 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 52.6369 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 46.2559 | 1
1558 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-SOUTH_MEIRIONNYDD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 11.9533 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 166.6556 | 2
1559 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm |  | 36.6301 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 60.4265 | 1
1560 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SYNOD INN LLANARTH-LLANARTH TO ABERAERON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (0,70] | 1.1288 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 1960.9357 | 5
1561 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(0,70]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (0,70] | 9.5909 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 161.5486 | 2
1562 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 12.3438 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 161.3829 | 2
1563 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(120,160]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 21.5387 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 143.871 | 2
1564 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(120,160]-PEMBROKESHIRE-BOLTON_HILL-BRAWDY ST DAVIDS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 1.7547 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 1135.2948 | 5
1565 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(120,160]-PEMBROKESHIRE-BOLTON_HILL-TEMPLETON TO MARTLETWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 4.8237 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 321.2042 | 3
1566 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 25.5916 | 4.2055 | 2.5 | 68.22% | +/- 50% | OVER | 164.3317 | 2
1567 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-CAPEL_DEWI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 4.1435 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 373.9372 | 3
1568 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-CAPEL_DEWI-EBENEZER SR OUTLETS-FOEL RES TO EBENEEZER RES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 1.2998 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 1192.0272 | 5
1569 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-CAPEL_DEWI-FOEL TO MAENIEUAN-FOEL RES TALOG-ABERNANT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (120,160] | 3.0796 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 862.4927 | 4
1570 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(160,320]-TYWI_C.U._AREA-CAPEL_DEWI-PENLLAIN TO NIMPWLL-PENLLAIN RES TO NIMPWLL RES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (160,320] | 4.7147 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 657.27 | 4
1571 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 40.5141 | 4.8695 | 2.5 | 94.78% | +/- 50% | OVER | 120.1938 | 1
1572 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-CROSSROADS TO CRUGIAU AND TREGAMMON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 23.8648 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 102.0236 | 1
1573 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 38.0996 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 58.0958 | 1
1574 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-MAESTIR TO BRYNGARREG-BRYNCARREG RES OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 13.9386 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 206.438 | 2
1575 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 26.7185 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 99.411 | 1
1576 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 27.5234 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 80.42 | 1
1577 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL-TEMPLETON TO MARTLETWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 9.8366 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 180.0159 | 2
1578 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 37.6847 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 82.2296 | 1
1579 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 16.2038 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 109.2794 | 1
1580 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAERAU__YSTRADFELLTE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 15.3355 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 101.0335 | 1
1581 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAPEL_DEWI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 33.3032 | 2.6561 | 2.5 | 6.245% | +/- 50% | PASS | 79.7555 | 1
1582 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAPEL_DEWI-FOEL TO MAENIEUAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 9.0296 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 171.5908 | 2
1583 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAPEL_DEWI-STONECUTTER TALOG ABERNANT-ABERNANT BPT OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 7.1855 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 400.4529 | 3
1584 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CRAY__CLYDACH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 16.9479 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 182.8421 | 2
1585 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-DAFEN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 14.6098 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 121.202 | 1
1586 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-LLANELLI_FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 11.7282 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 150.9819 | 2
1587 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm | (70,120] | 29.5487 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 67.417 | 1
1588 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN | PLASTIC_PVC |  |  | DIAM_LT_320 | <=320mm |  | 35.3402 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 56.3688 | 1
1589 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_EAST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B14_1980 | DIAM_LT_320 | <=320mm | (70,120] | 5.1021 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 347.0627 | 3
1590 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_HEATH_&_LLANISHEN-UPPER AND LOWER GRAIG | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | PLASTIC_PVC | 1961_1980 | B14_1980 | DIAM_LT_320 | <=320mm | (70,120] | 5.9732 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 259.3928 | 3
1591 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1961_1980-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1961_1980 | B14_1980 | DIAM_LT_320 | <=320mm | (70,120] | 7.3203 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 272.1329 | 3
1592 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1961_1980-NORTHERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | PLASTIC_PVC | 1961_1980 | B14_1980 | DIAM_LT_320 | <=320mm |  | 25.6375 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 94.969 | 1
1593 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1961_1980-NORTHERN-NONE-(0,70]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-LLYN CONWY MINOR-NEBO RES 0/LET CAPEL GARMON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B14_1980 | DIAM_LT_320 | <=320mm | (0,70] | 0.62926 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 3165.758 | 5
1594 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1961_1980-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1961_1980 | B14_1980 | DIAM_LT_320 | <=320mm | (70,120] | 41.7981 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 37.0686 | 1
1595 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1961_1980-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | PLASTIC_PVC | 1961_1980 | B14_1980 | DIAM_LT_320 | <=320mm |  | 20.7475 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 74.6789 | 1
1596 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1981_2000-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | PLASTIC_PVC | 1981_2000 | B14_1980 | DIAM_LT_320 | <=320mm |  | 7.3987 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 269.2498 | 3
1597 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1981_2000-EASTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1981_2000 | B14_1980 | DIAM_LT_320 | <=320mm | (120,160] | 7.3019 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 272.8176 | 3
1598 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1981_2000-NORTHERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | PLASTIC_PVC | 1981_2000 | B14_1980 | DIAM_LT_320 | <=320mm |  | 59.0725 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 33.7227 | 1
1599 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1981_2000-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1981_2000 | B14_1980 | DIAM_LT_320 | <=320mm | (70,120] | 68.6514 | 5.5336 | 2.5 | 121.3% | +/- 50% | OVER | 80.6039 | 1
1600 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1981_2000-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1981_2000 | B14_1980 | DIAM_LT_320 | <=320mm | (70,120] | 35.3496 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 43.8308 | 1
1601 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1981_2000-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1981_2000 | B14_1980 | DIAM_LT_320 | <=320mm | (70,120] | 21.2098 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 83.4869 | 1
1602 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1981_2000-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1981_2000 | B14_1980 | DIAM_LT_320 | <=320mm | (70,120] | 53.5777 | 3.0988 | 2.5 | 23.95% | +/- 50% | PASS | 57.8375 | 1
1603 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1981_2000-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | PLASTIC_PVC | 1981_2000 | B14_1980 | DIAM_LT_320 | <=320mm |  | 52.3607 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 29.5909 | 1
1604 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1981_2000-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1981_2000 | B14_1980 | DIAM_LT_320 | <=320mm | (120,160] | 59.1171 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 41.1856 | 1
1605 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1981_2000-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1981_2000 | B14_1980 | DIAM_LT_320 | <=320mm | (70,120] | 163.0006 | 6.4189 | 2.5 | 156.8% | +/- 50% | OVER | 39.3799 | 1
1606 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1981_2000-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1981_2000 | B14_1980 | DIAM_LT_320 | <=320mm | (70,120] | 49.0382 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 49.6505 | 1
1607 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | PLASTIC_PVC | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm |  | 45.0118 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 39.3395 | 1
1608 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-CENTRAL-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (120,160] | 47.0148 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 32.9556 | 1
1609 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-CENTRAL-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (70,120] | 69.9955 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 31.6225 | 1
1610 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-CENTRAL-NONE-(70,120]-CYNON-ABERDARE_HIRWAUN__PONSTICILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (70,120] | 14.5531 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 106.4653 | 1
1611 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (70,120] | 25.992 | 1.9921 | 2.5 | -20.32% | +/- 50% | PASS | 76.6422 | 1
1612 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (120,160] | 75.2 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 23.5471 | 1
1613 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (70,120] | 116.0447 | 4.6482 | 2.5 | 85.93% | +/- 50% | OVER | 40.0553 | 1
1614 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (70,120] | 21.2558 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 72.8932 | 1
1615 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-NORTHERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | PLASTIC_PVC | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm |  | 41.9468 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 42.214 | 1
1616 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (70,120] | 145.3049 | 3.7628 | 2.5 | 50.51% | +/- 50% | OVER | 25.8961 | 1
1617 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | PLASTIC_PVC | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm |  | 91.3193 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 16.9668 | 1
1618 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (120,160] | 96.6922 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 25.1806 | 1
1619 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-WESTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (70,120] | 176.8226 | 3.7628 | 2.5 | 50.51% | +/- 50% | OVER | 21.2802 | 1
1620 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (70,120] | 65.5636 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 27.008 | 1
1621 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (70,120] | 146.601 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 22.6475 | 1
1622 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (70,120] | 58.8033 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 26.3488 | 1
1623 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAPEL_DEWI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (70,120] | 76.9935 | 2.4348 | 2.5 | -2.609% | +/- 50% | PASS | 31.6231 | 1
1624 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CRAY__CLYDACH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (70,120] | 40.5199 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 81.9386 | 1
1625 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CRAY__CLYDACH-CAEHOPKIN AND PENYCAE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | PLASTIC_PVC | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (70,120] | 4.6082 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 336.2233 | 3
1626 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-LLANELLI_FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (70,120] | 71.6533 | 2.8775 | 2.5 | 15.1% | +/- 50% | PASS | 40.1581 | 1
1627 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PENCOED__BRIDGEND_VALLEYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1981_2000 | B15_1990 | DIAM_LT_320 | <=320mm | (70,120] | 27.7444 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 63.8235 | 1
1628 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B16_2000-2001_2020 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | PLASTIC_PVC | 2001_2020 | B16_2000 | DIAM_LT_320 | <=320mm |  | 68.5366 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 25.8364 | 1
1629 | DIAM_LT_320-STEEL-<=320mm | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY | STEEL |  |  | DIAM_LT_320 | <=320mm |  | 40.1967 | 3.9842 | 2.5 | 59.37% | +/- 50% | OVER | 99.1169 | 1
1630 | DIAM_LT_320-STEEL-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | STEEL | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (120,160] | 3.3018 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 670.373 | 4
1631 | DIAM_LT_320-STEEL-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(160,320]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_SW__RISCA__ABERCARN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | STEEL | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (160,320] | 4.8201 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 367.3627 | 3
1632 | DIAM_LT_320-STEEL-<=320mm-B07_1910-1901_1920-WESTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | STEEL | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm |  | 8.4544 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 261.8074 | 3
1633 | DIAM_LT_320-STEEL-<=320mm-B07_1910-1901_1920-WESTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | STEEL | 1901_1920 | B07_1910 | DIAM_LT_320 | <=320mm | (120,160] | 5.6235 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 275.5216 | 3
1634 | DIAM_LT_320-STEEL-<=320mm-B09_1930-1921_1940 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | STEEL | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm |  | 8.6194 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 179.7577 | 2
1635 | DIAM_LT_320-STEEL-<=320mm-B09_1930-1921_1940-WESTERN-BITUMEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | STEEL | 1921_1940 | B09_1930 | DIAM_LT_320 | <=320mm |  | 17.8157 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 86.9683 | 1
1636 | DIAM_LT_320-STEEL-<=320mm-B11_1950-1941_1960 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | STEEL | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm |  | 18.8485 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 93.9459 | 1
1637 | DIAM_LT_320-STEEL-<=320mm-B11_1950-1941_1960-WESTERN-BITUMEN-(70,120]-TYWI_C.U._AREA-BRYNGWYN-TWYNLLANAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | STEEL | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (70,120] | 6.1723 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 251.0239 | 3
1638 | DIAM_LT_320-STEEL-<=320mm-B11_1950-1941_1960-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | STEEL | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm |  | 11.9505 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 148.1737 | 2
1639 | DIAM_LT_320-STEEL-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(160,320]-PEMBROKESHIRE-BOLTON_HILL-TEMPLETON TO MARTLETWY-CROSSHANDS VILLAGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | STEEL | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (160,320] | 4.0694 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 435.1336 | 3
1640 | DIAM_LT_320-STEEL-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(160,320]-PEMBROKESHIRE-BOLTON_HILL-TTM OFF PENT PUMPS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | STEEL | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (160,320] | 8.0372 | 2.2134 | 2.5 | -11.46% | +/- 50% | PASS | 275.3978 | 3
1641 | DIAM_LT_320-STEEL-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(160,320]-PEMBROKESHIRE-PRESELI_SUPPLY-TENBY MAIN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | STEEL | 1941_1960 | B11_1950 | DIAM_LT_320 | <=320mm | (160,320] | 9.2119 | 3.3201 | 2.5 | 32.81% | +/- 50% | PASS | 360.4175 | 3
1642 | DIAM_LT_320-STEEL-<=320mm-B12_1960-1961_1980 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | STEEL | 1961_1980 | B12_1960 | DIAM_LT_320 | <=320mm |  | 27.26 | 1.7707 | 2.5 | -29.17% | +/- 50% | PASS | 64.9575 | 1
1643 | DIAM_LT_320-STEEL-<=320mm-B13_1970-1961_1980-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | STEEL | 1961_1980 | B13_1970 | DIAM_LT_320 | <=320mm |  | 1.7796 | 1.5494 | 2.5 | -38.02% | +/- 50% | PASS | 870.624 | 4
[8 empty] | Total | 27875.2 | 4033.4 | 4049 | -0.3853% | +/- 10% | PASS

## Cumulative Plot
Shaded by Condition Grade
Ranked on Burst Rate
COHORT_ID | Average of bursts_year | Sum of LENGTH_KM | Cumulative Length km | Average of bursts_1000km_year | Cumulative Bursts/Yr
DIAM_LT_320-ALKATHENE-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(0,70]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_EAST-BRYN CELYN-BRYN CELYN | 1.5494 | 0.03781 | 0.03781 | 40978.149 | 1.5494
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-CONWY-GYFFIN-CASTLE VIEW | 1.5494 | 0.050541 | 0.088352 | 30656.1545 | 3.0988
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-POLYURETHANE-(0,70]-BRECON_/_PORTIS-PORTIS-PORTIS LOW-LLANDEW LINE | 2.2134 | 0.14504 | 0.23339 | 15260.9132 | 5.3122
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-PORTHYRHYD TO CEFNEITHIN-FOELGASTELL | 1.9921 | 0.13471 | 0.3681 | 14788.1964 | 7.3043
DIAM_LT_320-AC-<=320mm-B14_1980-1961_1980-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-HAFOD FELINWYNT-HAFOD FELINWYNT 5 | 2.2134 | 0.15081 | 0.51891 | 14677.0597 | 9.5177
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-BRYNGWYN-TRAPP BULK EXPORT-CARMARTHEN RD. LLANDEILO RD. | 3.0988 | 0.25877 | 0.77767 | 11975.2808 | 12.6165
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-LLANWNEN TO LLANLLWNI-LLANYBYTHER RES OUTLET | 4.6482 | 0.39386 | 1.1715 | 11801.6539 | 17.2647
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(160,320]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_HEATH_&_LLANISHEN-BLACKOAK ROAD-BLACKOAK ROAD | 7.9683 | 0.7559 | 1.9274 | 10541.5364 | 25.2331
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(0,70]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RASSAU__SIRHOWY_VALLEY-TY FRY SR-TY FRY OUTLET TO BLACKWOOD | 1.7707 | 0.17062 | 2.0981 | 10378.2153 | 27.0038
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-PENRHYNDEUDRAETH-PENRHYD LLANFROTHEN | 2.4348 | 0.23856 | 2.3366 | 10205.9932 | 29.4386
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-CROSS ASH-THE BOOT NEWCASTLE | 2.6561 | 0.28281 | 2.6194 | 9391.9137 | 32.0947
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-EASTERN-NONE-(0,70]-ELAN_/_BUILTH-BUILTH | 1.5494 | 0.16572 | 2.7852 | 9349.2358 | 33.6441
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-TREFRIW-TREFRIW SERVICE RES. O/LET. | 1.5494 | 0.17521 | 2.9604 | 8843.0359 | 35.1935
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(0,70]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-RHOSGADFAN | 1.5494 | 0.17869 | 3.1391 | 8670.9028 | 36.7429
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-BRYNGWYN-BETTWS-MAESQUERRE | 4.8695 | 0.56229 | 3.7013 | 8660.1696 | 41.6125
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-WAUNFAWR-WAUNFAWR NEW | 3.0988 | 0.36525 | 4.0666 | 8484.0953 | 44.7113
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE | 1.5494 | 0.18787 | 4.2545 | 8247.0154 | 46.2607
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(0,70]-TALYBONT-ABERGAVENNY__CWMTILLERY-PONTYPOOL TDMA-AREA FED BY SUB SUPPLY SYSTEM | 1.5494 | 0.1904 | 4.4449 | 8137.7708 | 47.81
DIAM_LT_320-ALKATHENE-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-PORTHMADOG WEST-TYDDYN LLWYN | 1.9921 | 0.25081 | 4.6957 | 7942.6177 | 49.8021
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-SOUTH_MEIRIONNYDD-DOLGELLAU_PEN_Y_CEFN-PENYCEFN GAP-PENMAENPOOL | 4.2055 | 0.54572 | 5.2414 | 7706.3579 | 54.0076
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(0,70]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-CERRIG-POINT D TO CERRIG | 5.7549 | 0.75421 | 5.9956 | 7630.3853 | 59.7626
DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-WESTERN-CEMENT_MORTAR-(120,160]-TYWI_C.U._AREA-DAFEN__FELINDRE-FRAMPTON OUTLET RED DMA-PRINCESS STREET | 1.9921 | 0.2621 | 6.2577 | 7600.3595 | 61.7546
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(0,70]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-WAENHIR-PENTIR | 1.5494 | 0.20736 | 6.4651 | 7471.9384 | 63.304
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-PENRHYNDEUDRAETH-PENRHYD LLANFROTHEN | 1.7707 | 0.23962 | 6.7047 | 7389.8561 | 65.0748
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-MAESTIR TO BRYNGARREG-MAESTIR TO BRYNGARREG | 1.5494 | 0.21322 | 6.9179 | 7266.5871 | 66.6242
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE-MYNYDD NEWYDD TO FFOREST FACH-IVORITES | 1.5494 | 0.2168 | 7.1347 | 7146.8371 | 68.1736
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SKEWEN__LLANDARCY_FELINDRE__CRAY-EAST SWANSEA DOCKS-BURROWS ENTRANCE | 2.2134 | 0.32472 | 7.4594 | 6816.3214 | 70.387
DIAM_LT_320-OTHER-<=320mm-B12_1960 | 1.5494 | 0.2377 | 7.6971 | 6518.2684 | 71.9364
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SYNOD INN LLANARTH-LLANARTH VILLAGE | 2.2134 | 0.34019 | 8.0373 | 6506.4868 | 74.1498
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-BUTLINS-LLANGYBI - BODOWEN | 3.5415 | 0.57811 | 8.6154 | 6125.9846 | 77.6913
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-BRYNGWYN-SALEM SR OUTLET-SALEM LLANFYNYDD | 6.4189 | 1.0648 | 9.6803 | 6028.1478 | 84.1103
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-CWMYSTRADLLYN GAP-CENIN | 4.2055 | 0.7125 | 10.3928 | 5902.4448 | 88.3158 |  | bursts | Cumulative bursts share | length | Cumulative length share
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF-PENTREBANE NORTH-PENTREBANE NORTH | 1.5494 | 0.2747 | 10.6675 | 5640.4063 | 89.8652 | Grade 5 | 763.6327 | 18.93% | 390.4311 | 1.401%
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PENDINE-THREE LORDS OUTLET-THREE LORDS (BROADWAY/LAUGHARN | 1.7707 | 0.32191 | 10.9894 | 5500.7108 | 91.6359 | Grade 4 | 1418.4482 | 35.17% | 1331.9442 | 4.778%
DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-BETTWS LLANGYBI AND LLANDDEWI BREFI-BETTWS BLEDRWS | 3.0988 | 0.56634 | 11.5557 | 5471.6476 | 94.7347 | Grade 3 | 2437.2892 | 60.43% | 4338.3487 | 15.56%
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-CAERAU__YSTRADFELLTE-RESOLVEN SR OUTLET-GLYN CASTLE | 2.6561 | 0.48646 | 12.0422 | 5460.0524 | 97.3908 | Grade 2 | 3262.898 | 80.9% | 8881.0294 | 31.86%
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-BRYNGWYN-TWYNLLANAN-BRYNGLAS | 1.9921 | 0.37396 | 12.4161 | 5327.022 | 99.3829 | Grade 1 | 4033.4 | 100% | 27875.2 | 100%
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-MAESTIR TO BRYNGARREG-BRYNCARREG RES OUTLET | 1.9921 | 0.37557 | 12.7917 | 5304.2001 | 101.375
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-PENARTH-ST TEILOS PENDINE AND SKOMER RD | 1.5494 | 0.29837 | 13.0901 | 5192.8793 | 102.9244
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-BRYNGWYN-TRAPP BULK EXPORT-PENYBANK/NANTGARDEIG 6 INCH | 2.8775 | 0.5771 | 13.6672 | 4986.0489 | 105.8019
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SYNOD INN LLANARTH-LLANARTH TO ABERAERON | 3.9842 | 0.80227 | 14.4694 | 4966.1365 | 109.786
DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-NORTH_CEREDIGION-ABERYSTWYTH_BONTGOCH__LOVESGROVE-CEFNLLAN SR OUTLETS-ST DAVIDS RD | 1.7707 | 0.37258 | 14.842 | 4752.6859 | 111.5568
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(0,70]-SOUTH_MEIRIONNYDD-DOLGELLAU_PEN_Y_CEFN-PENYCEFN TRUNK-GANLLWYN RES INLET | 1.5494 | 0.32803 | 15.17 | 4723.2955 | 113.1062
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-PEN TO LLANFAIRFECHAN TRUNK-AREA FED BY S/SUPPLY 30C30A07 | 1.9921 | 0.42211 | 15.5921 | 4719.3881 | 115.0983
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-EASTERN-NONE-(0,70]-ELAN_/_BUILTH-BUILTH-BUILTH WELLS-AREA FEED BY 1T810231 | 5.9763 | 1.279 | 16.8711 | 4672.6662 | 121.0745
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(0,70]-TALYBONT-ABERGAVENNY__CWMTILLERY-PONTYPOOL TDMA-AREA FED BY SUB SUPPLY SYSTEM | 4.2055 | 0.91095 | 17.7821 | 4616.6183 | 125.28
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(0,70]-ALWEN_/_DEE-DENBIGH_ALWEN-MEIFOD-1104 FOELAS (G10) | 3.0988 | 0.68782 | 18.4699 | 4505.2726 | 128.3788
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-DEINIOLEN CEFN COCH-ASHTON HOUSE | 2.8775 | 0.65502 | 19.1249 | 4392.9363 | 131.2563
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-EASTERN-NONE-(0,70]-ELAN_/_BUILTH-BUILTH-BUILTH WELLS-BUILTH TO CILMERY | 1.5494 | 0.35372 | 19.4786 | 4380.2431 | 132.8057
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-BEUDY MAWR-BEUDY MAWR | 3.5415 | 0.82088 | 20.2995 | 4314.247 | 136.3472
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT & GORSWEN MINOR-LLANDDOGED | 3.7628 | 0.87424 | 21.1738 | 4304.1014 | 140.11
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-DRUIDS STONE-DRUID'S STONE | 1.7707 | 0.41905 | 21.5928 | 4225.5891 | 141.8808
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL-TEMPLETON TO TAVERNSPITE-LLANTEG OFF T/SPITE | 2.2134 | 0.524 | 22.1168 | 4224.0656 | 144.0942
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT VALLEY TRUNK-AREA FED BY S/SUPPLY 3SC20M18 | 4.4269 | 1.0697 | 23.1865 | 4138.5613 | 148.521
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RHYMNEY__BARGOED-RHYMNEY SOUTH-ABERTYSSWG | 2.4348 | 0.59805 | 23.7845 | 4071.1603 | 150.9558
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-PENDINE-BRANDY HILL TO ST. CLEARS-THE SMITHY | 5.7549 | 1.4686 | 25.2531 | 3918.6108 | 156.7107
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(70,120]-BARMOUTH-BARMOUTH_-_HARLECH-DYFFRYN TALYBONT LLANBEDR-TALYBONT VILLAGE | 2.6561 | 0.69619 | 25.9493 | 3815.2261 | 159.3668
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT VALLEY GAP-MAENAN RISING | 3.0988 | 0.81406 | 26.7634 | 3806.5874 | 162.4656
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-SOUTH_MEIRIONNYDD-DOLGELLAU_PEN_Y_CEFN-PENYCEFN GAP-PENCEFN ROAD | 1.5494 | 0.41137 | 27.1748 | 3766.4094 | 164.015
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-MAESTWYNOG-PANTYBRYN CILYCWM | 3.3201 | 0.8953 | 28.0701 | 3708.3945 | 167.3352
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-PENWCH SERVICE RES OUTLET-MAESBEIDIOG TO LLANGWYRYFON | 2.2134 | 0.59785 | 28.6679 | 3702.2863 | 169.5486
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__RUMNEY-LLANRUMNEY AVENUE-NEWPORT ROAD RUMNEY | 1.5494 | 0.42346 | 29.0914 | 3658.9123 | 171.098
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-PENDINE-BRANDY HILL TO ST. CLEARS-PWLL TRAPP | 3.3201 | 0.93087 | 30.0223 | 3566.6917 | 174.4181
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-PENWCH SERVICE RES OUTLET-PENUWCH TO BWLCHLLAN | 1.5494 | 0.43483 | 30.4571 | 3563.1939 | 175.9675
DIAM_LT_320-ALKATHENE-<=320mm-B12_1960-1941_1960-EASTERN-NONE-(0,70]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_SW__RISCA__ABERCARN-MICHAELSTONE TO MARSHFIELD SOUTH-MICHAELSTONE | 1.5494 | 0.43602 | 30.8931 | 3553.5344 | 177.5169
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-MYNYDD CROGWY TO EGLWYSWRW AND CRYMYCH-POSTGWYN CRYMYCH | 3.0988 | 0.88567 | 31.7788 | 3498.8277 | 180.6157
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-NEWQUAY-SYNOD INN TO NEW QUAY 6 | 7.083 | 2.0653 | 33.844 | 3429.5888 | 187.6987
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE-CLASE SR OUTLET TO GWYROSEDD-LLANGYFELACH | 1.7707 | 0.52356 | 34.3676 | 3382.126 | 189.4695
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-BRYNGWYN-SALEM SR OUTLET-SALEM VILLAGE METER | 11.2885 | 3.3562 | 37.7238 | 3363.5009 | 200.7579
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-CEFN BRYN HOUSE-CEFN BRYN HOUSE | 2.2134 | 0.65943 | 38.3832 | 3356.5986 | 202.9714
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(120,160]-PONTSTICILL_LOW_LEVEL-CAERPHILLY-MORNINGTON MEADOWS-MORNINGTON MEADOW | 1.7707 | 0.52768 | 38.9109 | 3355.7317 | 204.7421
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(0,70]-ELAN_/_BUILTH-BUILTH-GARTH SR-TIRABAD | 2.4348 | 0.72706 | 39.6379 | 3348.7765 | 207.1769
DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(0,70]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH-CAPEL SEION LLANRHYSTUD-LLANFARIAN VILLAGE | 1.9921 | 0.60058 | 40.2385 | 3316.958 | 209.169
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(0,70]-ELAN_/_BUILTH-BUILTH-GARTH SR-GARTH-BEALAH | 2.2134 | 0.67056 | 40.9091 | 3300.8639 | 211.3824
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-RHOSHILL TO CROSSROADS-PENYBRYN TO CILGERRAN WD | 3.0988 | 0.96657 | 41.8756 | 3205.9612 | 214.4812
DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1961_1980-NORTHERN-NONE-(0,70]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-LLYN CONWY MINOR-NEBO RES 0/LET CAPEL GARMON | 1.9921 | 0.62926 | 42.5049 | 3165.758 | 216.4733
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAPEL_DEWI | 1.5494 | 0.50267 | 43.0076 | 3082.3542 | 218.0227
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-WHITBOURNE-WHITBOURNE-RIDGEWAY STIFFORDS BRIDGE-STIFFORDS BRIDGE | 1.7707 | 0.5745 | 43.5821 | 3082.234 | 219.7934
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-LLANELLEN 6INCH-LLANELLEN BRIDGE | 4.6482 | 1.5261 | 45.1082 | 3045.8136 | 224.4416
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-WHITBOURNE-UPPER_SAPEY-LEYSTER SR 3" OUTLET GAP-THE FOX(SEVERN TRENT) | 3.0988 | 1.0203 | 46.1285 | 3037.1692 | 227.5404
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(0,70]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | 1.7707 | 0.58756 | 46.716 | 3013.7165 | 229.3112
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-EPOXY_RESIN-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL-MALVERN RD-LEDBURY RES MALVERN RD | 1.5494 | 0.51598 | 47.232 | 3002.8483 | 230.8606
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-BRYNGWYN | 1.9921 | 0.66632 | 47.8983 | 2989.6891 | 232.8527
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-RHOSHILL TO CROSSROADS-PENYBRYN TO CARDIGAN | 5.3122 | 1.7856 | 49.6839 | 2975.1104 | 238.1649
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-MYNYTHO WILLIS-SAETHON BACH MYNYTHO PUMPED | 1.9921 | 0.67435 | 50.3582 | 2954.0812 | 240.157
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-WHITBOURNE-WHITBOURNE-WARRENWOOD-UPPER SAPEY METER | 1.7707 | 0.6001 | 50.9583 | 2950.7468 | 241.9277
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(160,320]-PEMBROKESHIRE-BOLTON_HILL-ORIELTON TO WOGASTON-ORIELTON WOGASTON | 8.8537 | 3.0463 | 54.0047 | 2906.3447 | 250.7814
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-CROSSROADS TO CRUGIAU AND TREGAMMON-TREGAMMON WD | 6.6403 | 2.3846 | 56.3893 | 2784.6183 | 257.4217
DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PENCOED__BRIDGEND_VALLEYS-RED COW TO NANT ST EAST ALT-REVLON OAKWOOD | 1.5494 | 0.55881 | 56.9481 | 2772.667 | 258.9711
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(0,70]-ALWEN_/_DEE-DENBIGH_ALWEN-BYLCHAU HIGH-1008 BWLCHOUTLET(LLANNEFYDD) ( | 3.5415 | 1.2837 | 58.2318 | 2758.8174 | 262.5126
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-SOUTH_MEIRIONNYDD-DOLGELLAU_PEN_Y_CEFN-PENYCEFN GAP-BRITHDIR VILLAGE | 1.9921 | 0.73185 | 58.9637 | 2721.9719 | 264.5047
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-LLYN CONWY TRUNK-AREA FED BY S/SUPPLY 3SC70B08 | 1.9921 | 0.7372 | 59.7008 | 2702.2439 | 266.4968
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-EPOXY_RESIN-(120,160]-TYWI_C.U._AREA-CAPEL_DEWI-CARMARTHEN TOWN-CWMOERNANT - CARMS TOWN | 1.5494 | 0.59725 | 60.2981 | 2594.2108 | 268.0462
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON-HOLYWELL ST PHILOMENIA-ST.PHILOMENIAHOLYWELL. | 1.5494 | 0.59805 | 60.8962 | 2590.7349 | 269.5956
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RHYMNEY__BARGOED-WINDSOR HOTEL-THE GARTH ABERTRIDWR | 1.9921 | 0.77481 | 61.671 | 2571.0789 | 271.5876
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-NORTH_ERYRI_/_YNYS_MON-SOUTH_ANGLESEY_CWELLYN__MYNYDD-PENMYNYDD CADNANT GAERWEN | 1.7707 | 0.69039 | 62.3614 | 2564.8303 | 273.3584
DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-BRYN GWENALLT-CARMEL BOOSTER | 2.2134 | 0.86996 | 63.2313 | 2544.2914 | 275.5718
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-EPOXY_RESIN-(70,120]-RHONDDA-TYNYWAUN-BAGLAN STREET TO DR THOMAS-ROCK DRIVE GELLI | 1.5494 | 0.60898 | 63.8403 | 2544.2469 | 277.1212
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-CORWEN GAP-BETWS GG TYRPEG | 2.6561 | 1.0661 | 64.9064 | 2491.4625 | 279.7773
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-PENPARC SR TO CARDIGAN SR-PENPARC SOUTH | 5.0909 | 2.0532 | 66.9595 | 2479.5297 | 284.8682
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(160,320]-ALWEN_/_DEE-FLINT__CONNAHS_QUAY_BRETTON-ASTON 9 INCH-ASTON FROM PLOUGHINN. | 1.9921 | 0.807 | 67.7665 | 2468.5083 | 286.8603
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(70,120]-ELAN_/_BUILTH | 1.7707 | 0.71939 | 68.4859 | 2461.4429 | 288.631
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-BALA-BALA-COED TALOG OUTLET-PANT SAER OUTLETS NEW DMA | 2.2134 | 0.90111 | 69.3871 | 2456.3299 | 290.8445
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT AND GORSWEN GAP-BODRACH | 11.2885 | 4.6094 | 73.9965 | 2448.9891 | 302.133
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-VALE_OF_GLAM__RHONDDA_VALLEYS-LILLYPOT RESERVOIR-WELSH ST DONATS | 2.6561 | 1.0857 | 75.0822 | 2446.4234 | 304.7891
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-EGLWYSWRW-BRYNBERIAN WD | 5.3122 | 2.1834 | 77.2657 | 2432.9572 | 310.1013
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-HAFOD LLECHRYD-LECHRYD VILLIAGE | 4.6482 | 1.9164 | 79.182 | 2425.5116 | 314.7495
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-BETTWS-SCOTCH PINES | 1.5494 | 0.63905 | 79.8211 | 2424.539 | 316.2989
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-RHOSYMRYSON TO PENRHYWLLAN-PENRHIWLLAN SCHEME | 3.0988 | 1.2826 | 81.1036 | 2416.1152 | 319.3977
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-SOUTH_MEIRIONNYDD-PENNAL__CORRIS_SEVERN_TRENT-CORRIS TALGARTH TRUNK-PLASTALGARTH RES | 1.9921 | 0.8293 | 81.9329 | 2402.1206 | 321.3898
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-FFYNNON LLAWDDOG-BEULAH TO CWMCOU | 2.4348 | 1.0176 | 82.9505 | 2392.7441 | 323.8246
DIAM_LT_320-ALKATHENE-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-LLANELLI_FELINDRE-REHOBOTH RED DMA-REHOBOTH | 2.4348 | 1.0196 | 83.9701 | 2388.067 | 326.2593
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(0,70]-TALYBONT-ABERGAVENNY__CWMTILLERY-PONTYPOOL TDMA-AREA FED BY SUB SUPPLY SYSTEM | 1.9921 | 0.83958 | 84.8096 | 2372.7288 | 328.2514
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-NEWQUAY-SYNOD INN 4 | 5.5336 | 2.377 | 87.1867 | 2327.9167 | 333.785
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-PONTRHYDFENDIGAID-PONTRHYDFENDIGAID NORTH | 1.9921 | 0.86401 | 88.0507 | 2305.6398 | 335.7771
DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-WESTERN-CEMENT_MORTAR-(160,320]-TYWI_C.U._AREA-PENCOED__BRIDGEND_VALLEYS-CEFN HIRGOED TO LLANGEINOR-TYN-Y-WAUN | 1.5494 | 0.67383 | 88.7245 | 2299.4088 | 337.3265
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-EASTERN-NONE-(0,70]-ELAN_/_BUILTH-BUILTH-GARTH SR-LLANWRTYD WELLS | 1.5494 | 0.69857 | 89.4231 | 2217.9474 | 338.8759
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-EPOXY_RESIN-(70,120]-CYNON-MERTHYR__ABERCYNON-PENLOCKS 19INCH-HAWTHORN TERRACE | 1.7707 | 0.80307 | 90.2262 | 2204.9654 | 340.6466
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | 1.9921 | 0.90435 | 91.1305 | 2202.7806 | 342.6387
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(120,160]-CLWYD_COASTAL-ABERGELE__RHYL_GLASCOED-RHUALLT TO BODFARI-0702TREMEIRCHION/BODFARI (R70) | 6.1976 | 2.8584 | 93.9889 | 2168.2312 | 348.8363
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-PENRHYNDEUDRAETH-PENRHYD LLANFROTHEN | 1.7707 | 0.82214 | 94.811 | 2153.8166 | 350.607
DIAM_LT_320-ALKATHENE-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-LLANELLI_FELINDRE-POLIN TO RHYDARGAEAU-NANTGAREDIG BRIDGE | 3.0988 | 1.4401 | 96.2511 | 2151.8061 | 353.7058
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-CWMYSTRADLLYN GAP-CENIN | 3.5415 | 1.6539 | 97.9051 | 2141.2289 | 357.2473
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-BEUDY MAWR-BEUDY MAWR | 2.4348 | 1.1418 | 99.0469 | 2132.3727 | 359.6821
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-LLEYNHARLECH-BANGOR__CAERNARFON | 1.7707 | 0.84518 | 99.8921 | 2095.1046 | 361.4528
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-PILLETH-PILLETH_KNIGHTON__BLEDDFA-WHITTON BEGGARS BUSH-MAESTREYLOW TO NORTON | 1.7707 | 0.84929 | 100.7413 | 2084.9713 | 363.2236
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-NORTHERN-EPOXY_RESIN-(120,160]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-LLANDUDNO MAESDU ROAD | 1.5494 | 0.75157 | 101.4929 | 2061.5446 | 364.773
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-MID_-_SOUTH_CEREDIGION-LLECHRYD-PENPARC SR TO CARDIGAN SR-PENPARC SOUTH | 3.9842 | 1.9395 | 103.4325 | 2054.1802 | 368.7571
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-CLWYD_COASTAL-PRESTATYN_GLASCOED__TRECASTELL-DYSERTH-0805 DYSERTHGRAVITY (R80) | 1.5494 | 0.75678 | 104.1892 | 2047.3531 | 370.3065
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(120,160]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL-WESTHIDE HEREFORD | 1.5494 | 0.76275 | 104.952 | 2031.3397 | 371.8559
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-CEFN BRYN OUTLETS TO S W GOWER-PENMAEN WD | 2.6561 | 1.3151 | 106.2671 | 2019.7044 | 374.5121
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-CEFN BRYN OUTLETS TO S W GOWER-PENMAEN WD | 8.6324 | 4.2806 | 110.5477 | 2016.6247 | 383.1444
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(0,70]-TALYBONT-ABERGAVENNY__CWMTILLERY-LITTLE MILL TO USK | 1.5494 | 0.7691 | 111.3168 | 2014.5747 | 384.6938
DIAM_GT_320-FERROUS_2->320mm and <=450mm-B14_1980-1961_1980-WESTERN-CEMENT_MORTAR-(320,450]-TYWI_C.U._AREA-CAERAU__YSTRADFELLTE-ONLLWYN OUTLET-ONLLWYN POST OFFICE | 0.88537 | 0.43955 | 111.7563 | 2014.2681 | 385.5792
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-MERTHYR__ABERCYNON-QUAKERS YARD 24INCH-SUB SUPPLY SYSTEM | 2.4348 | 1.2103 | 112.9666 | 2011.7358 | 388.014
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-MAESTWYNOG-CYNGHORDY OUTLET | 20.8062 | 10.3974 | 123.364 | 2001.1007 | 408.8202
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(120,160]-WHITBOURNE-WHITBOURNE-LEYSTERS 8INCH-POLE FARM | 1.7707 | 0.88762 | 124.2516 | 1994.9435 | 410.5909
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-PEMBROKESHIRE-BOLTON_HILL-ROSEPOOL-FOXHILL RES | 1.5494 | 0.78737 | 125.039 | 1967.8161 | 412.1403
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(0,70]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW | 1.7707 | 0.89996 | 125.939 | 1967.5818 | 413.9111
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-LLANNOR SAETHON TRUNK-AREA FED BY S/SUPPLY 3A401608 | 2.4348 | 1.2388 | 127.1777 | 1965.452 | 416.3459
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SYNOD INN LLANARTH-LLANARTH TO ABERAERON | 2.2134 | 1.1288 | 128.3065 | 1960.9357 | 418.5593
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-LLANLLWNI-BELL VUE TO LLANYBYDDER | 4.2055 | 2.1487 | 130.4552 | 1957.2115 | 422.7648
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF-TREFOREST-TREFOREST IND. EST. WEST | 3.0988 | 1.5931 | 132.0483 | 1945.1179 | 425.8636
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(160,320]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN-BETTWS EAST-BETTWS EAST | 3.3201 | 1.7217 | 133.7701 | 1928.3665 | 429.1837
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-Y FELINHELI-BUSH RES Y FELINHELI | 2.2134 | 1.1638 | 134.9339 | 1901.9409 | 431.3972
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-FFYNNON WEN-GROESLON VILLAGE | 1.5494 | 0.81518 | 135.749 | 1900.6879 | 432.9466
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-COEDEN TO LLANFAETHLU-RHYDWYN VILLAGE | 2.6561 | 1.405 | 137.154 | 1890.5286 | 435.6027
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN-MALPAS ROAD HIGH PRESSURE | 1.7707 | 0.94237 | 138.0964 | 1879.0306 | 437.3734
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SKEWEN__LLANDARCY_FELINDRE__CRAY-TYDRAW ROAD-MAES YR HAF | 1.9921 | 1.0702 | 139.1665 | 1861.4704 | 439.3655
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-PENTIR BRYNREFAIL | 1.5494 | 0.84082 | 140.0073 | 1842.7329 | 440.9149
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(160,320]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY-SOUTHERNDOWN-OGMORE BY SEA | 1.7707 | 0.96763 | 140.975 | 1829.9774 | 442.6856
DIAM_LT_320-FERROUS_2-<=320mm-B15_1990-1981_2000-CENTRAL-CEMENT_MORTAR-(160,320]-CYNON-PENDERYN__PONTSTICILL-RHIGOS VILLAGE 8IN & 10IN OUTLETS-HIRWAUN INDUSTRIAL ESTATE | 3.7628 | 2.06 | 143.035 | 1826.6325 | 446.4485
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-PONTRHYDFENDIGAID-FFAIR RHOS YSBYTY YSTWYTH | 2.8775 | 1.5759 | 144.6109 | 1825.8725 | 449.3259
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-EGLWYSWRW-BRYNBERIAN WD | 2.2134 | 1.2282 | 145.839 | 1802.2405 | 451.5394
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-MID_-_SOUTH_CEREDIGION-LLECHRYD-WAUNLLWYD TO GORLLWYN -CAPEL IWAN TO CENARTH | 2.4348 | 1.3745 | 147.2135 | 1771.3974 | 453.9741
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-CEMENT_MORTAR-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-BANGOR FROM BRYNIAU-PENRHOS ROAD | 1.5494 | 0.8752 | 148.0887 | 1770.3374 | 455.5235
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-BOLTON_HILL-QUARRY LINE-QUARRY LINE | 1.9921 | 1.1318 | 149.2206 | 1760.0464 | 457.5156
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PENDINE-BRANDY HILL TO CROSSHANDS-PONT Y FENNI | 1.5494 | 0.88876 | 150.1093 | 1743.3198 | 459.065
DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-BETTWS-BUTCHERS | 1.7707 | 1.021 | 151.1304 | 1734.2968 | 460.8358
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SARNAU CROSS CONNECTION-TANYGROES | 3.3201 | 1.9396 | 153.07 | 1711.7578 | 464.1559
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_EAST | 1.5494 | 0.9101 | 153.9801 | 1702.4568 | 465.7053
DIAM_LT_320-ALKATHENE-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-BRYNGWYN-LLANNON WEST-PONT MORLAIS | 4.4269 | 2.6164 | 156.5964 | 1691.9859 | 470.1322
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-EPOXY_RESIN-(70,120]-CYNON-PENDERYN__PONTSTICILL-PERTHCELYN-PERTHCELYN PUMPS | 1.5494 | 0.91825 | 157.5147 | 1687.3411 | 471.6816
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-CORWEN GAP-BETTWS GG O/TLET | 2.2134 | 1.3161 | 158.8308 | 1681.81 | 473.895
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(0,70]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT & GORSWEN MINOR-EGLWYSBACH 85 LLYN CONWY | 3.0988 | 1.8691 | 160.6998 | 1657.9436 | 476.9938
DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(0,70] | 1.7707 | 1.0706 | 161.7704 | 1654.0103 | 478.7645
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | 3.5415 | 2.1655 | 163.936 | 1635.3805 | 482.306
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SARNAU CROSS CONNECTION-TRESAITH SCHEME | 5.0909 | 3.1246 | 167.0605 | 1629.2987 | 487.3969
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-PENRHYNDEUDRAETH | 1.9921 | 1.2302 | 168.2907 | 1619.3256 | 489.389
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-DERLWYN-DERLWYN | 1.5494 | 0.95812 | 169.2489 | 1617.1296 | 490.9384
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-SOUTH_MEIRIONNYDD-DOLGELLAU_PEN_Y_CEFN-FAIRBOURNE-FAIRBOURNE FRIOG | 6.1976 | 3.8366 | 173.0855 | 1615.3768 | 497.136
DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(120,160]-PEMBROKESHIRE-BOLTON_HILL-ROSEPOOL-ROSEPOOL | 2.2134 | 1.3797 | 174.4652 | 1604.2315 | 499.3494
DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(160,320]-PONTSTICILL_LOW_LEVEL-VALE_OF_GLAM__RHONDDA_VALLEYS-12 LLANILID OUTLET TDMA-AREA FED BY SUB SUPPLY SYSTEM | 2.2134 | 1.3837 | 175.8489 | 1599.6723 | 501.5628
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN-MALPAS ROAD HIGH PRESSURE-WHITTLE DRIVE | 2.2134 | 1.389 | 177.2379 | 1593.4903 | 503.7763
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-NORTH_CEREDIGION | 1.5494 | 0.98235 | 178.2203 | 1577.2454 | 505.3257
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL-WEOBLEY NORTH-DILWYN | 1.9921 | 1.2778 | 179.4981 | 1559.0283 | 507.3178
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-EPOXY_RESIN-(70,120]-CYNON-MERTHYR__ABERCYNON-PENLOCKS 19INCH-HAWTHORN TERRACE | 1.5494 | 0.99484 | 180.4929 | 1557.4428 | 508.8672
DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-BRYN BEDDAU SOUTH-BICELL RESERVOIR | 3.0988 | 2.0079 | 182.5008 | 1543.3199 | 511.966
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-PRESELI_SUPPLY-CROESFORDD OUTLET-CROESFORDD 4 INCH | 1.5494 | 1.0068 | 183.5076 | 1538.9112 | 513.5154
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160]-ALWEN_/_DEE-DENBIGH_ALWEN-DENBIGH TRUNK-1402 LLANGWYFAN(G40) | 2.8775 | 1.8709 | 185.3785 | 1537.9938 | 516.3928
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SARNAU CROSS CONNECTION-BEULAH SCHEME | 8.411 | 5.5356 | 190.9141 | 1519.4514 | 524.8038
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-PRESELI_SUPPLY-LETTERSTON-LLANGLOFFAN CROSS | 3.7628 | 2.4834 | 193.3974 | 1515.2143 | 528.5667
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-POLYURETHANE-(70,120]-PEMBROKESHIRE-BOLTON_HILL-ROSEPOOL-FOXHILL RES | 1.7707 | 1.1812 | 194.5786 | 1499.0989 | 530.3374
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-TWYNLLANAN-MOUNTPLEASANT | 2.6561 | 1.7758 | 196.3545 | 1495.7223 | 532.9935
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CRAY__CLYDACH-CLYDACH AREA ALT-YNYSTAWE | 2.2134 | 1.4882 | 197.8426 | 1487.367 | 535.2069
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-BRYNGWYN-TRAPP BULK EXPORT | 2.4348 | 1.6498 | 199.4924 | 1475.7913 | 537.6417
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-PRESELI_SUPPLY-PENYGARN TO HOTWELLS-PENYGARN/AMBLESTON 3 INCH | 1.9921 | 1.3525 | 200.8449 | 1472.9285 | 539.6338
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-HAFOD LLECHRYD-LECHRYD VILLIAGE | 1.7707 | 1.2023 | 202.0472 | 1472.7799 | 541.4045
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-PENDINE | 1.5494 | 1.0571 | 203.1043 | 1465.7602 | 542.9539
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-GWENLLI-PENBONTARBOTHAU BPT | 1.5494 | 1.0639 | 204.1682 | 1456.3003 | 544.5033
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKEWEN__LLANDARCY_FELINDRE__CRAY-MAES RHEDYN AND LODGE DRIVE | 1.5494 | 1.0648 | 205.2329 | 1455.1702 | 546.0527
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | 5.3122 | 3.6751 | 208.908 | 1445.4707 | 551.365
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(0,70]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON | 2.6561 | 1.8393 | 210.7473 | 1444.1064 | 554.0211
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_SW__RISCA__ABERCARN-RHIWDERIN TO DUFFRYN SR OUT TDMA-RHIWDERIN TO DUFFRYN S.R. | 2.4348 | 1.6884 | 212.4357 | 1442.0822 | 556.4559
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-BETTWS-BUTCHERS | 2.2134 | 1.5358 | 213.9715 | 1441.1839 | 558.6693
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-HOLLAND ARMS 9INCH-LLYS LEW TO LLANDDANIEL | 2.4348 | 1.6983 | 215.6698 | 1433.6795 | 561.1041
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-CROSS ASH-THE BOOT NEWCASTLE | 2.4348 | 1.7035 | 217.3733 | 1429.2934 | 563.5388
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-DERI GOCH PS TO RHOSYMRYSON SR-CAPEL Y GROES TO LLANWNEN | 1.5494 | 1.0864 | 218.4596 | 1426.2433 | 565.0882
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(0,70] | 2.6561 | 1.8729 | 220.3325 | 1418.2103 | 567.7443
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(0,70]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | 1.5494 | 1.1018 | 221.4342 | 1406.2892 | 569.2937
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH__BARRY-LOWER PENARTH PRV-AREA FED BY SSS | 1.7707 | 1.263 | 222.6973 | 1401.985 | 571.0645
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SARNAU CROSS CONNECTION-GOGERDDAN | 3.5415 | 2.5399 | 225.2371 | 1394.367 | 574.606
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(160,320]-TYWI_C.U._AREA-BRYNGWYN | 1.5494 | 1.1116 | 226.3487 | 1393.8638 | 576.1554
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(0,70]-TALYBONT-ABERGAVENNY__CWMTILLERY-PONTYPOOL TDMA-AREA FED BY SUB SUPPLY SYSTEM | 3.7628 | 2.7064 | 229.0551 | 1390.3393 | 579.9182
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-SYCHNANT-MAEN HIR BRYNCROES | 2.8775 | 2.0864 | 231.1415 | 1379.1286 | 582.7957
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CAERPHILLY-TY CANOL-NANTGARW OFF TYCANOL | 1.7707 | 1.3045 | 232.446 | 1357.4065 | 584.5664
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-EASTERN-NONE-(0,70]-BRECON_/_PORTIS-PORTIS-PORTIS LOW-LOWER CHAPEL LINE | 1.7707 | 1.3053 | 233.7514 | 1356.5295 | 586.3371
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-FFYNNON LLAWDDOG-BEULAH TO CWMCOU | 4.4269 | 3.2952 | 237.0466 | 1343.4325 | 590.764
DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-CRYMYCH-CRYMYCH AT GARN | 1.9921 | 1.4875 | 238.5341 | 1339.2198 | 592.7561
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SYNOD INN SR TO RHOSYMRYSON SR-TALGERREG PISGAH | 1.7707 | 1.333 | 239.8671 | 1328.3794 | 594.5268
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-SOUTH_MEIRIONNYDD-DOLGELLAU_PEN_Y_CEFN-DOLGELLAU | 2.2134 | 1.6716 | 241.5387 | 1324.0987 | 596.7403
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(120,160]-BALA-BALA-COED TALOG OUTLET-COED TALOG OUTLET NEW DMA | 3.3201 | 2.5251 | 244.0639 | 1314.8417 | 600.0604
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-GRWYNE FAWR-GELLI/FELIN | 4.8695 | 3.7344 | 247.7983 | 1303.966 | 604.9299
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_EAST-COED Y GORAS-COED Y GORES | 2.4348 | 1.8704 | 249.6687 | 1301.7321 | 607.3647
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-RHYMNEY__BARGOED-CEFN FOREST NORTH | 1.5494 | 1.1954 | 250.8641 | 1296.1468 | 608.9141
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(160,320]-BRECON_/_PORTIS | 1.7707 | 1.375 | 252.2391 | 1287.8129 | 610.6849
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-PENCOED__BRIDGEND_VALLEYS-CEFN HIRGOED TO LLANGEINOR | 1.7707 | 1.3802 | 253.6192 | 1283.0012 | 612.4556
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(120,160]-TALYBONT-ABERGAVENNY__CWMTILLERY-BUNKERS-HILLSIDE NO.1 | 1.5494 | 1.2101 | 254.8293 | 1280.4375 | 614.005
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH-STUMPY EAST NO. 2 OUTLET-HOLTON ROAD | 1.7707 | 1.3918 | 256.2211 | 1272.2309 | 615.7757
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SYNOD INN SR TO RHOSYMRYSON SR-CROESGWYN | 1.5494 | 1.2196 | 257.4408 | 1270.3725 | 617.3251
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-POLYURETHANE-(70,120]-PONTSTICILL_LOW_LEVEL-MERTHYR__ABERCYNON-TWYNRODYN BULK-SUMMERHILL PLACE | 2.6561 | 2.0923 | 259.5331 | 1269.4624 | 619.9813
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-PENARTH | 1.7707 | 1.4053 | 260.9384 | 1260.0037 | 621.752
DIAM_GT_320-STEEL->450mm and <=610mm-B09_1930-1921_1940-CENTRAL-NONE-(450,610]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF-RHYDLAFAR 18 TDMA-SUPPLY SUB-SYSTEM BOUNDARY | 1.1067 | 0.89 | 261.8284 | 1243.4971 | 622.8587
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-TRAPP BULK EXPORT-PENYBANK/NANTGARDEIG 6 INCH | 1.9921 | 1.6162 | 263.4446 | 1232.5745 | 624.8508
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-MYNYDD CROGWY TO EGLWYSWRW AND CRYMYCH-STAR PUMPS | 5.7549 | 4.7385 | 268.1831 | 1214.499 | 630.6057
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-BRYN GWENALLT-BRYNGWENALLT TO LLANDDEUSANT | 2.2134 | 1.8271 | 270.0102 | 1211.4455 | 632.8191
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-CYNON-MERTHYR__ABERCYNON-TAFF 8INCH HIGH LEVEL-SUB SUPPLY SYSTEM BOUNDARY | 1.5494 | 1.2905 | 271.3007 | 1200.6097 | 634.3685
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-CAPEL_DEWI-EBENEZER SR OUTLETS-FOEL RES TO EBENEEZER RES | 1.5494 | 1.2998 | 272.6005 | 1192.0272 | 635.9179
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-GARNFADRYN-GARNFADRYN RES OUTLET | 1.9921 | 1.695 | 274.2956 | 1175.2613 | 637.91
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-CEFN BRYN HOUSE-REYNOLDSTON | 1.5494 | 1.3203 | 275.6158 | 1173.5481 | 639.4594
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-EPOXY_RESIN-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_SW__RISCA__ABERCARN-SALISBURY STREET-WEST END NEWBRIDGE | 1.5494 | 1.3219 | 276.9377 | 1172.1241 | 641.0088
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-PILLETH-PILLETH_KNIGHTON__BLEDDFA-WOODHOUSE-KNIGHTON-KNUCKLAS | 1.7707 | 1.5122 | 278.4499 | 1170.9565 | 642.7796
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-PONTYPRIDD_PONTSTICILL_HIGH-TY GWYN 12INCH | 1.5494 | 1.3237 | 279.7736 | 1170.5027 | 644.329
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-BALA-BALA-RHYD UCHAF OUTLET-LLWYN IOLYN OUTLET NEW DMA | 5.9763 | 5.1114 | 284.885 | 1169.2081 | 650.3052
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(120,160]-TYWYN_/_ABERDYFI-BRYNCRUG-ESCUAN ABERDYFI TRUNK-AREA FED BY S/SUPPLY 3H900394 | 5.3122 | 4.5654 | 289.4504 | 1163.5831 | 655.6174
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-BITUMEN-(70,120]-WHITBOURNE-WHITBOURNE | 1.7707 | 1.5242 | 290.9746 | 1161.7673 | 657.3882
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-WHITBOURNE-WHITBOURNE-WARRENWOOD-HOLLY TREE METER | 3.3201 | 2.8672 | 293.8418 | 1157.98 | 660.7083
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-VOWCHURCH-VOWCHURCH-BRAMPTON SR-MYNYDD FERDDYN (LONGTOWN) | 1.5494 | 1.3443 | 295.1861 | 1152.554 | 662.2577
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-CEFN BRYN OUTLETS TO S W GOWER-OXWICH | 2.8775 | 2.5153 | 297.7014 | 1143.9595 | 665.1352
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-LLYSWEN-LLYSWEN-HAY ON WYE-DORSTONE OUTLET | 1.5494 | 1.3618 | 299.0632 | 1137.7857 | 666.6846
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CRAY__CLYDACH-GURNOS CROSS | 2.2134 | 1.9484 | 301.0116 | 1136.037 | 668.898
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(120,160]-PEMBROKESHIRE-BOLTON_HILL-BRAWDY ST DAVIDS | 1.9921 | 1.7547 | 302.7663 | 1135.2948 | 670.8901
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-TRAPP BULK EXPORT-TRAPP 4 INCH | 2.6561 | 2.3534 | 305.1197 | 1128.6139 | 673.5462
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-PRESELI_SUPPLY-PRESELI USL OUTLETS-WISTON | 5.3122 | 4.7299 | 309.8496 | 1123.1114 | 678.8584
DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(0,70]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON | 1.7707 | 1.5846 | 311.4342 | 1117.4688 | 680.6292
DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-NORTHERN-EPOXY_RESIN-(70,120] | 1.7707 | 1.5862 | 313.0204 | 1116.3261 | 682.3999
DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-PENCOED__BRIDGEND_VALLEYS-BRIDGEND ROAD-LLANHARRY ROAD 7IN | 1.5494 | 1.4002 | 314.4207 | 1106.5241 | 683.9493
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN | 5.3122 | 4.8045 | 319.2251 | 1105.6862 | 689.2616
DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-EASTERN-NONE-(0,70]-ELAN_/_BUILTH-BUILTH | 1.5494 | 1.4022 | 320.6273 | 1104.9859 | 690.811
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-EPOXY_RESIN-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY | 1.9921 | 1.8161 | 322.4434 | 1096.8979 | 692.803
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH-MAESNEWYDD TO TRE’RDDOL -MAESNEWYDD TO GLANDYFI | 4.4269 | 4.06 | 326.5034 | 1090.3682 | 697.2299
DIAM_LT_320-ALKATHENE-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(0,70] | 1.7707 | 1.628 | 328.1314 | 1087.691 | 699.0006
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-POLYURETHANE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-TROEDYRHIW TO MAESTWYNOG-POST GWYN FFARMERS | 2.6561 | 2.4545 | 330.5859 | 1082.1217 | 701.6568
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-BOLTON_HILL-TTM OFF PENT PUMPS-DEVON DRIVE | 2.2134 | 2.0497 | 332.6356 | 1079.892 | 703.8702
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL-BEWDLEY RES TO WOEBLEY RES TDMA-AREA FEED BY 1T810310 | 1.5494 | 1.4414 | 334.077 | 1074.9464 | 705.4196
DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(160,320]-WHITBOURNE-WHITBOURNE | 2.4348 | 2.2664 | 336.3434 | 1074.2983 | 707.8544
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-CYNON-MERTHYR__ABERCYNON-TAFF 8INCH HIGH LEVEL-HIRWAUN 8 INCH SUPPLY | 2.2134 | 2.0744 | 338.4178 | 1067.0183 | 710.0678
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT & GORSWEN MINOR-LLANDDOGED | 2.2134 | 2.0766 | 340.4943 | 1065.9039 | 712.2812
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-SAETHON GAP-CAPEL TYDDYN PUMPED | 1.9921 | 1.8714 | 342.3658 | 1064.4819 | 714.2733
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT & GORSWEN TRUNK-OUTLET LLANGERNYW SRV | 2.8775 | 2.7041 | 345.0699 | 1064.098 | 717.1507
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH | 1.5494 | 1.4579 | 346.5277 | 1062.7862 | 718.7001
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-TREGARON TOWN-LLANIO ROAD TO LLANGEITHO | 2.6561 | 2.5404 | 349.0681 | 1045.5514 | 721.3563
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKEWEN__LLANDARCY_FELINDRE__CRAY-MAES RHEDYN AND LODGE DRIVE-LODGE DRIVE BAGLAN | 1.5494 | 1.4943 | 350.5624 | 1036.9023 | 722.9057
DIAM_LT_320-AC-<=320mm-B14_1980-1981_2000-EASTERN-NONE | 1.7707 | 1.7123 | 352.2747 | 1034.1276 | 724.6764
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-DUNFIELD_CROSSWAYS-CROSSWAYS NORTH AND HIGH-KINGSWOOD(CROSSWAYS HIGH) | 2.2134 | 2.1412 | 354.4159 | 1033.7532 | 726.8898
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-GORLLWYN RHOS TREALAU-RHOS RES | 3.3201 | 3.2204 | 357.6363 | 1030.9672 | 730.21
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-DERIGOCH TO ABERAERON-DERI GOCH TO ABERAERON | 2.4348 | 2.3651 | 360.0013 | 1029.4778 | 732.6447
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-EAST_ANGLESEY_CEFNI-RHOSYBOL TO COEDEN | 1.9921 | 1.9364 | 361.9377 | 1028.7612 | 734.6368
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(160,320]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM-PENHOW QUARRY TDMA-PENHOW QUARRY TO HIGHMOOR HILL | 3.9842 | 3.8971 | 365.8348 | 1022.3418 | 738.621
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | 5.5336 | 5.4197 | 371.2545 | 1021.0115 | 744.1546
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-NEWQUAY-SYNOD INN TO NEW QUAY 6 | 2.6561 | 2.6072 | 373.8617 | 1018.7787 | 746.8107
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-MAENLLWYD-MAENLLWYD | 4.4269 | 4.3518 | 378.2134 | 1017.2558 | 751.2375
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SARNAU CROSS CONNECTION-SARNAU BPT OUTLET | 5.0909 | 5.0112 | 383.2246 | 1015.9064 | 756.3284
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RHYMNEY__BARGOED-RHYMNEY SOUTH-PONTLOTTYN | 3.3201 | 3.2696 | 386.4942 | 1015.4569 | 759.6486
DIAM_GT_320-FERROUS_2->320mm and <=450mm-B13_1970-1961_1980-EASTERN-NONE-(320,450]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RASSAU__SIRHOWY_VALLEY-8119-CONFIRMED OUTSIDE OF SDMAS-UNALLOCATED LAND TREFIL | 1.1067 | 1.0905 | 387.5847 | 1014.8718 | 760.7553
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(120,160]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-BUTLINS-LLANGYBI - BODOWEN | 2.8775 | 2.8464 | 390.4311 | 1010.9265 | 763.6327
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_HEATH_&_LLANISHEN | 3.3201 | 3.3258 | 393.7569 | 998.2997 | 766.9529
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-BETTWS LLANGYBI AND LLANDDEWI BREFI-LANGYBI | 1.7707 | 1.7786 | 395.5355 | 995.5806 | 768.7236
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-VALE_OF_GLAM__RHONDDA_VALLEYS-ALFRED STREET | 1.9921 | 2.0028 | 397.5383 | 994.6424 | 770.7157
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(0,70]-ALWEN_/_DEE-DENBIGH_ALWEN | 1.9921 | 2.013 | 399.5513 | 989.6024 | 772.7078
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-SOUTH_ANGLESEY_CWELLYN__MYNYDD-CADNANT BEAUMARIS-LLANDEGFAN BOOSTER | 1.9921 | 2.0143 | 401.5656 | 988.9845 | 774.6999
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-RHOSYMRYSON TO PENRHYWLLAN-HOREB TO FFOSTRASOL | 1.9921 | 2.015 | 403.5806 | 988.6146 | 776.692
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-EPOXY_RESIN-(70,120]-CYNON-PENDERYN__PONTSTICILL-MOUNTAIN ASH WEST-MOUNTAIN ASH WEST | 1.7707 | 1.7987 | 405.3793 | 984.4779 | 778.4627
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__RUMNEY-PLASNEWYDD ROAD PRV-SUPPLY SUB-SYSTEM BOUNDARY | 1.5494 | 1.575 | 406.9542 | 983.7762 | 780.0121
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA-CAPEL_DEWI-EBENEZER SR OUTLETS-EBENEZER-LLANGAIN 4 INCH | 1.5494 | 1.5768 | 408.531 | 982.6153 | 781.5615
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-MAESTIR TO BRYNGARREG-MAESTIR TO BRYNGARREG | 4.8695 | 4.9561 | 413.4872 | 982.5265 | 786.4311
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(0,70]-ELAN_/_BUILTH-ELAN-NEUADD NORTH | 1.9921 | 2.035 | 415.5221 | 978.9268 | 788.4231
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-CYNON-PENDERYN__PONTSTICILL-RHIGOS VILLAGE 8IN & 10IN OUTLETS-RHIGOS VILLAGE | 2.4348 | 2.4999 | 418.022 | 973.9494 | 790.8579
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-PEMBROKESHIRE-BOLTON_HILL-BRAWDY ST DAVIDS-ST DAVIDS LOW PRES | 1.9921 | 2.0577 | 420.0797 | 968.1347 | 792.85
DIAM_LT_320-FERROUS_1-<=320mm-B04_1880-1881_1900-CENTRAL-EPOXY_RESIN-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 1.5494 | 1.6079 | 421.6876 | 963.6213 | 794.3994
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-CEFN PENDEGAR REDUCED DMA-CEFN PENDEGAR | 2.6561 | 2.7659 | 424.4535 | 960.3169 | 797.0555
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RHYMNEY__BARGOED-BRITHDIR AND DERI-DERI | 4.4269 | 4.6101 | 429.0636 | 960.2464 | 801.4824
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-BETWS-Y-COED-BETWS Y COED / DOLWYDDELAN VILLAGE | 1.7707 | 1.8476 | 430.9112 | 958.3924 | 803.2531
DIAM_LT_320-ALKATHENE-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(0,70]-PONTSTICILL_LOW_LEVEL | 1.7707 | 1.8519 | 432.7631 | 956.1997 | 805.0239
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY-SIGGINGSTONE 12INCH OUTLET | 1.9921 | 2.0893 | 434.8523 | 953.4862 | 807.0159
DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-CRYMYCH-PENTREGALAR AT GARN | 2.8775 | 3.0278 | 437.8802 | 950.3328 | 809.8934
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-SYCHNANT | 1.5494 | 1.6357 | 439.5159 | 947.2408 | 811.4428
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-PENARTH | 2.2134 | 2.3452 | 441.861 | 943.8199 | 813.6562
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-HAFOD FELINWYNT-HAFOD FELINWYNT 5 | 3.3201 | 3.5242 | 445.3852 | 942.0971 | 816.9764
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-PRESELI_SUPPLY-HOTWELLS TO LETTERSTON-CO/OP LETTERSTON | 5.0909 | 5.4127 | 450.7979 | 940.5511 | 822.0672
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM-ST BRIDES ROAD-MAGOR | 2.4348 | 2.5896 | 453.3875 | 940.2154 | 824.502
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(120,160]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-SYCHNANT-MAENHIR PENGROESLON | 1.5494 | 1.6524 | 455.0399 | 937.6497 | 826.0514
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-PONTYPOOL TDMA-AREA FED BY SUB SUPPLY SYSTEM | 1.5494 | 1.6552 | 456.6951 | 936.0783 | 827.6008
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH-PENYCWM-PENYCWM CAPEL SEION RES | 2.4348 | 2.6017 | 459.2969 | 935.828 | 830.0356
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-MID_-_SOUTH_CEREDIGION-LLECHRYD-EGLWYSWRW-POST GWYN - EGLWYSWRW | 4.2055 | 4.4953 | 463.7922 | 935.5289 | 834.2411
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL-TENBY 7 DMA-TENBY 7 WD | 1.5494 | 1.6621 | 465.4543 | 932.2044 | 835.7905
DIAM_GT_320-PLASTIC_PVC->320mm and <=450mm-B13_1970-1961_1980-NORTHERN-NONE-(320,450]-NORTH_ERYRI_/_YNYS_MON-SOUTH_ANGLESEY_CWELLYN__MYNYDD-YNYS MON SOSI TM-AREA FED BY S/SUPPLY 3B300A03 | 3.0988 | 3.3272 | 468.7815 | 931.3456 | 838.8893
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(0,70]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT & GORSWEN MINOR-LLANDDOGED | 3.0988 | 3.3292 | 472.1107 | 930.8051 | 841.9881
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL | 2.2134 | 2.3832 | 474.4938 | 928.7708 | 844.2015
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-RHONDDA-TYNYWAUN-BAGLAN STREET TO DR THOMAS | 1.5494 | 1.6698 | 476.1636 | 927.8889 | 845.7509
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAPEL_DEWI | 3.3201 | 3.5917 | 479.7554 | 924.3808 | 849.0711
DIAM_LT_320-PLASTIC_PE-<=320mm-B18_2020-2021_ONWARDS-NORTHERN-NONE-(0,70] | 2.2968 | 2.4863 | 482.2417 | 923.7956 | 851.3679
DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-EPOXY_RESIN-(120,160]-TALYBONT-ABERGAVENNY__CWMTILLERY-8116-CONFIRMED OUTSIDE OF SDMAS-PANT FARM OUTLET TO CROSS ASH | 1.7707 | 1.9173 | 484.159 | 923.5602 | 853.1387
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-GORLLWYN RHOS TREALAU-GORLLWYN TO RHOS/TREALAU | 2.4348 | 2.6571 | 486.8162 | 916.31 | 855.5734
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(160,320]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-CERRIG-POINT D TO CERRIG | 2.8775 | 3.1411 | 489.9572 | 916.0781 | 858.4509
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SYNOD INN SR TO RHOSYMRYSON SR-GRESFFORDD MOUNT BRANCH | 4.2055 | 4.6187 | 494.5759 | 910.5335 | 862.6564
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-BRYNGWYN | 3.9842 | 4.401 | 498.9769 | 905.2943 | 866.6406
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT AND GORSWEN GAP-MAENAN INLET | 3.3201 | 3.6985 | 502.6754 | 897.7116 | 869.9607
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RHYMNEY__BARGOED-RHYMNEY CENTRAL AND NORTH-RHYMNEY CENTRAL | 2.6561 | 2.9727 | 505.6481 | 893.4911 | 872.6168
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-EPOXY_RESIN-(70,120]-NORTH_ERYRI_/_YNYS_MON-EAST_ANGLESEY_CEFNI | 1.5494 | 1.7424 | 507.3905 | 889.2294 | 874.1662
DIAM_LT_320-AC-<=320mm-B14_1980-1981_2000-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON | 1.9921 | 2.247 | 509.6375 | 886.5399 | 876.1583
DIAM_LT_320-ALKATHENE-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(0,70]-SLUVAD__COURT_FARM__LLWYNON | 2.2134 | 2.5052 | 512.1428 | 883.5162 | 878.3717
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(120,160]-SOUTH_MEIRIONNYDD-LLWYNGWRIL_GWASTADCOED-GWASTADCOED-HENBLAS | 3.7628 | 4.262 | 516.4048 | 882.878 | 882.1346
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-MAENLLWYD-MAENLLWYD | 1.5494 | 1.7608 | 518.1656 | 879.9496 | 883.684
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-CARDIGAN SR OUTLET | 1.9921 | 2.2792 | 520.4448 | 874.0322 | 885.676
DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(0,70]-PEMBROKESHIRE | 1.5494 | 1.7768 | 522.2216 | 872.0114 | 887.2254
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-EPOXY_RESIN-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL-WEOBLEY NORTH-WEOBLEY RES NORTH | 2.4348 | 2.7953 | 525.0169 | 871.0256 | 889.6602
DIAM_LT_320-STEEL-<=320mm-B13_1970-1961_1980-WESTERN-NONE | 1.5494 | 1.7796 | 526.7965 | 870.624 | 891.2096
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-RHYMNEY__BARGOED-CEFN FOREST NORTH-BRITTANIA | 1.5494 | 1.7853 | 528.5818 | 867.8861 | 892.759
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-POLYURETHANE-(70,120]-TALYBONT | 2.2134 | 2.5553 | 531.1371 | 866.2155 | 894.9724
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-COED Y FRON-BODWI | 1.9921 | 2.3042 | 533.4413 | 864.5273 | 896.9645
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM | 1.7707 | 2.0495 | 535.4908 | 863.9962 | 898.7353
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-CAPEL_DEWI-FOEL TO MAENIEUAN-FOEL RES TALOG-ABERNANT | 2.6561 | 3.0796 | 538.5704 | 862.4927 | 901.3914
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-POLYURETHANE-(70,120]-PONTSTICILL_LOW_LEVEL-PONTYPRIDD_PONTSTICILL_HIGH-RHYDYFELIN LOW LEVEL BULK-RHYDYFELIN SOUTH | 1.5494 | 1.7996 | 540.37 | 860.9671 | 902.9408
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SARNAU CROSS CONNECTION-SARNAU BPT OUTLET | 3.0988 | 3.6154 | 543.9853 | 857.1217 | 906.0396
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-POLYURETHANE-(70,120]-RHONDDA-VALE_OF_GLAM__RHONDDA_VALLEYS | 1.5494 | 1.8106 | 545.7959 | 855.7589 | 907.589
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PENDINE-THREE LORDS OUTLET-THREE LORDS (BROADWAY/LAUGHARN | 1.5494 | 1.8145 | 547.6104 | 853.8795 | 909.1384
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SYNOD INN LLANARTH-LLANARTH TO ABERAERON | 1.5494 | 1.8191 | 549.4295 | 851.7596 | 910.6878
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-ELAN_/_BUILTH-ELAN-ELAN-BWLCH-Y-SARNAU S.R. | 1.5494 | 1.82 | 551.2495 | 851.3004 | 912.2372
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-NORTHERN-CEMENT_MORTAR-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-DEINIOLEN CEFN COCH | 1.9921 | 2.3533 | 553.6028 | 846.5074 | 914.2293
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(0,70]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | 2.4348 | 2.8846 | 556.4874 | 844.0705 | 916.664
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(0,70]-ALWEN_/_DEE-DENBIGH_ALWEN-LLANFWROG-1511 LLANFWROG(G50) | 2.6561 | 3.1549 | 559.6423 | 841.8891 | 919.3202
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-BOLTON_HILL-TESCO SOUTH | 1.7707 | 2.1042 | 561.7465 | 841.5165 | 921.0909
DIAM_GT_320-PLASTIC_PE->320mm and <=450mm-B16_2000-2001_2020-CENTRAL-NONE-(320,450] | 0.66403 | 0.78978 | 562.5363 | 840.772 | 921.7549
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-BEULAU TO ABERBANC-BLAENGWENLLAN CROSS | 1.7707 | 2.1062 | 564.6425 | 840.7483 | 923.5257
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-LLANFAIRFECHAN-LLANFAIRFECHAN | 4.2055 | 5.0201 | 569.6626 | 837.7269 | 927.7312
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(120,160]-TALYBONT-ABERGAVENNY__CWMTILLERY | 1.5494 | 1.8673 | 571.5299 | 829.7712 | 929.2806
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | 4.6482 | 5.6022 | 577.1321 | 829.7036 | 933.9288
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(120,160]-RHONDDA-MAERDY__PORTH | 1.5494 | 1.872 | 579.0042 | 827.6612 | 935.4782
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 1.9921 | 2.4122 | 581.4164 | 825.8236 | 937.4703
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SYNOD INN SR TO RHOSYMRYSON SR-GRESFFORDD MOUNT BRANCH | 1.9921 | 2.4366 | 583.853 | 817.5819 | 939.4624
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-SOUTH_ANGLESEY_CWELLYN__MYNYDD-FELIN ENGAN LLANFAIR PG-FELIN ENGAN TO LLANFAIRPWLL | 1.7707 | 2.1678 | 586.0208 | 816.8294 | 941.2331
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE | 2.2134 | 2.7111 | 588.7318 | 816.4427 | 943.4465
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__RUMNEY | 1.5494 | 1.902 | 590.6338 | 814.613 | 944.9959
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-BEULAU TO ABERBANC-BLEANGWENLLAN X NCE | 2.4348 | 2.9898 | 593.6237 | 814.3504 | 947.4307
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-PONTRHYDFENDIGAID-FFAIR RHOS YSBYTY YSTWYTH | 1.5494 | 1.9243 | 595.5479 | 805.1905 | 948.9801
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-HAFOD LLECHRYD-LLANDYGWYDD | 3.3201 | 4.1336 | 599.6816 | 803.2068 | 952.3002
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-CEFN BRYN HOUSE-KENNEXESTONE | 1.7707 | 2.2098 | 601.8913 | 801.3168 | 954.071
DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-LLANGWYFAN-WAEN ABERWHEELER GEINAS | 2.8775 | 3.5935 | 605.4849 | 800.7289 | 956.9484
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-USK MARKET ST AND DAVINGTON HOUSE-LLANDENNY MAIN | 2.2134 | 2.7708 | 608.2557 | 798.8361 | 959.1619
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-MERTHYR__ABERCYNON | 1.7707 | 2.2216 | 610.4773 | 797.0489 | 960.9326
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-EPOXY_RESIN-(120,160]-TYWI_C.U._AREA-CAPEL_DEWI-EBENEZER SR OUTLETS-LLANSTEPHAN | 1.9921 | 2.5094 | 612.9867 | 793.8504 | 962.9247
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-COEDEN TO LLANFAETHLU-LLANRHUDDLAD TO RHYDWYN | 2.2134 | 2.7922 | 615.7789 | 792.728 | 965.1381
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SYNOD INN LLANARTH-LLANARTH TO ABERAERON | 1.7707 | 2.248 | 618.0269 | 787.6896 | 966.9089
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-POLYURETHANE-(70,120]-PEMBROKESHIRE-BOLTON_HILL | 1.9921 | 2.5296 | 620.5565 | 787.5177 | 968.901
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-EPOXY_RESIN-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-BYLCHAU HIGH-CEFN LLWYDHENLLAN | 2.2134 | 2.8247 | 623.3812 | 783.5976 | 971.1144
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-HAFOD LLECHRYD-LECHRYD VILLIAGE | 2.4348 | 3.115 | 626.4961 | 781.64 | 973.5492
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-EASTERN-NONE-(0,70] | 1.9921 | 2.5498 | 629.0459 | 781.276 | 975.5412
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-CROSSROADS TO CRUGIAU AND TREGAMMON-TREGAMMON WD | 8.6324 | 11.0909 | 640.1368 | 778.3277 | 984.1736
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(70,120]-TALYBONT | 1.9921 | 2.5717 | 642.7086 | 774.6089 | 986.1657
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-NORTHERN-CEMENT_MORTAR-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-CAERNARFON SEGONTIWM-PRINCE OF WALES | 1.9921 | 2.5731 | 645.2817 | 774.1837 | 988.1578
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(0,70] | 3.0988 | 4.0392 | 649.3209 | 767.1819 | 991.2566
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-MYNYDD CROGWY TO EGLWYSWRW AND CRYMYCH-POST GWYN BONCATH | 2.8775 | 3.7736 | 653.0945 | 762.5192 | 994.134
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-LLEYNHARLECH-BANGOR__CAERNARFON | 1.7707 | 2.3254 | 655.42 | 761.4652 | 995.9048
DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD | 1.5494 | 2.0403 | 657.4603 | 759.4004 | 997.4542
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PORT_TALBOT_FELINDRE__CRAY-RODERICKS AND DYFFRYN YD-RODERICKS | 2.2134 | 2.9238 | 660.3841 | 757.0293 | 999.6676
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-PRESELI_SUPPLY-TENBY MAIN-PICTON/RHOS | 3.3201 | 4.3868 | 664.7709 | 756.8435 | 1002.9877
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-LITTLE MILL TO USK-GWEHELOG SUPPLY | 3.3201 | 4.387 | 669.1579 | 756.8188 | 1006.3079
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | 2.6561 | 3.5494 | 672.7074 | 748.3179 | 1008.964
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-CEMAES-CEMAES BAY VILLAGE | 1.7707 | 2.3822 | 675.0895 | 743.3376 | 1010.7347
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-BETHANIA TO CROSS INN-CROSSINN TO LLANON | 6.8616 | 9.2424 | 684.3319 | 742.4058 | 1017.5964
DIAM_LT_320-ALKATHENE-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(0,70]-BRECON_/_PORTIS | 1.7707 | 2.3933 | 686.7252 | 739.8712 | 1019.3671
DIAM_LT_320-FERROUS_1-<=320mm-B04_1880-PRE_1880-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE-HAFOD-HAFOD | 1.7707 | 2.3989 | 689.1242 | 738.1424 | 1021.1379
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PRESELI_SUPPLY-HOTWELLS TO LETTERSTON-CO/OP LETTERSTON | 2.2134 | 2.9991 | 692.1232 | 738.0322 | 1023.3513
DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-MERTHYR__ABERCYNON-PONSTICILL AND VAYNOR-TREFECHAN | 2.6561 | 3.6236 | 695.7469 | 732.9952 | 1026.0074
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-PILLETH-PILLETH_KNIGHTON__BLEDDFA-BEGGARS BUSH TO KNOWLE HILL TDMA-KINNERTON | 3.9842 | 5.4534 | 701.2003 | 730.5888 | 1029.9916
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SARNAU CROSS CONNECTION-BEULAH SCHEME | 3.3201 | 4.563 | 705.7633 | 727.6227 | 1033.3117
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-CYNON-MERTHYR__ABERCYNON-CWMDARE AND BRYNNAU FARM-CWMDARE LESS BRYNAU FARM | 1.7707 | 2.4358 | 708.1991 | 726.9641 | 1035.0825
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAPEL_DEWI-FOEL SR TO RHYDARGAEAU-PENIEL BRONWYDD | 1.5494 | 2.1343 | 710.3334 | 725.9432 | 1036.6319
DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN-THORNHILL-THORNHILL ROAD | 3.0988 | 4.2817 | 714.6151 | 723.7335 | 1039.7307
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE | 3.5415 | 4.9067 | 719.5218 | 721.7655 | 1043.2721
DIAM_GT_320-AC->320mm and <=450mm-B14_1980-1961_1980-CENTRAL-NONE-(320,450]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__RUMNEY-ROVER WAY BULK-ROVER WAY | 0.66403 | 0.92426 | 720.446 | 718.4464 | 1043.9362
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-RHONDDA-MAERDY__PORTH-GRAIGWEN AND LANWOOD-GRAIGWEN & LANWOOD OFF R.L | 1.7707 | 2.4722 | 722.9183 | 716.2507 | 1045.7069
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY-NEWTON NOTTAGE-NEWTON NOTTAGE | 2.2134 | 3.1216 | 726.0398 | 709.0786 | 1047.9203
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__CANTON__CATHAYS | 1.7707 | 2.4999 | 728.5398 | 708.3125 | 1049.6911
DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-PILLETH-PILLETH_KNIGHTON__BLEDDFA | 1.7707 | 2.5068 | 731.0466 | 706.3668 | 1051.4618
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-CENTRAL-NONE-(0,70]-SLUVAD__COURT_FARM__LLWYNON | 1.9921 | 2.8204 | 733.867 | 706.3105 | 1053.4539
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-BETHANIA TO CROSS INN-CROSSINN TO LLANRHYSTUD | 3.7628 | 5.3651 | 739.2322 | 701.3477 | 1057.2167
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-LLANAELHAEARN AND TRALLWYN-TRALLWYN RES OUTLET | 1.7707 | 2.5272 | 741.7594 | 700.6679 | 1058.9875
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(120,160]-WHITBOURNE-WHITBOURNE-LEYSTERS 8INCH | 2.2134 | 3.1606 | 744.92 | 700.3108 | 1061.2009
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-LLANGWYFAN-WAEN ABERWHEELER GEINAS | 1.7707 | 2.5309 | 747.4509 | 699.6594 | 1062.9717
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH__BARRY | 2.2134 | 3.165 | 750.6159 | 699.3514 | 1065.1851
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-TRAPP BULK EXPORT-CWM ISAF TO BETHLEHEM | 3.3201 | 4.7513 | 755.3671 | 698.7927 | 1068.5052
DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(120,160]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-GWYTHERIN-GWYTHERIN RESOUTLET (R00) | 1.9921 | 2.8529 | 758.22 | 698.2568 | 1070.4973
DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-NORTHERN-CEMENT_MORTAR-(160,320]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT VALLEY TRUNK-AREA FED BY S/SUPPLY 3SC20M18 | 1.9921 | 2.8543 | 761.0743 | 697.9238 | 1072.4894
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-EGLWYSWRW-BRYNBERIAN WD | 4.6482 | 6.6829 | 767.7572 | 695.5389 | 1077.1376
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-CENTRAL-EPOXY_RESIN-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 1.9921 | 2.8892 | 770.6464 | 689.4988 | 1079.1297
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-MONMOUTH-TRELLECH__MAYHILL__FYNNON_GAER-TRELLECK-NEW MILLS | 2.4348 | 3.5315 | 774.1779 | 689.4403 | 1081.5644
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-COEDEN TO LLANFAETHLU-RHYDWYN BOOSTER | 2.4348 | 3.5318 | 777.7097 | 689.3812 | 1083.9992
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-CEMENT_MORTAR-(120,160] | 1.7707 | 2.5752 | 780.2849 | 687.6184 | 1085.77
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-WHITBOURNE-WHITBOURNE-LEYSTERS 8INCH-POLE FARM | 3.5415 | 5.1526 | 785.4375 | 687.3257 | 1089.3114
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-EPOXY_RESIN-(70,120]-PONTSTICILL_LOW_LEVEL-CAERPHILLY-BEDWAS OUTLET | 1.7707 | 2.5776 | 788.0151 | 686.981 | 1091.0822
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-USK MARKET ST AND DAVINGTON HOUSE | 1.9921 | 2.9089 | 790.9239 | 684.8327 | 1093.0743
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL-ADMIRALTY SITE-ADMIRALTY SITE | 2.6561 | 3.8853 | 794.8093 | 683.6243 | 1095.7304
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-ALWEN_/_DEE-DENBIGH_ALWEN | 5.5336 | 8.1172 | 802.9265 | 681.7082 | 1101.264
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PRESELI_SUPPLY-PENYGARN TO HOTWELLS-PENYGARN/AMBLESTON 3 INCH | 3.7628 | 5.5288 | 808.4553 | 680.5855 | 1105.0268
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-EASTERN-EPOXY_RESIN-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-TALYWAIN-TALYWAIN | 2.2134 | 3.2536 | 811.7089 | 680.3079 | 1107.2402
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | 1.5494 | 2.2789 | 813.9877 | 679.9037 | 1108.7896
DIAM_LT_320-FERROUS_1-<=320mm-B04_1880-1881_1900-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__CANTON__CATHAYS | 1.7707 | 2.6068 | 816.5945 | 679.2841 | 1110.5604
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(160,320]-ALWEN_/_DEE-FLINT__CONNAHS_QUAY_BRETTON-HAWARDEN | 2.2134 | 3.2616 | 819.8561 | 678.628 | 1112.7738
DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | 1.7707 | 2.614 | 822.4701 | 677.4146 | 1114.5445
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(160,320]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-LLYN CONWY TRUNK-AREA FED BY S/SUPPLY 3SC70B08 | 6.4189 | 9.4852 | 831.9553 | 676.7333 | 1120.9635
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE | 1.5494 | 2.2951 | 834.2503 | 675.0939 | 1122.5129
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT-ST JULIANS ROAD-FIRBANK AVENUE | 2.4348 | 3.6224 | 837.8727 | 672.1498 | 1124.9476
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH__BARRY-REDLANDS ROAD SOUTH-REDLANDS ROAD SOUTH | 1.7707 | 2.6388 | 840.5115 | 671.0506 | 1126.7184
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-SALEM SR OUTLET-SALEM VILLAGE METER | 18.1501 | 27.0711 | 867.5826 | 670.46 | 1144.8685
DIAM_LT_320-STEEL-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | 2.2134 | 3.3018 | 870.8844 | 670.373 | 1147.0819
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON-BUCKLEY LIVERPOOL ROAD-EWLOE/HAWARDEN. | 2.2134 | 3.3099 | 874.1943 | 668.7333 | 1149.2954
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-FFYNNON LLAWDDOG-FFYNNON LLAWDDDOG SCHEME | 3.3201 | 4.9998 | 879.194 | 664.0599 | 1152.6155
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PENCOED__BRIDGEND_VALLEYS-OGMORE VALE | 3.5415 | 5.3355 | 884.5295 | 663.7611 | 1156.157
DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(120,160]-ALWEN_/_DEE-DENBIGH_ALWEN-ALWEN TO PEN Y COED & ACCRE TRUNK-ACCRE PUMPING STATION | 1.9921 | 3.012 | 887.5415 | 661.388 | 1158.1491
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-DERI GOCH PS TO RHOSYMRYSON SR-CAPEL Y GROES TO LLANWNEN | 4.2055 | 6.3604 | 893.9019 | 661.2062 | 1162.3546
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD | 10.1818 | 15.4357 | 909.3376 | 659.6248 | 1172.5363
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(160,320]-TYWI_C.U._AREA-CAPEL_DEWI-PENLLAIN TO NIMPWLL-PENLLAIN RES TO NIMPWLL RES | 3.0988 | 4.7147 | 914.0522 | 657.27 | 1175.6351
DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM | 1.5494 | 2.358 | 916.4102 | 657.0887 | 1177.1845
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_EAST-COED Y GORAS-COED Y GORES | 1.9921 | 3.0327 | 919.4429 | 656.8689 | 1179.1766
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-RHYMNEY__BARGOED-MAESYCWMMER-FLEUR DE LYS | 2.2134 | 3.3755 | 922.8184 | 655.7401 | 1181.3901
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-EBBW_VALE__BRYNMAWR-NANTYGLO AND FFOESMAEN-BLAINA VILLAGE | 1.5494 | 2.3668 | 925.1851 | 654.6416 | 1182.9395
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON | 4.6482 | 7.1095 | 932.2946 | 653.8019 | 1187.5877
DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-WHITBOURNE-WHITBOURNE-WARRENWOOD | 2.8775 | 4.4189 | 936.7136 | 651.1641 | 1190.4651
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(120,160]-PILLETH-PILLETH_KNIGHTON__BLEDDFA-LLANGUNLLO LINE-AREA FEED BY 1T810701 | 2.6561 | 4.0872 | 940.8008 | 649.8656 | 1193.1212
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-POLYURETHANE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-TWYNLLANAN-MOUNTPLEASANT | 1.7707 | 2.7287 | 943.5295 | 648.923 | 1194.892
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-POLYURETHANE-(70,120]-CYNON-MERTHYR__ABERCYNON-ABERCYNON WEST | 1.9921 | 3.0853 | 946.6148 | 645.6654 | 1196.8841
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-MOEL Y PENMAEN-MOEL PENMAEN RES OUTLET | 1.7707 | 2.7443 | 949.3591 | 645.2391 | 1198.6548
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-ALWEN TO BWLCH TRUNK-CRICOR SUPPLY FROM ALWEN | 1.5494 | 2.4038 | 951.7629 | 644.5659 | 1200.2042
DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | 2.2134 | 3.4417 | 955.2047 | 643.1134 | 1202.4176
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF | 2.8775 | 4.4759 | 959.6805 | 642.8833 | 1205.2951
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-CENTRAL-NONE-(70,120]-RHONDDA-PONTYPRIDD_PONTSTICILL_HIGH-GLYNCOCH HIGH-GLYNCOCH HIGH | 3.3201 | 5.1739 | 964.8544 | 641.7113 | 1208.6152
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA | 3.5415 | 5.5226 | 970.377 | 641.2737 | 1212.1567
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-USK MARKET ST AND DAVINGTON HOUSE-GWERNESNEY | 3.3201 | 5.1911 | 975.568 | 639.5896 | 1215.4769
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-SOUTH_MEIRIONNYDD-DINAS_MAWDDWY-DINAS MAWDDWY-MALLWYD | 1.7707 | 2.7764 | 978.3444 | 637.7829 | 1217.2476
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-ALWEN_/_DEE-DENBIGH_ALWEN-BYLCHAU HIGH | 2.8775 | 4.5143 | 982.8588 | 637.4031 | 1220.1251
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-PONTYPRIDD_PONTSTICILL_HIGH-CILFYNYDD HIGH-CILFYNYDD HIGH | 1.9921 | 3.1292 | 985.988 | 636.6073 | 1222.1171
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-POLYURETHANE-(70,120]-PONTSTICILL_LOW_LEVEL-MERTHYR__ABERCYNON-TWYNRODYN BULK-SUMMERHILL PLACE | 1.9921 | 3.1333 | 989.1213 | 635.7872 | 1224.1092
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(70,120] | 1.7707 | 2.7935 | 991.9148 | 633.8844 | 1225.88
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-POLYURETHANE-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | 1.9921 | 3.1503 | 995.065 | 632.3498 | 1227.8721
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL-NORCHARD BEACON SR OUTLET | 1.5494 | 2.4506 | 997.5156 | 632.2577 | 1229.4215
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT VALLEY GAP-EGLWYSBACH TALYCAFN | 1.5494 | 2.4545 | 999.9701 | 631.258 | 1230.9709
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF | 1.5494 | 2.4568 | 1002.4269 | 630.6589 | 1232.5203
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN-LLANDERFEL-HENLLYS 4 INCH | 1.7707 | 2.8259 | 1005.2528 | 626.6032 | 1234.291
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH__BARRY | 1.5494 | 2.4748 | 1007.7276 | 626.075 | 1235.8404
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(120,160]-SOUTH_MEIRIONNYDD-DOLGELLAU_PEN_Y_CEFN | 1.5494 | 2.4835 | 1010.2111 | 623.8862 | 1237.3898
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-BRYNGWYN-BRYNCOCH - PENTWYN-FOLLAND ROAD | 1.5494 | 2.488 | 1012.6991 | 622.7401 | 1238.9392
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-CEMENT_MORTAR-(70,120]-NORTH_ERYRI_/_YNYS_MON-SOUTH_ANGLESEY_CWELLYN__MYNYDD-PENMYNYDD CADNANT GAERWEN | 1.7707 | 2.8501 | 1015.5492 | 621.2956 | 1240.7099
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-EPOXY_RESIN-(70,120]-PEMBROKESHIRE-BOLTON_HILL | 4.6482 | 7.528 | 1023.0771 | 617.4586 | 1245.3581
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__RUMNEY-LLANRUMNEY AVENUE | 2.2134 | 3.5991 | 1026.6762 | 615.0002 | 1247.5716
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-WESTERN-NONE-(70,120] | 1.7707 | 2.8808 | 1029.557 | 614.6761 | 1249.3423
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(0,70]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON | 4.6482 | 7.6249 | 1037.1819 | 609.607 | 1253.9905
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-FLINT__CONNAHS_QUAY_BRETTON-ASTON 9 INCH-ASTON FROM PLOUGHINN. | 1.7707 | 2.9052 | 1040.0871 | 609.5087 | 1255.7613
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-BALA-BALA-COED TALOG OUTLET-COED TALOG OUTLET NEW DMA | 2.2134 | 3.6343 | 1043.7214 | 609.0355 | 1257.9747
DIAM_GT_320-STEEL->320mm and <=450mm-B07_1910-1901_1920-NORTHERN-NONE-(320,450]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-BRYNIAU (CONWY)-BRYNIAU RES OUTLET | 0.66403 | 1.0956 | 1044.817 | 606.0885 | 1258.6387
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL | 1.5494 | 2.5565 | 1047.3735 | 606.0696 | 1260.1881
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-MYNYDD CROGWY TO EGLWYSWRW AND CRYMYCH-WAUNYDD TEGRYN WD | 3.5415 | 5.8435 | 1053.217 | 606.0506 | 1263.7296
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-MERTHYR__ABERCYNON-QUAKERS YARD 24INCH-TRELEWIS - STORMTOWN (PT 4) | 1.7707 | 2.9251 | 1056.1421 | 605.3693 | 1265.5003
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-MERTHYR__ABERCYNON-BLACK LION | 1.5494 | 2.5713 | 1058.7134 | 602.5812 | 1267.0497
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-POLYURETHANE-(70,120]-RHONDDA-MAERDY__PORTH | 1.5494 | 2.5719 | 1061.2852 | 602.4387 | 1268.5991
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__CANTON__CATHAYS | 2.6561 | 4.4141 | 1065.6993 | 601.7406 | 1271.2552
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-DUNFIELD_CROSSWAYS-CROSSWAYS SOUTH-SARNESFIELD JUNCTION | 1.7707 | 2.9518 | 1068.6511 | 599.8922 | 1273.026
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-CENTRAL-POLYURETHANE-(70,120]-PONTSTICILL_LOW_LEVEL-CAERPHILLY-GWERNAU 12INCH CAERPHILLY FLOW-CAERPHILLY NORTH | 3.5415 | 5.9064 | 1074.5575 | 599.6 | 1276.5675
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-POLYURETHANE-(70,120]-PONTSTICILL_LOW_LEVEL-MERTHYR__ABERCYNON-TREHARRIS TANK-TREHARRIS TANK | 1.7707 | 2.965 | 1077.5225 | 597.2091 | 1278.3382
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN-BETTWS EAST-BETTWS EAST | 2.4348 | 4.0791 | 1081.6016 | 596.8951 | 1280.773
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(70,120]-BARMOUTH-BARMOUTH_-_HARLECH | 1.9921 | 3.3617 | 1084.9633 | 592.5818 | 1282.7651
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-SOUTH_MEIRIONNYDD | 2.8775 | 4.8665 | 1089.8297 | 591.2806 | 1285.6425
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH-FRONGOCH SR OUT-FRONGOCH TO CLARACH | 1.5494 | 2.6207 | 1092.4505 | 591.2144 | 1287.1919
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL-STEPHENS GREEN SR OUTLET-JAMESTON YOUTH CLUB | 1.7707 | 2.9955 | 1095.4459 | 591.1366 | 1288.9627
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-NONE-(70,120]-NORTH_CEREDIGION-ABERYSTWYTH_BONTGOCH__LOVESGROVE-CHALYBEATE STREET | 1.7707 | 3.0035 | 1098.4495 | 589.5531 | 1290.7334
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-MONMOUTH-TRELLECH__MAYHILL__FYNNON_GAER-TRELLECK-FARR HILL | 2.4348 | 4.1417 | 1102.5911 | 587.8737 | 1293.1682
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | 1.7707 | 3.0362 | 1105.6273 | 583.2126 | 1294.9389
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKEWEN__LLANDARCY_FELINDRE__CRAY | 3.0988 | 5.3162 | 1110.9436 | 582.8925 | 1298.0377
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON-RHOSESMOR BERTH DDU | 1.5494 | 2.6603 | 1113.6039 | 582.4091 | 1299.5871
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-MERTHYR__ABERCYNON-PENTREBACH-PENTREBACH/TROEDYRHIW | 1.5494 | 2.661 | 1116.2649 | 582.2618 | 1301.1365
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(120,160]-VOWCHURCH-VOWCHURCH-KINGSTONE SR-CLEHONGER | 1.5494 | 2.6616 | 1118.9265 | 582.1293 | 1302.6859
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(120,160]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL-WESTHIDE NEWTON-WESTHIDE TO NEWTOWN | 1.7707 | 3.0441 | 1121.9706 | 581.6913 | 1304.4567
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(0,70]-SLUVAD__COURT_FARM__LLWYNON | 2.4348 | 4.2062 | 1126.1769 | 578.8498 | 1306.8914
DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON | 1.9921 | 3.4514 | 1129.6282 | 577.1877 | 1308.8835
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON-BUCKLEY BROOKE STREET-BROOKEST.BUCKLEY. | 1.7707 | 3.0739 | 1132.7021 | 576.0625 | 1310.6543
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-GORLLWYN HERMON AND TANGLWYST-GORLLWYN TO HERMON | 2.6561 | 4.6167 | 1137.3188 | 575.33 | 1313.3104
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-EASTERN-NONE-(0,70]-WHITBOURNE | 1.5494 | 2.6991 | 1140.0179 | 574.0352 | 1314.8598
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-NEWTON P.O.-CAMBRIDGE WD | 1.7707 | 3.0906 | 1143.1085 | 572.9489 | 1316.6305
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(0,70]-ALWEN_/_DEE-DENBIGH_ALWEN | 1.7707 | 3.0928 | 1146.2012 | 572.5432 | 1318.4013
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(160,320]-ALWEN_/_DEE-DENBIGH_ALWEN-MEIFOD-1104 FOELAS (G10) | 1.7707 | 3.1007 | 1149.3019 | 571.0806 | 1320.172
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(120,160]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-DOLBENMAEN WEST TRUNK -AREA FED BY S/SUPPLY 3A401601 | 1.5494 | 2.7145 | 1152.0164 | 570.7843 | 1321.7214
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-WHITBOURNE-WHITBOURNE-RIDGEWAY STIFFORDS BRIDGE-STIFFORDS BRIDGE | 1.7707 | 3.105 | 1155.1214 | 570.2895 | 1323.4922
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-DUNFIELD_CROSSWAYS-CROSSWAYS NORTH AND HIGH-THE SHAWL | 3.3201 | 5.8569 | 1160.9784 | 566.8725 | 1326.8123
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-DERI GOCH PS TO RHOSYMRYSON SR-CWRTNEWYDD QUARRY | 3.9842 | 7.0326 | 1168.011 | 566.5254 | 1330.7965
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-CRICCIETH LLANYSTUMDWY-GAERDDU BACH | 1.5494 | 2.7469 | 1170.7579 | 564.0497 | 1332.3459
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-BOLTON_HILL-PLUMSTONE TO BRAWDY-DRUIDSTON CROSS | 2.2134 | 3.9411 | 1174.699 | 561.6325 | 1334.5593
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(70,120] | 1.7707 | 3.1538 | 1177.8528 | 561.4701 | 1336.33
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-CERRIG | 3.0988 | 5.5255 | 1183.3783 | 560.8154 | 1339.4288
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-FLINT__CONNAHS_QUAY_BRETTON | 1.7707 | 3.1668 | 1186.5451 | 559.151 | 1341.1996
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE | 2.2134 | 3.9624 | 1190.5075 | 558.6093 | 1343.413
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | 4.6482 | 8.3517 | 1198.8593 | 556.5549 | 1348.0612
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-EPOXY_RESIN-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-TREVETHIN HILL-TREVETHIN L/LEVEL | 1.5494 | 2.7927 | 1201.652 | 554.794 | 1349.6106
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-MEIFOD-CYFFYLLIOG | 2.4348 | 4.389 | 1206.041 | 554.7392 | 1352.0454
DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY-NOTTAGE MAIN-FULMAR ROAD | 2.2134 | 3.9957 | 1210.0368 | 553.9466 | 1354.2588
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-CYNON-MERTHYR__ABERCYNON-PENYWAUN / CEMETERY ROAD-PENYWAUN/CEMETERY RD | 3.7628 | 6.7936 | 1216.8304 | 553.8764 | 1358.0216
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-RHONDDA-MAERDY__PORTH-CYMMER | 1.5494 | 2.7997 | 1219.6301 | 553.4171 | 1359.571
DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN | 3.0988 | 5.6146 | 1225.2447 | 551.9162 | 1362.6698
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_HEATH_&_LLANISHEN-LLANDENNIS ROAD-LLANDENNIS ROAD 10 INCH | 2.8775 | 5.2671 | 1230.5118 | 546.309 | 1365.5473
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH-CAPEL SEION LLANRHYSTUD-CAPEL SEION/LLANRHYSTUD | 1.5494 | 2.8445 | 1233.3564 | 544.6934 | 1367.0967
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PORT_TALBOT_FELINDRE__CRAY-TOLLGATE | 1.9921 | 3.6629 | 1237.0192 | 543.856 | 1369.0888
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-DERI GOCH PS TO RHOSYMRYSON SR-CWRTNEWYDD CWRT FARM | 2.2134 | 4.095 | 1241.1143 | 540.5169 | 1371.3022
DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-CENTRAL-POLYURETHANE-(120,160] | 1.5494 | 2.8853 | 1243.9995 | 537.0065 | 1372.8516
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | 5.5336 | 10.3059 | 1254.3054 | 536.9343 | 1378.3852
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-TRAPP BULK EXPORT-PENYBANC RHOSMAEN LLANDILO | 2.8775 | 5.3818 | 1259.6872 | 534.6643 | 1381.2626
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-ALWEN_/_DEE-DENBIGH_ALWEN-ALWEN TO BWLCH GAP | 1.5494 | 2.9132 | 1262.6004 | 531.8526 | 1382.812
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-VALE_OF_GLAM__RHONDDA_VALLEYS | 1.5494 | 2.9162 | 1265.5166 | 531.3002 | 1384.3614
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-VALE_OF_GLAM__RHONDDA_VALLEYS-LLANTRISANT TANK 12INCH PONTYCLUN | 1.5494 | 2.9221 | 1268.4388 | 530.2286 | 1385.9108
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(120,160] | 1.5494 | 2.9316 | 1271.3704 | 528.5137 | 1387.4602
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-LLANELLI_FELINDRE | 2.4348 | 4.6882 | 1276.0586 | 519.3395 | 1389.895
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-EBBW_VALE__BRYNMAWR-CRAIG DDU | 1.7707 | 3.4101 | 1279.4687 | 519.2604 | 1391.6657
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-POLYURETHANE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-PONTYPOOL WEST-CWMYNYSCOY | 1.5494 | 2.9886 | 1282.4573 | 518.4388 | 1393.2151
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-RHYMNEY__BARGOED | 1.5494 | 2.9924 | 1285.4497 | 517.7761 | 1394.7645
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-SOUTH_MEIRIONNYDD | 1.7707 | 3.4271 | 1288.8769 | 516.6819 | 1396.5353
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(70,120]-RHONDDA-MAERDY__PORTH | 2.4348 | 4.7418 | 1293.6186 | 513.4721 | 1398.9701
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(0,70] | 1.9921 | 3.8801 | 1297.4988 | 513.4058 | 1400.9621
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(0,70]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-CERRIG-BRYN GLAS SRV O/LET | 1.5494 | 3.0293 | 1300.528 | 511.4788 | 1402.5115
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-CENTRAL-NONE | 1.9921 | 3.8971 | 1304.4251 | 511.1715 | 1404.5036
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-MAERDY__PORTH-CASTLE INN BRIDGE-MAESYCOED | 1.5494 | 3.0378 | 1307.4629 | 510.04 | 1406.053
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-CENTRAL-POLYURETHANE-(70,120]-RHONDDA-VALE_OF_GLAM__RHONDDA_VALLEYS | 3.7628 | 7.4013 | 1314.8642 | 508.4033 | 1409.8159
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-PENTREGAT CROSS CONNECTION-PENTREGAT RES OUTLET | 2.2134 | 4.3563 | 1319.2205 | 508.0978 | 1412.0293
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN-SLUVAD A-LLANGIBBY VILLAGE | 1.5494 | 3.0538 | 1322.2743 | 507.3637 | 1413.5787
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-DAFEN__FELINDRE | 1.5494 | 3.0644 | 1325.3387 | 505.6124 | 1415.1281
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-CHAIN ROAD DAN Y DERRY-CHAIN ROAD(UNDERHILL) | 1.7707 | 3.5189 | 1328.8576 | 503.2121 | 1416.8988
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-POLYURETHANE-(70,120] | 1.5494 | 3.0866 | 1331.9442 | 501.9795 | 1418.4482
DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(120,160]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-GOSEN TYN Y FRITH-GOSEN | 1.5494 | 3.1016 | 1335.0458 | 499.5492 | 1419.9976
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(0,70]-ELAN_/_BUILTH-BUILTH-GARTH SR | 2.8775 | 5.7607 | 1340.8065 | 499.4978 | 1422.8751
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | 2.4348 | 4.8863 | 1345.6927 | 498.2891 | 1425.3099
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-POLYURETHANE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-TREVETHIN | 1.5494 | 3.1098 | 1348.8026 | 498.2294 | 1426.8593
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70] | 3.0988 | 6.2282 | 1355.0308 | 497.5396 | 1429.9581
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-LLYN CONWY TRUNK-PENMACHNO/LLYN CONWY SILOAM | 1.5494 | 3.1168 | 1358.1476 | 497.1085 | 1431.5075
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_EAST-LLANRUMNEY PUMPS-LLANRUMNEY PUMP | 2.4348 | 4.9025 | 1363.0501 | 496.6386 | 1433.9422
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-ELAN_/_BUILTH-ELAN-NEUADD SOUTH-HOWEY-BUILTH | 1.7707 | 3.5676 | 1366.6177 | 496.3448 | 1435.713
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(160,320]-NORTH_ERYRI_/_YNYS_MON | 1.9921 | 4.0195 | 1370.6372 | 495.6052 | 1437.7051
DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-BRECON_/_PORTIS-BRECON_BOREHOLES | 1.5494 | 3.1321 | 1373.7693 | 494.6909 | 1439.2545
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | 2.2134 | 4.4817 | 1378.251 | 493.8789 | 1441.4679
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SYNOD INN SR TO RHOSYMRYSON SR-CROESGWYN | 6.4189 | 13.0218 | 1391.2728 | 492.9369 | 1447.8868
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | 1.5494 | 3.151 | 1394.4238 | 491.7206 | 1449.4362
DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-LLANELLI_FELINDRE-FURNACE ROAD TO KIDWELLY RED DMA | 1.9921 | 4.058 | 1398.4818 | 490.9022 | 1451.4283
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAPEL_DEWI-POLIN TO RHYDARGAEAU-RHYDARGAEAU P S | 1.9921 | 4.0586 | 1402.5404 | 490.836 | 1453.4204
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN-LLANYRAVON-LLANYRAVON | 3.0988 | 6.3288 | 1408.8691 | 489.6378 | 1456.5192
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-SALEM SR OUTLET-SALEM LLANFYNYDD | 4.8695 | 9.9712 | 1418.8403 | 488.3614 | 1461.3887
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-POLYURETHANE-(70,120]-PONTSTICILL_LOW_LEVEL-MERTHYR__ABERCYNON | 1.5494 | 3.1788 | 1422.0191 | 487.4173 | 1462.9381
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-CARROG-TYN CEFN TRAFFICLIGHTS. | 2.8775 | 5.9052 | 1427.9243 | 487.2735 | 1465.8156
DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE-MYNYDD NEWYDD TO FFOREST FACH-BLEAN Y MAES | 1.5494 | 3.1898 | 1431.1141 | 485.7387 | 1467.365
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON-WHITFORD SR TO MOSTYN DOCKS | 1.5494 | 3.1987 | 1434.3128 | 484.3825 | 1468.9144
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN | 6.8616 | 14.2112 | 1448.524 | 482.8322 | 1475.776
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-SYCHNANT-MAEN HIR BRYNCROES | 2.6561 | 5.5027 | 1454.0267 | 482.6953 | 1478.4321
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-BANGOR MAESGEIRCHEN-MAESGERCHEN | 1.5494 | 3.2159 | 1457.2426 | 481.7934 | 1479.9815
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RHYMNEY__BARGOED | 1.5494 | 3.2173 | 1460.4598 | 481.5903 | 1481.5309
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-POLYURETHANE-(70,120]-PONTSTICILL_LOW_LEVEL-CAERPHILLY-MAESYCWMMER-MAESYCWMMER | 1.5494 | 3.2232 | 1463.683 | 480.7058 | 1483.0803
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-PONTRHYDFENDIGAID-PONTRHYDFENDIGAID LLANAFAN | 2.4348 | 5.0669 | 1468.7499 | 480.5282 | 1485.5151
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT-RINGWOOD 1 AND 2 | 1.5494 | 3.2273 | 1471.9772 | 480.0898 | 1487.0645
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120] | 4.2055 | 8.7767 | 1480.7539 | 479.1697 | 1491.27
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-BEULAU TO ABERBANC-BLAENGWENLLAN CROSS | 3.3201 | 6.9358 | 1487.6896 | 478.6972 | 1494.5902
DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(120,160] | 2.2134 | 4.6256 | 1492.3152 | 478.5221 | 1496.8036
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF | 1.9921 | 4.1785 | 1496.4937 | 476.7499 | 1498.7957
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-EPOXY_RESIN-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-CEFN PENDEGAR REDUCED DMA-LLANTILLIO | 3.5415 | 7.4396 | 1503.9333 | 476.0326 | 1502.3372
DIAM_LT_320-FERROUS_1-<=320mm-B04_1880-1881_1900-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT | 1.5494 | 3.2653 | 1507.1986 | 474.5042 | 1503.8866
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY | 3.0988 | 6.5387 | 1513.7372 | 473.9174 | 1506.9854
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL-PLUMSTONE TO BRAWDY-DRUIDSTON CROSS | 2.2134 | 4.6737 | 1518.4109 | 473.5946 | 1509.1988
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-CLWYD_COASTAL-ABERGELE__RHYL_GLASCOED-RHUALLT TO BODFARI-0702TREMEIRCHION/BODFARI (R70) | 2.4348 | 5.1457 | 1523.5566 | 473.1679 | 1511.6336
DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120] | 1.5494 | 3.2862 | 1526.8428 | 471.4828 | 1513.183
DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN | 1.7707 | 3.7616 | 1530.6045 | 470.7388 | 1514.9537
DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(0,70] | 2.8775 | 6.1236 | 1536.7281 | 469.8966 | 1517.8312
DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(120,160]-PEMBROKESHIRE-PRESELI_SUPPLY | 2.2134 | 4.7199 | 1541.4479 | 468.9613 | 1520.0446
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-CARROG-TY CERRIG 6 INCH | 1.9921 | 4.2704 | 1545.7183 | 466.484 | 1522.0367
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-RHOSHILL TO CROSSROADS-RHOSHILL CROSSROADS WD | 1.5494 | 3.3337 | 1549.052 | 464.7746 | 1523.5861
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL-WEOBLEY SOUTH | 1.7707 | 3.8274 | 1552.8794 | 462.6466 | 1525.3568
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-MONA TO HOLLAND ARMS-CEFN CWMWD TO BETHEL | 4.4269 | 9.5703 | 1562.4497 | 462.5615 | 1529.7837
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE | 2.4348 | 5.2894 | 1567.7391 | 460.3154 | 1532.2184
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-RHONDDA-MAERDY__PORTH-MAERDY HP OUTLET | 1.7707 | 3.8701 | 1571.6092 | 457.5389 | 1533.9892
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN | 2.4348 | 5.3294 | 1576.9386 | 456.8574 | 1536.424
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-SOUTH_MEIRIONNYDD-PENNAL__CORRIS_SEVERN_TRENT-CORRIS | 3.3201 | 7.3288 | 1584.2675 | 453.0237 | 1539.7441
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY-LLANGEWYDD-LLANGEWYDD | 1.7707 | 3.911 | 1588.1785 | 452.7594 | 1541.5148
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY-NOTTAGE MAIN | 1.9921 | 4.4018 | 1592.5802 | 452.5646 | 1543.5069
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PORT_TALBOT_FELINDRE__CRAY-TY CANOL PUMPED OUTLET | 1.5494 | 3.4355 | 1596.0157 | 450.9984 | 1545.0563
DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-ALWEN_/_DEE | 1.7707 | 3.9297 | 1599.9454 | 450.6038 | 1546.8271
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__RUMNEY | 1.9921 | 4.423 | 1604.3684 | 450.396 | 1548.8192
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN-LLANDERFEL | 2.2134 | 4.9217 | 1609.2901 | 449.7266 | 1551.0326
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-RHOSYMRYSON TO PENRHYWLLAN | 2.4348 | 5.4299 | 1614.72 | 448.4022 | 1553.4674
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH | 1.7707 | 3.9506 | 1618.6706 | 448.2204 | 1555.2381
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-PRESELI_SUPPLY | 1.7707 | 3.9705 | 1622.6411 | 445.9715 | 1557.0088
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-DERI GOCH PS TO RHOSYMRYSON SR-FFYNON RHYS | 2.4348 | 5.5141 | 1628.1552 | 441.5523 | 1559.4436
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE | 1.7707 | 4.0593 | 1632.2145 | 436.223 | 1561.2143
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH__BARRY | 1.5494 | 3.5533 | 1635.7678 | 436.0433 | 1562.7637
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-POLYURETHANE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-EBBW_VALE__BRYNMAWR | 3.5415 | 8.1362 | 1643.904 | 435.2736 | 1566.3052
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT | 3.0988 | 7.1194 | 1651.0234 | 435.2638 | 1569.404
DIAM_LT_320-STEEL-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(160,320]-PEMBROKESHIRE-BOLTON_HILL-TEMPLETON TO MARTLETWY-CROSSHANDS VILLAGE | 1.7707 | 4.0694 | 1655.0928 | 435.1336 | 1571.1748
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-LLANELLI_FELINDRE | 1.5494 | 3.5616 | 1658.6544 | 435.0311 | 1572.7242
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA | 2.6561 | 6.1077 | 1664.7621 | 434.878 | 1575.3803
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-VALE_OF_GLAM__RHONDDA_VALLEYS | 2.8775 | 6.6235 | 1671.3856 | 434.4307 | 1578.2577
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-CAERGEILIOG SCHOOL 150-REFAIL CROSSROADS TO RHOSCOLY | 1.5494 | 3.5678 | 1674.9534 | 434.275 | 1579.8071
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-LLANELLI_FELINDRE | 1.5494 | 3.5694 | 1678.5228 | 434.0778 | 1581.3565
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(160,320]-ELAN_/_BUILTH-ELAN | 1.5494 | 3.5806 | 1682.1034 | 432.7235 | 1582.9059
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | 5.0909 | 11.7898 | 1693.8932 | 431.8057 | 1587.9968
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-RHOSYMRYSON TO PENRHYWLLAN-HOREB BANGOR TEIFI | 1.7707 | 4.1171 | 1698.0103 | 430.0925 | 1589.7676
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA | 1.9921 | 4.6609 | 1702.6712 | 427.4072 | 1591.7597
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY-NEWTON NOTTAGE-NEWTON NOTTAGE | 2.4348 | 5.7028 | 1708.374 | 426.9429 | 1594.1944
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA | 3.0988 | 7.2639 | 1715.6379 | 426.6007 | 1597.2932
DIAM_LT_320-FERROUS_1-<=320mm-B04_1880-PRE_1880-NORTHERN | 2.2134 | 5.2029 | 1720.8408 | 425.4228 | 1599.5067
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-NEWQUAY-SYNOD INN TO NEW QUAY 6 | 2.4348 | 5.736 | 1726.5768 | 424.4722 | 1601.9414
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH-CAPEL SEION LLANRHYSTUD-ABERMAD TO LLANRHYSTUD | 1.7707 | 4.1751 | 1730.7519 | 424.1171 | 1603.7122
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-EASTERN-NONE-(120,160]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL-WESTHIDE HEREFORD | 1.5494 | 3.6672 | 1734.4191 | 422.5038 | 1605.2616
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | 1.9921 | 4.7184 | 1739.1375 | 422.196 | 1607.2537
DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-CEMENT_MORTAR-(120,160] | 2.4348 | 5.7834 | 1744.9209 | 420.9912 | 1609.6884
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF-PENTREBANE NORTH-PENTREBANE NORTH | 1.5494 | 3.6876 | 1748.6085 | 420.1642 | 1611.2378
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM | 1.9921 | 4.7583 | 1753.3668 | 418.6519 | 1613.2299
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CRAY__CLYDACH | 2.6561 | 6.3517 | 1759.7185 | 418.174 | 1615.886
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF | 1.5494 | 3.7195 | 1763.4381 | 416.556 | 1617.4354
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON-RHOSESMOR BERTH DDU | 1.5494 | 3.726 | 1767.164 | 415.8398 | 1618.9848
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(70,120]-CYNON-ABERDARE_HIRWAUN__PONSTICILL | 1.5494 | 3.7308 | 1770.8949 | 415.2959 | 1620.5342
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-PENTIR BRYNREFAIL | 1.7707 | 4.2656 | 1775.1605 | 415.1185 | 1622.305
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_HEATH_&_LLANISHEN | 3.3201 | 8.0149 | 1783.1754 | 414.2483 | 1625.6251
DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-EASTERN-EPOXY_RESIN-(70,120] | 4.8695 | 11.7602 | 1794.9356 | 414.0692 | 1630.4947
DIAM_LT_320-FERROUS_1-<=320mm-B05_1890-1881_1900-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__RUMNEY | 3.7628 | 9.1146 | 1804.0502 | 412.8353 | 1634.2575
DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN | 1.9921 | 4.8547 | 1808.9049 | 410.3388 | 1636.2496
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN | 2.8775 | 7.0228 | 1815.9277 | 409.7318 | 1639.127
DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-PENWCH SERVICE RES OUTLET-BETHANIA TREFENTER | 1.7707 | 4.3223 | 1820.25 | 409.6738 | 1640.8978
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_WEST | 3.0988 | 7.5705 | 1827.8205 | 409.3253 | 1643.9966
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-EPOXY_RESIN-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_HEATH_&_LLANISHEN | 2.2134 | 5.4099 | 1833.2305 | 409.1416 | 1646.21
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-NORTH_ERYRI_/_YNYS_MON | 2.4348 | 5.9678 | 1839.1983 | 407.9831 | 1648.6448
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(120,160]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-CERRIG-CERRIGYDRUDION SRV O/LET | 1.9921 | 4.8866 | 1844.0849 | 407.6643 | 1650.6368
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-ACCRE OUTLET-ACCRE/LLANDEGLA | 1.7707 | 4.3715 | 1848.4564 | 405.0651 | 1652.4076
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-PENMORFA-PENMORFA RES OUTLET-PRENTEG | 1.5494 | 3.8275 | 1852.2838 | 404.8083 | 1653.957
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-ELAN_/_BUILTH-BUILTH-BUILTH WELLS-BUILTH TO ABERDW | 3.0988 | 7.6629 | 1859.9468 | 404.3878 | 1657.0558
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-CEMENT_MORTAR-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-MONA TO HOLLAND ARMS-PENTRE BERW TO LLANGAFFO | 1.5494 | 3.8419 | 1863.7887 | 403.2922 | 1658.6052
DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-CEMENT_MORTAR-(70,120] | 1.5494 | 3.8437 | 1867.6324 | 403.0983 | 1660.1546
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-CENTRAL-NONE-(70,120]-RHONDDA-MAERDY__PORTH-FURNACE ROAD | 1.9921 | 4.9533 | 1872.5857 | 402.1748 | 1662.1467
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-EASTERN-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_SW__RISCA__ABERCARN | 3.3201 | 8.2743 | 1880.86 | 401.2586 | 1665.4668
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(0,70]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM | 1.5494 | 3.8631 | 1884.7231 | 401.0745 | 1667.0162
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAPEL_DEWI-STONECUTTER TALOG ABERNANT-ABERNANT BPT OUTLET | 2.8775 | 7.1855 | 1891.9086 | 400.4529 | 1669.8937
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | 2.2134 | 5.5303 | 1897.4389 | 400.2365 | 1672.1071
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-POLYURETHANE-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | 3.3201 | 8.2965 | 1905.7354 | 400.1877 | 1675.4272
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON-BUCKLEY PRECINCT WAY-PRECINCT WAYBUCKLEY. | 1.9921 | 4.9969 | 1910.7323 | 398.6644 | 1677.4193
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_HEATH_&_LLANISHEN | 2.8775 | 7.2435 | 1917.9758 | 397.2458 | 1680.2968
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PENDINE-BRANDY HILL TO ST. CLEARS | 2.4348 | 6.1404 | 1924.1162 | 396.5165 | 1682.7316
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-EPOXY_RESIN-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-VARTEG-VARTEG VILLAGE | 2.4348 | 6.1821 | 1930.2983 | 393.8452 | 1685.1663
DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | 2.4348 | 6.1843 | 1936.4826 | 393.7004 | 1687.6011
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_EAST-TY DRAW ROAD | 1.7707 | 4.4997 | 1940.9823 | 393.5234 | 1689.3718
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | 1.5494 | 3.9435 | 1944.9258 | 392.9021 | 1690.9212
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-CEMENT_MORTAR-(70,120]-PEMBROKESHIRE-BOLTON_HILL | 2.6561 | 6.7603 | 1951.686 | 392.9015 | 1693.5774
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-PILLETH-PILLETH_KNIGHTON__BLEDDFA-WHITTON BEGGARS BUSH | 2.2134 | 5.6352 | 1957.3213 | 392.7845 | 1695.7908
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(120,160]-NORTH_ERYRI_/_YNYS_MON-EAST_ANGLESEY_CEFNI | 2.2134 | 5.6395 | 1962.9608 | 392.4838 | 1698.0042
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-CEMENT_MORTAR-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD | 1.9921 | 5.0757 | 1968.0365 | 392.4747 | 1699.9963
DIAM_LT_320-FERROUS_1-<=320mm-B05_1890-1881_1900-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | 2.2134 | 5.6537 | 1973.6902 | 391.5028 | 1702.2097
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(70,120]-MONMOUTH-MONMOUTH_MAYHILL | 1.5494 | 3.9595 | 1977.6496 | 391.3145 | 1703.7591
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-PONTYPRIDD_PONTSTICILL_HIGH-RHYDYFELIN LOW LEVEL BULK-RHYDYFELIN L.L. BULK | 1.5494 | 3.9627 | 1981.6123 | 390.9972 | 1705.3085
DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE | 1.5494 | 3.9657 | 1985.578 | 390.6999 | 1706.8579
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 3.3201 | 8.5221 | 1994.1002 | 389.5909 | 1710.1781
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD | 4.4269 | 11.3849 | 2005.485 | 388.837 | 1714.6049
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-POLYURETHANE-(70,120]-RHONDDA-VALE_OF_GLAM__RHONDDA_VALLEYS | 1.7707 | 4.5566 | 2010.0416 | 388.6098 | 1716.3757
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | 1.5494 | 3.9888 | 2014.0305 | 388.4339 | 1717.9251
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-CEFN BRYN HOUSE | 2.4348 | 6.2703 | 2020.3008 | 388.2996 | 1720.3598
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN | 2.6561 | 6.8497 | 2027.1505 | 387.7732 | 1723.016
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(160,320]-NORTH_ERYRI_/_YNYS_MON | 1.5494 | 3.9993 | 2031.1498 | 387.4169 | 1724.5654
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD | 3.5415 | 9.1606 | 2040.3104 | 386.5991 | 1728.1068
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL | 2.2134 | 5.7265 | 2046.0369 | 386.5214 | 1730.3203
DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 2.2134 | 5.7288 | 2051.7657 | 386.3703 | 1732.5337
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-SOUTH_ANGLESEY_CWELLYN__MYNYDD | 1.7707 | 4.5919 | 2056.3576 | 385.6267 | 1734.3044
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-EPOXY_RESIN-(70,120] | 1.5494 | 4.0244 | 2060.3819 | 385.0038 | 1735.8538
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-EPOXY_RESIN-(70,120]-ROSS-ON-WYE-ROSS-ON-WYE_MITCHELDEAN | 1.5494 | 4.0275 | 2064.4094 | 384.7051 | 1737.4032
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O | 1.7707 | 4.6067 | 2069.0161 | 384.3839 | 1739.174
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-POLYURETHANE-(70,120]-PONTSTICILL_LOW_LEVEL-VALE_OF_GLAM__RHONDDA_VALLEYS | 1.7707 | 4.6097 | 2073.6258 | 384.1362 | 1740.9447
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-EASTERN-POLYURETHANE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RASSAU__SIRHOWY_VALLEY | 1.9921 | 5.1876 | 2078.8134 | 384.0088 | 1742.9368
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL | 1.5494 | 4.0552 | 2082.8686 | 382.0807 | 1744.4862
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-EASTERN-NONE-(70,120]-PILLETH-PILLETH_KNIGHTON__BLEDDFA | 1.5494 | 4.0589 | 2086.9275 | 381.7248 | 1746.0356
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_HEATH_&_LLANISHEN | 2.4348 | 6.3868 | 2093.3144 | 381.2166 | 1748.4704
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 1.7707 | 4.6454 | 2097.9598 | 381.1827 | 1750.2411
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-LLANHILLETH | 2.2134 | 5.8133 | 2103.773 | 380.7548 | 1752.4545
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-CERRIG | 1.5494 | 4.0995 | 2107.8726 | 377.9448 | 1754.0039
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | 6.8616 | 18.1773 | 2126.0499 | 377.4826 | 1760.8656
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-BOLTON_HILL-BRAWDY TO FELINWYNT-BRAWDY FELINWYNT | 3.0988 | 8.212 | 2134.2619 | 377.3509 | 1763.9644
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-GORLLWYN RHOS TREALAU-TREALAU RES OUTLET | 3.3201 | 8.8023 | 2143.0642 | 377.1896 | 1767.2845
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(0,70]-SLUVAD__COURT_FARM__LLWYNON | 1.5494 | 4.1092 | 2147.1734 | 377.0549 | 1768.8339
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-CARMEL AND PENTREGWENLAIS | 1.9921 | 5.2919 | 2152.4653 | 376.4405 | 1770.826
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_EAST-NORTH PENTWYN SOUTH-NORTH PENTWYN SOUTH | 1.5494 | 4.116 | 2156.5813 | 376.436 | 1772.3754
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL | 1.7707 | 4.7049 | 2161.2862 | 376.3609 | 1774.1461
DIAM_LT_320-FERROUS_1-<=320mm-B05_1890-1881_1900-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_WEST | 2.4348 | 6.4704 | 2167.7566 | 376.2919 | 1776.5809
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(160,320]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SYNOD INN SR TO RHOSYMRYSON SR | 2.4348 | 6.4782 | 2174.2349 | 375.8384 | 1779.0157
DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | 1.7707 | 4.7119 | 2178.9467 | 375.8052 | 1780.7864
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-CENTRAL-NONE-(70,120]-RHONDDA-MAERDY__PORTH | 6.1976 | 16.5057 | 2195.4524 | 375.4824 | 1786.984
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-BRYNGWYN | 1.7707 | 4.7251 | 2200.1775 | 374.7536 | 1788.7548
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-CAPEL_DEWI | 1.5494 | 4.1435 | 2204.321 | 373.9372 | 1790.3042
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-WESTERN | 1.5494 | 4.1556 | 2208.4766 | 372.8448 | 1791.8536
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-RHYMNEY__BARGOED-QUAKERS YARD 31INCH | 1.7707 | 4.764 | 2213.2406 | 371.6925 | 1793.6243
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | 1.7707 | 4.7678 | 2218.0084 | 371.3969 | 1795.3951
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-EPOXY_RESIN-(70,120]-PONTSTICILL_LOW_LEVEL-CAERPHILLY | 1.7707 | 4.7771 | 2222.7854 | 370.677 | 1797.1658
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CRAY__CLYDACH | 3.3201 | 8.9634 | 2231.7488 | 370.4124 | 1800.4859
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-POLYURETHANE-(70,120] | 1.5494 | 4.1851 | 2235.9339 | 370.2173 | 1802.0353
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-POLYURETHANE-(70,120]-TYWI_C.U._AREA | 1.9921 | 5.3936 | 2241.3275 | 369.3432 | 1804.0274
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70] | 1.9921 | 5.3968 | 2246.7243 | 369.1243 | 1806.0195
DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | 1.9921 | 5.3977 | 2252.122 | 369.0619 | 1808.0116
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-EPOXY_RESIN-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-CEFN PENDEGAR REDUCED DMA-BRYN DERI | 1.5494 | 4.1982 | 2256.3202 | 369.0614 | 1809.561
DIAM_LT_320-STEEL-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(160,320]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_SW__RISCA__ABERCARN | 1.7707 | 4.8201 | 2261.1404 | 367.3627 | 1811.3317
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__RUMNEY | 2.4348 | 6.6308 | 2267.7711 | 367.1917 | 1813.7665
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__CANTON__CATHAYS | 1.7707 | 4.8271 | 2272.5982 | 366.8361 | 1815.5373
DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-EPOXY_RESIN-(70,120] | 1.9921 | 5.445 | 2278.0432 | 365.8533 | 1817.5293
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-LITTLE MILL TO USK-USK-LLANGIBBY | 1.5494 | 4.2554 | 2282.2987 | 364.0997 | 1819.0787
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-CENTRAL-NONE-(70,120] | 3.3201 | 9.1402 | 2291.4389 | 363.2464 | 1822.3989
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-NORTH_CEREDIGION-ABERYSTWYTH_BONTGOCH__LOVESGROVE | 1.7707 | 4.8806 | 2296.3195 | 362.8129 | 1824.1696
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-EPOXY_RESIN-(70,120] | 2.2134 | 6.1027 | 2302.4222 | 362.6962 | 1826.3831
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-POLYURETHANE-(120,160]-TALYBONT-ABERGAVENNY__CWMTILLERY | 2.6561 | 7.3253 | 2309.7475 | 362.593 | 1829.0392
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION | 2.2134 | 6.1094 | 2315.8569 | 362.2998 | 1831.2526
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(70,120] | 4.2055 | 11.6219 | 2327.4788 | 361.8617 | 1835.4581
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-MONMOUTH-TRELLECH__MAYHILL__FYNNON_GAER-TRELLECK-CATBROOK | 1.5494 | 4.2826 | 2331.7614 | 361.7854 | 1837.0075
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-PEMBROKESHIRE | 1.7707 | 4.8993 | 2336.6607 | 361.4294 | 1838.7783
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA | 7.5257 | 20.8369 | 2357.4975 | 361.1705 | 1846.3039
DIAM_LT_320-STEEL-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(160,320]-PEMBROKESHIRE-PRESELI_SUPPLY-TENBY MAIN | 3.3201 | 9.2119 | 2366.7095 | 360.4175 | 1849.624
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(120,160]-HEREFORD_C.U._AREA-HEREFORD__SOUTH_BROOMY_HILL_ | 2.4348 | 6.7581 | 2373.4676 | 360.2722 | 1852.0588
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_EAST | 1.5494 | 4.3021 | 2377.7697 | 360.153 | 1853.6082
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-WESTERN-POLYURETHANE-(70,120]-TYWI_C.U._AREA | 2.2134 | 6.163 | 2383.9327 | 359.1453 | 1855.8216
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(120,160]-PEMBROKESHIRE | 1.7707 | 4.9396 | 2388.8723 | 358.4775 | 1857.5924
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM | 2.8775 | 8.051 | 2396.9234 | 357.4016 | 1860.4698
DIAM_LT_320-ALKATHENE-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH | 1.9921 | 5.5747 | 2402.4981 | 357.343 | 1862.4619
DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-CENTRAL-POLYURETHANE-(70,120]-CYNON-ABERDARE_HIRWAUN__PONSTICILL | 1.5494 | 4.3368 | 2406.8349 | 357.2661 | 1864.0113
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN-PONTNEWYDD-MAENDY WAY TOP | 1.7707 | 4.9681 | 2411.803 | 356.4235 | 1865.7821
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 3.9842 | 11.1844 | 2422.9874 | 356.2246 | 1869.7662
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | 2.2134 | 6.2294 | 2429.2168 | 355.3204 | 1871.9797
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH | 1.5494 | 4.3659 | 2433.5827 | 354.8857 | 1873.5291
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-EPOXY_RESIN-(70,120]-PEMBROKESHIRE | 1.5494 | 4.3699 | 2437.9526 | 354.5627 | 1875.0785
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-CENTRAL-NONE | 1.5494 | 4.3762 | 2442.3288 | 354.0516 | 1876.6279
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PENCOED__BRIDGEND_VALLEYS | 2.4348 | 6.8788 | 2449.2076 | 353.9552 | 1879.0626
DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(70,120]-RHONDDA | 2.8775 | 8.1734 | 2457.3809 | 352.0531 | 1881.9401
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | 6.8616 | 19.4945 | 2476.8754 | 351.9776 | 1888.8017
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-DUNFIELD_CROSSWAYS-CROSSWAYS NORTH AND HIGH-PHONEBOX BRILLEY | 1.9921 | 5.664 | 2482.5395 | 351.7079 | 1890.7938
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(120,160]-BALA-BALA-ARENIG TRUNK MAINS-LLANERCH ARENIG NEW DMA | 1.9921 | 5.6694 | 2488.2089 | 351.3731 | 1892.7859
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_WEST | 3.5415 | 10.0796 | 2498.2885 | 351.3519 | 1896.3274
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-POLYURETHANE-(70,120]-PONTSTICILL_LOW_LEVEL-CAERPHILLY | 2.4348 | 6.9329 | 2505.2214 | 351.192 | 1898.7622
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(0,70] | 3.9842 | 11.3475 | 2516.5689 | 351.1061 | 1902.7463
DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(0,70] | 1.5494 | 4.4448 | 2521.0137 | 348.5873 | 1904.2957
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-MONMOUTH-TRELLECH__MAYHILL__FYNNON_GAER-TRELLECK-PENALLT | 2.4348 | 6.9887 | 2528.0024 | 348.386 | 1906.7305
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-BEULAU TO ABERBANC-BLAENGWENLLAN CROSS | 1.5494 | 4.4493 | 2532.4517 | 348.2335 | 1908.2799
DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-ELAN_/_BUILTH-ELAN-NEUADD NORTH | 2.8775 | 8.2851 | 2540.7368 | 347.3032 | 1911.1574
DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(120,160] | 1.7707 | 5.1008 | 2545.8376 | 347.1524 | 1912.9281
DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_EAST | 1.7707 | 5.1021 | 2550.9397 | 347.0627 | 1914.6988
DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN | 1.7707 | 5.1041 | 2556.0438 | 346.9227 | 1916.4696
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | 1.5494 | 4.4696 | 2560.5134 | 346.6554 | 1918.019
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-PONTYPRIDD_PONTSTICILL_HIGH-RHYDYFELIN LOW LEVEL BULK-RHYDYFELIN L.L. BULK | 1.7707 | 5.1106 | 2565.624 | 346.4838 | 1919.7897
DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-ALWEN TO PEN Y COED & ACCRE TRUNK-ERYRYS PUMPING STATION | 1.5494 | 4.4887 | 2570.1127 | 345.1774 | 1921.3391
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-BRYNIAU (CONWY)-BRYNIAU RES OUTLET | 3.5415 | 10.2625 | 2580.3752 | 345.091 | 1924.8806
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON | 2.2134 | 6.4331 | 2586.8082 | 344.0711 | 1927.094
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-PONTYPRIDD_PONTSTICILL_HIGH-CILFYNDD SR AND TY GWYN 9IN OUTLET | 2.6561 | 7.7379 | 2594.5462 | 343.2589 | 1929.7502
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 4.4269 | 12.9324 | 2607.4785 | 342.3085 | 1934.177
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-CENTRAL-EPOXY_RESIN | 1.5494 | 4.5294 | 2612.0079 | 342.074 | 1935.7264
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-CERRIG-RHYDLYDAN PENTREFOELAS SRV O/L | 1.5494 | 4.5385 | 2616.5465 | 341.3877 | 1937.2758
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940 | 1.9921 | 5.8399 | 2622.3864 | 341.1168 | 1939.2679
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-MID_-_SOUTH_CEREDIGION-LLECHRYD | 3.0988 | 9.1075 | 2631.4938 | 340.2485 | 1942.3667
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-SYCHNANT | 1.5494 | 4.5657 | 2636.0595 | 339.3557 | 1943.9161
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__RUMNEY | 1.5494 | 4.5912 | 2640.6508 | 337.4709 | 1945.4655
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 4.6482 | 13.8036 | 2654.4544 | 336.7378 | 1950.1137
DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CRAY__CLYDACH-CAEHOPKIN AND PENYCAE | 1.5494 | 4.6082 | 2659.0626 | 336.2233 | 1951.6631
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__SOUTH_BROOMY_HILL_ | 1.5494 | 4.609 | 2663.6716 | 336.1682 | 1953.2125
DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-EASTERN-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 1.7707 | 5.2726 | 2668.9442 | 335.8389 | 1954.9832
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-UWCH Y DRE CYNWYD-LLANDRILLO | 1.7707 | 5.2739 | 2674.2181 | 335.7562 | 1956.754
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-EPOXY_RESIN-(70,120]-PEMBROKESHIRE-PRESELI_SUPPLY-PRESELI DOLWEN-EITHBED OUTLET | 2.4348 | 7.2533 | 2681.4714 | 335.6785 | 1959.1887
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-CEMENT_MORTAR-(120,160]-PEMBROKESHIRE-PRESELI_SUPPLY-MOUNTAIN TREFFGARNE AND RUDBAXTON-PLUMSTONE TO TREFFGARNE | 1.7707 | 5.2817 | 2686.7531 | 335.2575 | 1960.9595
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | 1.9921 | 5.9475 | 2692.7006 | 334.9442 | 1962.9516
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE | 1.9921 | 5.9516 | 2698.6522 | 334.7156 | 1964.9437
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-EPOXY_RESIN-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY | 3.0988 | 9.3 | 2707.9523 | 333.2029 | 1968.0425
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-RHONDDA-MAERDY__PORTH | 6.8616 | 20.6435 | 2728.5957 | 332.3873 | 1974.9041
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-CEFN BRYN HOUSE-LLANGENNITH WD | 1.5494 | 4.6615 | 2733.2572 | 332.3841 | 1976.4535
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-POLYURETHANE-(70,120] | 1.7707 | 5.3276 | 2738.5848 | 332.3718 | 1978.2242
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PRESELI_SUPPLY-PRESELI USL OUTLETS-WISTON | 3.9842 | 11.9922 | 2750.577 | 332.2289 | 1982.2084
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | 1.7707 | 5.3327 | 2755.9098 | 332.0521 | 1983.9791
DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-EASTERN-POLYURETHANE-(70,120] | 2.4348 | 7.3755 | 2763.2853 | 330.114 | 1986.4139
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM | 1.9921 | 6.0447 | 2769.33 | 329.5599 | 1988.406
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-MERTHYR__ABERCYNON-GALON UCHAF ESTATE-GALON UCHAF ESTATE | 2.4348 | 7.3947 | 2776.7247 | 329.2602 | 1990.8408
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(160,320]-ALWEN_/_DEE | 2.4348 | 7.3981 | 2784.1228 | 329.1063 | 1993.2755
DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD | 3.5415 | 10.772 | 2794.8948 | 328.768 | 1996.817
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-GOSEN TYN Y FRITH-T1 TO RHYD Y FOEL | 1.7707 | 5.3959 | 2800.2907 | 328.1653 | 1998.5878
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 1.5494 | 4.7219 | 2805.0126 | 328.1311 | 2000.1372
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-DUNFIELD_CROSSWAYS-CROSSWAYS NORTH AND HIGH-BRILLEY SCHOOL | 3.5415 | 10.802 | 2815.8146 | 327.8531 | 2003.6787
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-VOWCHURCH-VOWCHURCH-BRAMPTON SR-SARAS CROSS (LONGTOWN) | 1.7707 | 5.4155 | 2821.2301 | 326.9776 | 2005.4494
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(120,160]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | 1.9921 | 6.105 | 2827.3351 | 326.305 | 2007.4415
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE | 2.6561 | 8.1666 | 2835.5017 | 325.2404 | 2010.0976
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160] | 2.2134 | 6.8078 | 2842.3095 | 325.1314 | 2012.311
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_WEST | 1.5494 | 4.7656 | 2847.0751 | 325.1197 | 2013.8604
DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(120,160]-PEMBROKESHIRE-BOLTON_HILL-PLUMSTONE TO BRAWDY-CUFFERN/SIMPSON CROSS | 1.7707 | 5.4483 | 2852.5235 | 325.0063 | 2015.6312
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-EPOXY_RESIN-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL-WEOBLEY SOUTH-NORTON WOOD | 2.8775 | 8.8654 | 2861.3888 | 324.5724 | 2018.5086
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-MERTHYR__ABERCYNON | 1.9921 | 6.1398 | 2867.5286 | 324.4545 | 2020.5007
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_EAST | 2.4348 | 7.5165 | 2875.0451 | 323.9237 | 2022.9355
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-EPOXY_RESIN-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RASSAU__SIRHOWY_VALLEY | 3.0988 | 9.6167 | 2884.6618 | 322.2313 | 2026.0343
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-EPOXY_RESIN-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN | 3.9842 | 12.3668 | 2897.0287 | 322.1656 | 2030.0185
DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-POLYURETHANE-(70,120]-TYWI_C.U._AREA-BRYNGWYN | 2.6561 | 8.263 | 2905.2917 | 321.4453 | 2032.6746
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(120,160]-PEMBROKESHIRE-BOLTON_HILL-TEMPLETON TO MARTLETWY | 1.5494 | 4.8237 | 2910.1154 | 321.2042 | 2034.224
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-DUNFIELD_CROSSWAYS | 1.9921 | 6.2137 | 2916.3291 | 320.5969 | 2036.216
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(160,320]-TALYBONT-ABERGAVENNY__CWMTILLERY | 2.6561 | 8.2861 | 2924.6152 | 320.551 | 2038.8722
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-EASTERN-NONE-(70,120] | 2.4348 | 7.6225 | 2932.2377 | 319.4191 | 2041.3069
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-WHITBOURNE-WHITBOURNE | 2.6561 | 8.3185 | 2940.5562 | 319.3007 | 2043.963
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | 3.9842 | 12.4874 | 2953.0436 | 319.0565 | 2047.9472
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_WEST | 1.5494 | 4.859 | 2957.9026 | 318.8725 | 2049.4966
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-DERI GOCH PS TO RHOSYMRYSON SR-CAPEL Y GROES TO LLANWNEN | 1.5494 | 4.8674 | 2962.7699 | 318.3244 | 2051.046
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-CENTRAL | 2.4348 | 7.6535 | 2970.4234 | 318.1244 | 2053.4808
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE-WYCHTREE MORFYDD PENTREMALWED | 1.5494 | 4.8712 | 2975.2946 | 318.0762 | 2055.0302
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-PENTREGAT CROSS CONNECTION-BRYNHOFFNANT RHYDLEWIS | 1.5494 | 4.8751 | 2980.1697 | 317.8212 | 2056.5796
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-POLYURETHANE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O | 2.4348 | 7.6613 | 2987.831 | 317.8007 | 2059.0144
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-CEMENT_MORTAR-(70,120]-PEMBROKESHIRE-BOLTON_HILL | 1.7707 | 5.5719 | 2993.4029 | 317.7963 | 2060.7851
DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | 1.5494 | 4.8758 | 2998.2788 | 317.7705 | 2062.3345
DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(70,120]-CYNON | 1.5494 | 4.8768 | 3003.1556 | 317.708 | 2063.8839
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-PENARTH | 1.5494 | 4.8862 | 3008.0418 | 317.0962 | 2065.4333
DIAM_LT_320-FERROUS_1-<=320mm-B01_1850-PRE_1880-NORTHERN | 1.9921 | 6.3191 | 3014.3609 | 315.2474 | 2067.4254
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-EASTERN-NONE-(70,120] | 4.6482 | 14.7763 | 3029.1373 | 314.5703 | 2072.0736
DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM | 2.6561 | 8.4515 | 3037.5888 | 314.277 | 2074.7297
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | 2.6561 | 8.4678 | 3046.0566 | 313.6722 | 2077.3858
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PRESELI_SUPPLY-CROESFORDD OUTLET | 1.9921 | 6.3562 | 3052.4128 | 313.4073 | 2079.3779
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY | 1.7707 | 5.653 | 3058.0658 | 313.2388 | 2081.1486
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-POLYURETHANE-(70,120]-PONTSTICILL_LOW_LEVEL-MERTHYR__ABERCYNON | 1.7707 | 5.672 | 3063.7378 | 312.1914 | 2082.9194
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-MERTHYR__ABERCYNON | 1.5494 | 4.977 | 3068.7147 | 311.3139 | 2084.4688
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | 2.2134 | 7.1227 | 3075.8374 | 310.7573 | 2086.6822
DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAERAU__YSTRADFELLTE | 3.0988 | 10.0027 | 3085.8401 | 309.7961 | 2089.781
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-WAUNLLWYD TO GORLLWYN -CAPEL IWAN TO CENARTH | 5.7549 | 18.6134 | 3104.4535 | 309.1815 | 2095.5359
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(120,160]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | 3.3201 | 10.7619 | 3115.2154 | 308.509 | 2098.8561
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-TRAPP BULK EXPORT-PENYBANK/NANTGARDEIG 6 INCH | 1.7707 | 5.7406 | 3120.956 | 308.4593 | 2100.6268
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-BRYNGWYN | 2.2134 | 7.2026 | 3128.1587 | 307.3079 | 2102.8402
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-MAERDY__PORTH | 1.5494 | 5.047 | 3133.2056 | 306.9958 | 2104.3896
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-BITUMEN-(70,120]-HEREFORD_C.U._AREA | 2.4348 | 7.9394 | 3141.145 | 306.6705 | 2106.8244
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-VALE_OF_GLAM__RHONDDA_VALLEYS | 1.5494 | 5.0536 | 3146.1986 | 306.5938 | 2108.3738
DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-WHITBOURNE-WHITBOURNE | 1.5494 | 5.0619 | 3151.2605 | 306.0919 | 2109.9232
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-MONMOUTH-TRELLECH__MAYHILL__FYNNON_GAER-TRELLECK | 4.6482 | 15.2062 | 3166.4667 | 305.6783 | 2114.5714
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-EPOXY_RESIN-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY | 2.6561 | 8.7155 | 3175.1821 | 304.7579 | 2117.2275
DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-CENTRAL-POLYURETHANE-(70,120]-PONTSTICILL_LOW_LEVEL | 1.5494 | 5.1028 | 3180.285 | 303.6348 | 2118.7769
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-SYCHNANT-RHOSHIRWAEN HALL | 3.3201 | 10.9472 | 3191.2322 | 303.2879 | 2122.0971
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | 2.4348 | 8.0434 | 3199.2755 | 302.7043 | 2124.5318
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PENCOED__BRIDGEND_VALLEYS | 4.4269 | 14.6348 | 3213.9103 | 302.4892 | 2128.9587
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM | 2.2134 | 7.3204 | 3221.2307 | 302.3638 | 2131.1721
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_HEATH_&_LLANISHEN | 2.8775 | 9.5279 | 3230.7586 | 302.0037 | 2134.0496
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-HOLLAND ARMS 9INCH-DWYRAN | 1.5494 | 5.1358 | 3235.8944 | 301.689 | 2135.599
DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-NORTH_CEREDIGION | 1.5494 | 5.1362 | 3241.0305 | 301.6632 | 2137.1484
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(0,70] | 2.4348 | 8.1131 | 3249.1437 | 300.1033 | 2139.5831
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 4.6482 | 15.5193 | 3264.663 | 299.5106 | 2144.2313
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT | 3.9842 | 13.3063 | 3277.9693 | 299.4202 | 2148.2155
DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-CEMENT_MORTAR-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 1.9921 | 6.6567 | 3284.626 | 299.2586 | 2150.2076
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA | 1.9921 | 6.6628 | 3291.2888 | 298.9865 | 2152.1997
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-NORTHERN-EPOXY_RESIN-(70,120]-CLWYD_COASTAL | 1.7707 | 5.942 | 3297.2307 | 298.0067 | 2153.9704
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-EPOXY_RESIN-(70,120]-PONTSTICILL_LOW_LEVEL-RHYMNEY__BARGOED | 1.7707 | 5.9443 | 3303.175 | 297.8912 | 2155.7412
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | 1.5494 | 5.2172 | 3308.3922 | 296.9786 | 2157.2906
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN | 1.7707 | 5.9755 | 3314.3677 | 296.3343 | 2159.0613
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA | 2.6561 | 8.9721 | 3323.3398 | 296.0425 | 2161.7174
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON | 3.9842 | 13.472 | 3336.8117 | 295.7381 | 2165.7016
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-CENTRAL | 1.5494 | 5.2457 | 3342.0574 | 295.3669 | 2167.251
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-LLANELLI_FELINDRE | 1.5494 | 5.2692 | 3347.3266 | 294.049 | 2168.8004
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-MERTHYR__ABERCYNON | 2.2134 | 7.5385 | 3354.8651 | 293.6169 | 2171.0138
DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CRAY__CLYDACH | 1.7707 | 6.0554 | 3360.9204 | 292.4254 | 2172.7846
DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-NORTHERN-NONE | 1.9921 | 6.8324 | 3367.7528 | 291.565 | 2174.7767
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120] | 2.8775 | 9.8795 | 3377.6323 | 291.2552 | 2177.6541
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF | 2.4348 | 8.3612 | 3385.9935 | 291.1994 | 2180.0889
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | 2.2134 | 7.6012 | 3393.5947 | 291.1954 | 2182.3023
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-EPOXY_RESIN-(70,120] | 1.5494 | 5.3414 | 3398.9361 | 290.0717 | 2183.8517
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN | 5.0909 | 17.5735 | 3416.5097 | 289.6906 | 2188.9426
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PRESELI_SUPPLY-CROESFORDD OUTLET-BRYN DERI | 1.5494 | 5.3659 | 3421.8756 | 288.7468 | 2190.492
DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAPEL_DEWI | 1.9921 | 6.9042 | 3428.7798 | 288.5319 | 2192.4841
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120] | 2.4348 | 8.4464 | 3437.2262 | 288.2611 | 2194.9189
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA | 2.8775 | 9.9933 | 3447.2195 | 287.9384 | 2197.7963
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON | 3.7628 | 13.1095 | 3460.3291 | 287.0296 | 2201.5591
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN | 7.3043 | 25.4566 | 3485.7856 | 286.9325 | 2208.8635
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON | 2.4348 | 8.5117 | 3494.2974 | 286.0493 | 2211.2982
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | 4.2055 | 14.7209 | 3509.0183 | 285.6825 | 2215.5037
DIAM_LT_320-ALKATHENE-<=320mm-B13_1970-1961_1980 | 2.2134 | 7.7481 | 3516.7664 | 285.6744 | 2217.7172
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT | 1.5494 | 5.4353 | 3522.2016 | 285.0642 | 2219.2666
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH | 1.9921 | 7.0003 | 3529.2019 | 284.572 | 2221.2587
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | 3.5415 | 12.4928 | 3541.6947 | 283.4831 | 2224.8001
DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-BETTWS LLANGYBI AND LLANDDEWI BREFI-LANGYBI | 1.7707 | 6.2494 | 3547.9441 | 283.3476 | 2226.5709
DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120] | 4.2055 | 14.8581 | 3562.8022 | 283.0449 | 2230.7764
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CRAY__CLYDACH | 3.0988 | 10.9566 | 3573.7588 | 282.825 | 2233.8752
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-ALWEN TO BWLCH TRUNK | 1.5494 | 5.4803 | 3579.239 | 282.7223 | 2235.4246
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(0,70] | 2.4348 | 8.6199 | 3587.8589 | 282.4605 | 2237.8594
DIAM_GT_320-STEEL->610mm-B13_1970-1961_1980-WESTERN-NONE-(610,1.7e+03]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE | 0.66403 | 2.3707 | 3590.2296 | 280.0994 | 2238.5234
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-MYNYDD CROGWY TO EGLWYSWRW AND CRYMYCH | 1.9921 | 7.1176 | 3597.3472 | 279.8831 | 2240.5155
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-POLYURETHANE-(70,120]-CLWYD_COASTAL-ABERGELE__RHYL_GLASCOED | 3.0988 | 11.0803 | 3608.4275 | 279.6672 | 2243.6143
DIAM_LT_320-ALKATHENE-<=320mm-B14_1980 | 2.4348 | 8.712 | 3617.1395 | 279.4731 | 2246.049
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PENDINE | 1.5494 | 5.5558 | 3622.6952 | 278.8816 | 2247.5984
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-TWYNLLANAN | 4.2055 | 15.1152 | 3637.8104 | 278.2308 | 2251.804
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_SW__RISCA__ABERCARN | 4.8695 | 17.5194 | 3655.3299 | 277.9508 | 2256.6735
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(0,70] | 2.6561 | 9.5787 | 3664.9086 | 277.2941 | 2259.3296
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | 1.7707 | 6.4101 | 3671.3186 | 276.2442 | 2261.1004
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | 4.8695 | 17.6408 | 3688.9595 | 276.0379 | 2265.9699
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | 2.4348 | 8.8347 | 3697.7942 | 275.5921 | 2268.4047
DIAM_LT_320-STEEL-<=320mm-B07_1910-1901_1920-WESTERN-NONE-(120,160] | 1.5494 | 5.6235 | 3703.4177 | 275.5216 | 2269.9541
DIAM_LT_320-STEEL-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(160,320]-PEMBROKESHIRE-BOLTON_HILL-TTM OFF PENT PUMPS | 2.2134 | 8.0372 | 3711.4549 | 275.3978 | 2272.1675
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(0,70] | 1.7707 | 6.4393 | 3717.8942 | 274.9911 | 2273.9382
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-NORTHERN-CEMENT_MORTAR-(70,120] | 3.3201 | 12.0852 | 3729.9793 | 274.7286 | 2277.2584
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | 1.7707 | 6.4626 | 3736.4419 | 274.0003 | 2279.0291
DIAM_LT_320-FERROUS_1-<=320mm-B05_1890-1881_1900-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | 2.6561 | 9.6966 | 3746.1384 | 273.9233 | 2281.6852
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 2.2134 | 8.096 | 3754.2345 | 273.3966 | 2283.8987
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-EASTERN-POLYURETHANE | 1.9921 | 7.2869 | 3761.5214 | 273.3782 | 2285.8908
DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1981_2000-EASTERN-NONE-(120,160] | 1.9921 | 7.3019 | 3768.8233 | 272.8176 | 2287.8828
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(160,320] | 2.4348 | 8.9367 | 3777.76 | 272.447 | 2290.3176
DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | 4.4269 | 16.2487 | 3794.0087 | 272.4431 | 2294.7445
DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1961_1980-EASTERN-NONE-(70,120] | 1.9921 | 7.3203 | 3801.329 | 272.1329 | 2296.7366
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH | 1.9921 | 7.3259 | 3808.6549 | 271.9222 | 2298.7286
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-BOLTON_HILL | 5.9763 | 22.0138 | 3830.6687 | 271.4775 | 2304.7049
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | 1.5494 | 5.72 | 3836.3888 | 270.8729 | 2306.2543
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE | 5.3122 | 19.6374 | 3856.0262 | 270.5157 | 2311.5665
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKEWEN__LLANDARCY_FELINDRE__CRAY | 1.5494 | 5.7288 | 3861.755 | 270.4566 | 2313.1159
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-RHONDDA | 2.6561 | 9.8463 | 3871.6013 | 269.7572 | 2315.772
DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1981_2000-CENTRAL-NONE | 1.9921 | 7.3987 | 3879 | 269.2498 | 2317.7641
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-COED Y FRON | 1.7707 | 6.5822 | 3885.5821 | 269.0214 | 2319.5349
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-EPOXY_RESIN-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL-WEOBLEY SOUTH-REDLION PUB BREDWARDINE | 4.6482 | 17.302 | 3902.8841 | 268.6509 | 2324.1831
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-EPOXY_RESIN-(70,120] | 2.4348 | 9.0651 | 3911.9492 | 268.5886 | 2326.6178
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70] | 2.2134 | 8.2456 | 3920.1948 | 268.4374 | 2328.8313
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-POLYURETHANE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O | 1.5494 | 5.7727 | 3925.9675 | 268.401 | 2330.3807
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-RHONDDA | 2.6561 | 9.9037 | 3935.8711 | 268.1954 | 2333.0368
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-CYNON-ABERDARE_HIRWAUN__PONSTICILL | 3.3201 | 12.3965 | 3948.2676 | 267.8297 | 2336.3569
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT VALLEY GAP | 2.6561 | 9.9379 | 3958.2055 | 267.2704 | 2339.013
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-EPOXY_RESIN-(120,160] | 2.8775 | 10.8045 | 3969.01 | 266.3205 | 2341.8905
DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY-SOUTHERNDOWN | 1.5494 | 5.823 | 3974.833 | 266.0823 | 2343.4399
DIAM_LT_320-FERROUS_2-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(70,120] | 1.9921 | 7.4889 | 3982.322 | 266.004 | 2345.432
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-EPOXY_RESIN-(70,120] | 3.0988 | 11.6705 | 3993.9925 | 265.5239 | 2348.5308
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-HOLLAND ARMS 9INCH | 1.7707 | 6.6768 | 4000.6693 | 265.2077 | 2350.3015
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 1.7707 | 6.7052 | 4007.3745 | 264.0854 | 2352.0723
DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-GOSEN TYN Y FRITH-GOSEN | 1.5494 | 5.8745 | 4013.249 | 263.7509 | 2353.6217
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON | 3.9842 | 15.11 | 4028.359 | 263.6772 | 2357.6058
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-RHYMNEY__BARGOED | 2.8775 | 10.9232 | 4039.2821 | 263.4274 | 2360.4833
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-NORTHERN-CEMENT_MORTAR-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON | 2.6561 | 10.1305 | 4049.4126 | 262.191 | 2363.1394
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120] | 2.6561 | 10.1374 | 4059.55 | 262.0117 | 2365.7955
DIAM_LT_320-STEEL-<=320mm-B07_1910-1901_1920-WESTERN | 2.2134 | 8.4544 | 4068.0044 | 261.8074 | 2368.0089
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | 5.7549 | 22.0481 | 4090.0525 | 261.0161 | 2373.7639
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_EAST | 1.5494 | 5.9495 | 4096.002 | 260.4244 | 2375.3133
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-EPOXY_RESIN-(120,160]-PONTSTICILL_HIGH_LEVEL/HEADS_O | 1.5494 | 5.9638 | 4101.9658 | 259.8008 | 2376.8627
DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_HEATH_&_LLANISHEN-UPPER AND LOWER GRAIG | 1.5494 | 5.9732 | 4107.939 | 259.3928 | 2378.4121
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-BITUMEN-(70,120]-VOWCHURCH-VOWCHURCH-BRAMPTON SR-WALTERSTONE | 1.5494 | 5.9769 | 4113.9159 | 259.2307 | 2379.9615
DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-DAFEN__FELINDRE | 1.5494 | 5.9861 | 4119.9021 | 258.831 | 2381.5109
DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA | 1.5494 | 5.9911 | 4125.8932 | 258.6158 | 2383.0603
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-POLYURETHANE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY | 5.0909 | 19.6888 | 4145.582 | 258.5678 | 2388.1511
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-WESTERN-CEMENT_MORTAR-(70,120]-TYWI_C.U._AREA | 1.9921 | 7.7075 | 4153.2894 | 258.4616 | 2390.1432
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-MERTHYR__ABERCYNON | 4.2055 | 16.2995 | 4169.589 | 258.0142 | 2394.3487
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON | 2.4348 | 9.4603 | 4179.0493 | 257.3668 | 2396.7835
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_HEATH_&_LLANISHEN-WERN GOCH ROAD | 2.2134 | 8.6009 | 4187.6502 | 257.3472 | 2398.9969
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-MERTHYR__ABERCYNON-GUERNOS EAST-GURNOS EAST | 1.5494 | 6.0302 | 4193.6804 | 256.9406 | 2400.5463
DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON | 1.5494 | 6.0327 | 4199.7131 | 256.833 | 2402.0957
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-EPOXY_RESIN-(70,120] | 4.6482 | 18.1363 | 4217.8494 | 256.293 | 2406.7439
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-EPOXY_RESIN-(120,160] | 1.7707 | 6.9141 | 4224.7635 | 256.1055 | 2408.5147
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(120,160]-NORTH_ERYRI_/_YNYS_MON-EAST_ANGLESEY_CEFNI-TREFOR BLAS LLANDDONA | 1.9921 | 7.7808 | 4232.5443 | 256.0257 | 2410.5068
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120] | 1.7707 | 6.9185 | 4239.4629 | 255.942 | 2412.2775
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-EPOXY_RESIN-(160,320]-NORTH_ERYRI_/_YNYS_MON-EAST_ANGLESEY_CEFNI-LLANDYFRYDOG TO PENSARN | 1.9921 | 7.7861 | 4247.249 | 255.8503 | 2414.2696
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | 5.5336 | 21.7284 | 4268.9774 | 254.6694 | 2419.8032
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE | 3.9842 | 15.6569 | 4284.6344 | 254.467 | 2423.7873
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT | 1.5494 | 6.1442 | 4290.7786 | 252.1729 | 2425.3367
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH | 10.4031 | 41.3978 | 4332.1764 | 251.2963 | 2435.7398
DIAM_LT_320-STEEL-<=320mm-B11_1950-1941_1960-WESTERN-BITUMEN-(70,120]-TYWI_C.U._AREA-BRYNGWYN-TWYNLLANAN | 1.5494 | 6.1723 | 4338.3487 | 251.0239 | 2437.2892
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-EPOXY_RESIN-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL | 5.5336 | 22.0706 | 4360.4192 | 250.7219 | 2442.8228
DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(160,320]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | 2.4348 | 9.7443 | 4370.1635 | 249.8672 | 2445.2576
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA | 2.2134 | 8.8845 | 4379.048 | 249.1335 | 2447.471
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-EPOXY_RESIN-(70,120]-MID_-_SOUTH_CEREDIGION | 1.7707 | 7.1098 | 4386.1578 | 249.058 | 2449.2418
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PRESELI_SUPPLY-PRESELI DOLWEN | 1.5494 | 6.2263 | 4392.3841 | 248.8462 | 2450.7912
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE | 1.7707 | 7.1162 | 4399.5003 | 248.8318 | 2452.5619
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-POLYURETHANE-(160,320]-PONTSTICILL_HIGH_LEVEL/HEADS_O-EBBW_VALE__BRYNMAWR | 1.7707 | 7.118 | 4406.6184 | 248.768 | 2454.3326
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-WESTERN-POLYURETHANE | 1.9921 | 8.0111 | 4414.6295 | 248.6649 | 2456.3247
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PORT_TALBOT_FELINDRE__CRAY | 2.8775 | 11.5872 | 4426.2166 | 248.3314 | 2459.2022
DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PORT_TALBOT_FELINDRE__CRAY | 3.5415 | 14.2791 | 4440.4957 | 248.0193 | 2462.7437
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 5.3122 | 21.4405 | 4461.9362 | 247.7657 | 2468.0559
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT | 1.9921 | 8.0493 | 4469.9855 | 247.4866 | 2470.048
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL | 3.0988 | 12.5409 | 4482.5264 | 247.096 | 2473.1468
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 3.5415 | 14.3354 | 4496.8618 | 247.0445 | 2476.6883
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-RHYMNEY__BARGOED | 4.6482 | 18.8361 | 4515.6979 | 246.7704 | 2481.3365
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-POLYURETHANE-(70,120]-PEMBROKESHIRE-BOLTON_HILL | 3.0988 | 12.5667 | 4528.2646 | 246.5882 | 2484.4353
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PENCOED__BRIDGEND_VALLEYS | 3.3201 | 13.5477 | 4541.8123 | 245.0709 | 2487.7554
DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD | 1.5494 | 6.3373 | 4548.1496 | 244.4877 | 2489.3048
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | 2.4348 | 9.9685 | 4558.1181 | 244.2466 | 2491.7396
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(120,160] | 2.8775 | 11.8098 | 4569.928 | 243.6492 | 2494.617
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(0,70] | 3.0988 | 12.8034 | 4582.7314 | 242.0293 | 2497.7158
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL | 1.9921 | 8.2346 | 4590.966 | 241.9169 | 2499.7079
DIAM_LT_320-AC-<=320mm-B14_1980-1981_2000-NORTHERN-NONE | 1.9921 | 8.2412 | 4599.2071 | 241.7238 | 2501.7
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON-PEN Y BALL TO GWESPYR & AXTON TRUNK-AREA FED BY S/SUPPLY 3SF8100 | 1.7707 | 7.328 | 4606.5351 | 241.642 | 2503.4708
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL | 1.5494 | 6.4172 | 4612.9523 | 241.4457 | 2505.0202
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-EASTERN-NONE-(70,120] | 1.9921 | 8.2637 | 4621.2159 | 241.0653 | 2507.0122
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120] | 2.8775 | 11.9747 | 4633.1907 | 240.2944 | 2509.8897
DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-CEMENT_MORTAR | 1.5494 | 6.471 | 4639.6617 | 239.4368 | 2511.4391
DIAM_LT_320-ALKATHENE-<=320mm-B12_1960-1961_1980 | 1.5494 | 6.489 | 4646.1506 | 238.7748 | 2512.9885
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__RUMNEY | 3.0988 | 12.9905 | 4659.1411 | 238.5441 | 2516.0873
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-FLINT__CONNAHS_QUAY_BRETTON | 6.1976 | 25.9864 | 4685.1275 | 238.4942 | 2522.2849
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-EPOXY_RESIN-(70,120]-PONTSTICILL_LOW_LEVEL-RHYMNEY__BARGOED | 3.0988 | 13.053 | 4698.1804 | 237.4019 | 2525.3837
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-POLYURETHANE-(70,120] | 3.3201 | 13.9907 | 4712.1711 | 237.3113 | 2528.7038
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(120,160]-PONTSTICILL_HIGH_LEVEL/HEADS_O-MERTHYR__ABERCYNON | 1.9921 | 8.4187 | 4720.5898 | 236.6269 | 2530.6959
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM | 1.5494 | 6.5519 | 4727.1417 | 236.4795 | 2532.2453
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY | 6.8616 | 29.0351 | 4756.1768 | 236.3218 | 2539.1069
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-WESTERN-CEMENT_MORTAR-(120,160]-TYWI_C.U._AREA | 1.7707 | 7.4964 | 4763.6732 | 236.2117 | 2540.8777
DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-PENWCH SERVICE RES OUTLET-BETHANIA TREFENTER | 3.0988 | 13.1197 | 4776.7929 | 236.1947 | 2543.9765
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-BITUMEN-(70,120] | 1.9921 | 8.4408 | 4785.2337 | 236.0074 | 2545.9686
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-CENTRAL | 2.2134 | 9.4197 | 4794.6534 | 234.9792 | 2548.182
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(120,160]-PEMBROKESHIRE-BOLTON_HILL | 1.5494 | 6.5979 | 4801.2513 | 234.8326 | 2549.7314
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120] | 4.4269 | 18.8512 | 4820.1025 | 234.8313 | 2554.1583
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-DUNFIELD_CROSSWAYS | 1.5494 | 6.6057 | 4826.7082 | 234.5533 | 2555.7077
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | 1.5494 | 6.6147 | 4833.323 | 234.2353 | 2557.2571
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE | 2.6561 | 11.4182 | 4844.7412 | 232.6202 | 2559.9132
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-VALE_OF_GLAM__RHONDDA_VALLEYS | 1.5494 | 6.6847 | 4851.4259 | 231.7823 | 2561.4626
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | 2.2134 | 9.5513 | 4860.9772 | 231.7408 | 2563.676
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL | 1.9921 | 8.6012 | 4869.5784 | 231.6057 | 2565.6681
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(120,160]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | 1.5494 | 6.7118 | 4876.2903 | 230.8461 | 2567.2175
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-CEMENT_MORTAR-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-GWALCHMAI | 1.9921 | 8.6569 | 4884.9471 | 230.1157 | 2569.2096
DIAM_LT_320-ALKATHENE-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(0,70] | 2.4348 | 10.611 | 4895.5581 | 229.4578 | 2571.6443
DIAM_LT_320-ALKATHENE-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(0,70] | 1.9921 | 8.6837 | 4904.2418 | 229.4051 | 2573.6364
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH | 2.6561 | 11.6198 | 4915.8616 | 228.5857 | 2576.2925
DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-WESTERN-EPOXY_RESIN | 1.5494 | 6.7799 | 4922.6415 | 228.5296 | 2577.8419
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT | 3.7628 | 16.497 | 4939.1385 | 228.0918 | 2581.6048
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CRAY__CLYDACH | 1.5494 | 6.8058 | 4945.9442 | 227.6603 | 2583.1542
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE | 1.7707 | 7.7878 | 4953.732 | 227.3738 | 2584.9249
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH | 1.7707 | 7.7967 | 4961.5287 | 227.1137 | 2586.6957
DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-TALYBONT | 1.5494 | 6.8251 | 4968.3538 | 227.0147 | 2588.2451
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PORT_TALBOT_FELINDRE__CRAY | 1.9921 | 8.8126 | 4977.1664 | 226.0504 | 2590.2371
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA | 4.4269 | 19.6663 | 4996.8327 | 225.0984 | 2594.664
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON-RHOSESMOR MOEL Y CREO-BABELL TO CAERWYS(RHOS) | 1.5494 | 6.889 | 5003.7217 | 224.909 | 2596.2134
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-EPOXY_RESIN-(70,120] | 1.7707 | 7.9106 | 5011.6323 | 223.8448 | 2597.9841
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-WESTERN-NONE-(120,160]-PEMBROKESHIRE-PENDINE | 1.7707 | 7.917 | 5019.5493 | 223.664 | 2599.7549
DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1921_1940-CENTRAL-NONE | 1.5494 | 6.9357 | 5026.485 | 223.3936 | 2601.3043
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-EASTERN-EPOXY_RESIN-(70,120] | 2.6561 | 11.9118 | 5038.3968 | 222.9824 | 2603.9604
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-POLYURETHANE-(70,120] | 3.0988 | 13.9102 | 5052.307 | 222.772 | 2607.0592
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-CROSS ASH | 1.5494 | 6.9629 | 5059.2699 | 222.5226 | 2608.6086
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-WESTERN-NONE-(70,120] | 1.9921 | 8.9554 | 5068.2253 | 222.4454 | 2610.6007
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(120,160] | 3.9842 | 17.9495 | 5086.1747 | 221.9661 | 2614.5848
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(120,160]-NORTH_ERYRI_/_YNYS_MON | 1.5494 | 6.9966 | 5093.1713 | 221.4519 | 2616.1342
DIAM_LT_320-ALKATHENE-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(0,70] | 2.2134 | 10.0147 | 5103.186 | 221.0175 | 2618.3477
DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT | 1.7707 | 8.024 | 5111.21 | 220.6806 | 2620.1184
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON | 1.5494 | 7.0287 | 5118.2387 | 220.4399 | 2621.6678
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 1.7707 | 8.0391 | 5126.2778 | 220.2659 | 2623.4386
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-CEMENT_MORTAR-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW | 4.8695 | 22.2482 | 5148.526 | 218.8731 | 2628.3081
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(0,70] | 2.2134 | 10.1224 | 5158.6485 | 218.6656 | 2630.5215
DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(120,160]-PEMBROKESHIRE-PENDINE | 1.5494 | 7.0866 | 5165.7351 | 218.6375 | 2632.0709
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-WESTERN-EPOXY_RESIN-(70,120]-MID_-_SOUTH_CEREDIGION | 1.5494 | 7.0944 | 5172.8294 | 218.3983 | 2633.6203
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-EPOXY_RESIN-(120,160]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL | 1.5494 | 7.0986 | 5179.928 | 218.2686 | 2635.1697
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-POLYURETHANE-(120,160] | 2.2134 | 10.1604 | 5190.0885 | 217.8479 | 2637.3832
DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | 2.2134 | 10.171 | 5200.2595 | 217.6214 | 2639.5966
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN | 1.5494 | 7.1243 | 5207.3838 | 217.4814 | 2641.146
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-DUNFIELD_CROSSWAYS-CROSSWAYS NORTH AND HIGH | 4.4269 | 20.3696 | 5227.7534 | 217.3264 | 2645.5728
DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-CENTRAL-NONE | 2.4348 | 11.2804 | 5239.0338 | 215.8407 | 2648.0076
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 1.7707 | 8.2054 | 5247.2392 | 215.8027 | 2649.7784
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-PILLETH-PILLETH_KNIGHTON__BLEDDFA | 2.2134 | 10.258 | 5257.4972 | 215.7759 | 2651.9918
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120] | 1.5494 | 7.1822 | 5264.6793 | 215.7287 | 2653.5412
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 1.9921 | 9.2444 | 5273.9237 | 215.4912 | 2655.5333
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH | 4.2055 | 19.6493 | 5293.573 | 214.0285 | 2659.7388
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN | 2.2134 | 10.3692 | 5303.9423 | 213.461 | 2661.9522
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RHYMNEY__BARGOED | 5.9763 | 28.0022 | 5331.9445 | 213.4208 | 2667.9285
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O | 1.5494 | 7.2701 | 5339.2146 | 213.1198 | 2669.4779
DIAM_LT_320-FERROUS_1-<=320mm-B04_1880-1881_1900-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__RUMNEY | 2.2134 | 10.3938 | 5349.6084 | 212.956 | 2671.6913
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160] | 1.7707 | 8.3169 | 5357.9253 | 212.9102 | 2673.462
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-SYCHNANT-RHYDLIOS | 1.5494 | 7.2904 | 5365.2156 | 212.5265 | 2675.0114
DIAM_LT_320-ALKATHENE-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(0,70] | 1.5494 | 7.2912 | 5372.5069 | 212.5025 | 2676.5608
DIAM_LT_320-FERROUS_1-<=320mm-B05_1890-1881_1900-CENTRAL-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 1.7707 | 8.3356 | 5380.8425 | 212.4305 | 2678.3316
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PORT_TALBOT_FELINDRE__CRAY | 2.8775 | 13.5455 | 5394.388 | 212.429 | 2681.209
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-NORTHERN-NONE-(70,120] | 1.5494 | 7.3036 | 5401.6916 | 212.1417 | 2682.7584
DIAM_GT_320-STEEL->320mm and <=450mm-B11_1950-1941_1960-WESTERN-NONE-(320,450]-PEMBROKESHIRE-PRESELI_SUPPLY-PRESELI USL OUTLETS-CLARBESTON RD/SCOLTON | 1.1067 | 5.2198 | 5406.9113 | 212.0244 | 2683.8652
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(120,160] | 2.4348 | 11.4959 | 5418.4073 | 211.7945 | 2686.2999
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKEWEN__LLANDARCY_FELINDRE__CRAY | 4.2055 | 19.8573 | 5438.2645 | 211.7868 | 2690.5054
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120] | 4.2055 | 19.9056 | 5458.1701 | 211.273 | 2694.711
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-CEFN BRYN HOUSE-BURRY GREEN | 1.5494 | 7.3366 | 5465.5067 | 211.1885 | 2696.2604
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-CYNON | 2.2134 | 10.4834 | 5475.9901 | 211.1366 | 2698.4738
DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960 | 2.6561 | 12.5951 | 5488.5852 | 210.8844 | 2701.1299
DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-NORTHERN | 1.9921 | 9.4721 | 5498.0574 | 210.3098 | 2703.122
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(70,120] | 2.4348 | 11.5865 | 5509.6439 | 210.1378 | 2705.5567
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-NORTHERN-EPOXY_RESIN-(70,120]-CLWYD_COASTAL-PRESTATYN_GLASCOED__TRECASTELL | 1.5494 | 7.3783 | 5517.0222 | 209.994 | 2707.1061
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH-CAPEL SEION LLANFI AND TRAWSCOED-CAPEL SEION LLANFIHANGEL | 1.9921 | 9.4923 | 5526.5145 | 209.8643 | 2709.0982
DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-POLYURETHANE-(70,120]-TYWI_C.U._AREA | 2.4348 | 11.6155 | 5538.13 | 209.6137 | 2711.533
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-CENTRAL-NONE | 1.7707 | 8.477 | 5546.607 | 208.8887 | 2713.3037
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | 2.8775 | 13.783 | 5560.39 | 208.7678 | 2716.1812
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | 5.9763 | 28.6512 | 5589.0412 | 208.5868 | 2722.1575
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_WEST | 1.9921 | 9.5551 | 5598.5963 | 208.4837 | 2724.1495
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-EPOXY_RESIN-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 2.4348 | 11.7195 | 5610.3158 | 207.7543 | 2726.5843
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_HEATH_&_LLANISHEN | 2.2134 | 10.6719 | 5620.9877 | 207.4067 | 2728.7977
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | 3.5415 | 17.1167 | 5638.1044 | 206.9023 | 2732.3392
DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120] | 2.2134 | 10.7059 | 5648.8103 | 206.748 | 2734.5527
DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-EPOXY_RESIN-(120,160]-PEMBROKESHIRE-BOLTON_HILL-MOUNTAIN TREFFGARNE AND RUDBAXTON-MOUNTAIN WATER | 1.5494 | 7.503 | 5656.3133 | 206.5044 | 2736.1021
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-MAESTIR TO BRYNGARREG-BRYNCARREG RES OUTLET | 2.8775 | 13.9386 | 5670.2519 | 206.438 | 2738.9795
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-WESTERN | 1.5494 | 7.5095 | 5677.7614 | 206.3258 | 2740.5289
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | 3.9842 | 19.4519 | 5697.2133 | 204.8216 | 2744.5131
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-NORTHERN-CEMENT_MORTAR-(70,120] | 2.2134 | 10.8136 | 5708.0269 | 204.6893 | 2746.7265
DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA | 2.8775 | 14.0843 | 5722.1111 | 204.3031 | 2749.604
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-POLYURETHANE-(70,120] | 1.9921 | 9.7679 | 5731.8791 | 203.9417 | 2751.5961
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA-BRYNGWYN-CARMEL TO LLANNON SR | 1.5494 | 7.6275 | 5739.5065 | 203.1342 | 2753.1455
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160]-LLEYNHARLECH | 1.5494 | 7.6377 | 5747.1442 | 202.8633 | 2754.6949
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120] | 1.5494 | 7.6398 | 5754.784 | 202.8065 | 2756.2443
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-NORTHERN-EPOXY_RESIN | 1.5494 | 7.6509 | 5762.4349 | 202.5115 | 2757.7937
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-RHOSYMRYSON TO PENRHYWLLAN | 1.5494 | 7.6639 | 5770.0988 | 202.1675 | 2759.3431
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(0,70] | 1.5494 | 7.6785 | 5777.7773 | 201.785 | 2760.8925
DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-EASTERN-EPOXY_RESIN-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL | 1.5494 | 7.6797 | 5785.457 | 201.7528 | 2762.4419
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-PRESELI_SUPPLY | 1.5494 | 7.6815 | 5793.1385 | 201.706 | 2763.9913
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-RHOSYMRYSON TO PENRHYWLLAN-HOREB TO FFOSTRASOL | 1.5494 | 7.6949 | 5800.8334 | 201.3538 | 2765.5407
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-POLYURETHANE-(70,120] | 3.0988 | 15.403 | 5816.2364 | 201.1811 | 2768.6395
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 3.3201 | 16.5119 | 5832.7483 | 201.0756 | 2771.9596
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-EASTERN-NONE-(70,120]-WHITBOURNE-WHITBOURNE | 2.2134 | 11.038 | 5843.7864 | 200.5272 | 2774.173
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-PENARTH | 3.0988 | 15.5337 | 5859.3201 | 199.4891 | 2777.2718
DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(120,160]-PEMBROKESHIRE-BOLTON_HILL | 3.0988 | 15.5997 | 5874.9198 | 198.6448 | 2780.3706
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH | 4.2055 | 21.2153 | 5896.1351 | 198.2298 | 2784.5761
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-LLYSFAEN-0059 BRYN Y PIN(R00) | 1.9921 | 10.1042 | 5906.2393 | 197.1547 | 2786.5682
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD | 9.7391 | 49.4402 | 5955.6795 | 196.9872 | 2796.3073
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160]-ALWEN_/_DEE-FLINT__CONNAHS_QUAY_BRETTON | 3.7628 | 19.1169 | 5974.7963 | 196.8329 | 2800.0701
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120] | 5.7549 | 29.3279 | 6004.1243 | 196.2264 | 2805.825
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | 1.7707 | 9.0342 | 6013.1585 | 196.0034 | 2807.5958
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-WESTERN-EPOXY_RESIN | 1.7707 | 9.0552 | 6022.2137 | 195.55 | 2809.3665
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY | 5.7549 | 29.5629 | 6051.7766 | 194.6667 | 2815.1214
DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-WESTERN-NONE | 2.8775 | 14.7815 | 6066.5581 | 194.666 | 2817.9989
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-EASTERN-EPOXY_RESIN-(70,120] | 3.3201 | 17.0597 | 6083.6178 | 194.619 | 2821.319
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA | 3.0988 | 15.9237 | 6099.5415 | 194.6027 | 2824.4178
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(120,160] | 1.9921 | 10.2489 | 6109.7905 | 194.3699 | 2826.4099
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | 2.2134 | 11.3971 | 6121.1875 | 194.2104 | 2828.6234
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN | 2.4348 | 12.5944 | 6133.782 | 193.3212 | 2831.0581
DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 2.8775 | 14.9489 | 6148.7308 | 192.4867 | 2833.9356
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | 2.2134 | 11.5317 | 6160.2625 | 191.9437 | 2836.149
DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120] | 1.5494 | 8.0783 | 6168.3408 | 191.7979 | 2837.6984
DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PENCOED__BRIDGEND_VALLEYS | 4.4269 | 23.1132 | 6191.454 | 191.5294 | 2842.1253
DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-CROSS ASH-CROSS ASH | 1.7707 | 9.2551 | 6200.7091 | 191.3261 | 2843.896
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKEWEN__LLANDARCY_FELINDRE__CRAY | 1.5494 | 8.1282 | 6208.8373 | 190.6199 | 2845.4454
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-EASTERN-NONE | 2.4348 | 12.7852 | 6221.6225 | 190.4367 | 2847.8802
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(120,160]-MONMOUTH-TRELLECH__MAYHILL__FYNNON_GAER-TRELLECK-FARR HILL | 1.5494 | 8.1374 | 6229.7599 | 190.405 | 2849.4296
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(120,160] | 3.3201 | 17.4756 | 6247.2355 | 189.9874 | 2852.7497
DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-MERTHYR__ABERCYNON | 3.0988 | 16.334 | 6263.5695 | 189.7144 | 2855.8485
DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(120,160] | 3.3201 | 17.5421 | 6281.1116 | 189.2672 | 2859.1687
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-LLANELLI_FELINDRE | 3.0988 | 16.3754 | 6297.487 | 189.2347 | 2862.2675
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF | 2.4348 | 12.885 | 6310.372 | 188.9613 | 2864.7022
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE | 3.5415 | 18.7665 | 6329.1386 | 188.7128 | 2868.2437
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-NORTHERN-NONE | 2.4348 | 12.9114 | 6342.05 | 188.5755 | 2870.6785
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RHYMNEY__BARGOED | 2.2134 | 11.7622 | 6353.8122 | 188.1814 | 2872.8919
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-CEMENT_MORTAR-(120,160]-PEMBROKESHIRE | 1.9921 | 10.6716 | 6364.4838 | 186.6712 | 2874.884
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PENDINE-THREE LORDS OUTLET | 1.7707 | 9.4901 | 6373.9739 | 186.5876 | 2876.6548
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE | 1.7707 | 9.5619 | 6383.5358 | 185.1873 | 2878.4255
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-EPOXY_RESIN-(70,120]-PEMBROKESHIRE-BOLTON_HILL | 1.7707 | 9.5703 | 6393.1061 | 185.025 | 2880.1962
DIAM_LT_320-ALKATHENE-<=320mm-B12_1960-1941_1960 | 1.5494 | 8.3767 | 6401.4829 | 184.9645 | 2881.7456
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(120,160]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RHYMNEY__BARGOED | 2.8775 | 15.5846 | 6417.0675 | 184.6345 | 2884.6231
DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(160,320]-SLUVAD__COURT_FARM__LLWYNON | 1.7707 | 9.624 | 6426.6915 | 183.9915 | 2886.3938
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(160,320]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW | 1.9921 | 10.8497 | 6437.5412 | 183.6072 | 2888.3859
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-NORTHERN | 1.9921 | 10.8721 | 6448.4133 | 183.2298 | 2890.378
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CRAY__CLYDACH | 3.0988 | 16.9479 | 6465.3613 | 182.8421 | 2893.4768
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(120,160] | 2.4348 | 13.3278 | 6478.689 | 182.6838 | 2895.9116
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(120,160] | 1.5494 | 8.5262 | 6487.2153 | 181.7212 | 2897.461
DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL | 3.3201 | 18.2924 | 6505.5076 | 181.5043 | 2900.7811
DIAM_LT_320-ALKATHENE-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD | 1.5494 | 8.5448 | 6514.0524 | 181.3276 | 2902.3305
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_WEST | 1.7707 | 9.7743 | 6523.8267 | 181.164 | 2904.1013
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL-TEMPLETON TO MARTLETWY | 1.7707 | 9.8366 | 6533.6632 | 180.0159 | 2905.872
DIAM_LT_320-STEEL-<=320mm-B09_1930-1921_1940 | 1.5494 | 8.6194 | 6542.2826 | 179.7577 | 2907.4214
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(160,320] | 1.7707 | 9.867 | 6552.1497 | 179.4604 | 2909.1921
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(120,160] | 4.6482 | 25.9641 | 6578.1137 | 179.0244 | 2913.8403
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-NONE-(70,120] | 1.9921 | 11.1292 | 6589.2429 | 178.9968 | 2915.8324
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-WESTERN-NONE-(70,120] | 1.5494 | 8.6606 | 6597.9035 | 178.9011 | 2917.3818
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-PEMBROKESHIRE-BOLTON_HILL | 3.5415 | 19.8948 | 6617.7983 | 178.0107 | 2920.9233
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON | 2.8775 | 16.2236 | 6634.0219 | 177.3623 | 2923.8008
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD | 3.3201 | 18.7472 | 6652.7691 | 177.1009 | 2927.1209
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL | 1.9921 | 11.2538 | 6664.0229 | 177.0146 | 2929.113
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE | 1.5494 | 8.7561 | 6672.779 | 176.951 | 2930.6624
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | 2.6561 | 15.0681 | 6687.8471 | 176.2739 | 2933.3185
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(120,160] | 7.083 | 40.1943 | 6728.0414 | 176.2183 | 2940.4015
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 1.7707 | 10.1225 | 6738.1639 | 174.9319 | 2942.1722
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-NORTHERN-CEMENT_MORTAR-(70,120] | 1.5494 | 8.8591 | 6747.023 | 174.8929 | 2943.7216
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-NORTHERN-CEMENT_MORTAR-(70,120] | 1.5494 | 8.8655 | 6755.8885 | 174.7677 | 2945.271
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(0,70] | 1.5494 | 8.8769 | 6764.7654 | 174.5434 | 2946.8204
DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1921_1940 | 1.5494 | 8.8888 | 6773.6542 | 174.3091 | 2948.3698
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-PILLETH-PILLETH_KNIGHTON__BLEDDFA-WHITTON BEGGARS BUSH | 2.4348 | 13.9832 | 6787.6374 | 174.1207 | 2950.8046
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-CEMENT_MORTAR-(70,120] | 3.5415 | 20.3503 | 6807.9878 | 174.0259 | 2954.3461
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW | 1.7707 | 10.2107 | 6818.1985 | 173.4199 | 2956.1168
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-MID_-_SOUTH_CEREDIGION-LLECHRYD | 1.7707 | 10.2277 | 6828.4262 | 173.1314 | 2957.8876
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-WESTERN-EPOXY_RESIN-(120,160] | 1.9921 | 11.5507 | 6839.977 | 172.4639 | 2959.8797
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-EPOXY_RESIN-(70,120]-CLWYD_COASTAL | 1.7707 | 10.2682 | 6850.2451 | 172.4494 | 2961.6504
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAPEL_DEWI-FOEL TO MAENIEUAN | 1.5494 | 9.0296 | 6859.2748 | 171.5908 | 2963.1998
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | 1.9921 | 11.6135 | 6870.8883 | 171.5319 | 2965.1919
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(120,160]-ALWEN_/_DEE | 2.2134 | 12.9304 | 6883.8187 | 171.1796 | 2967.4053
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-NONE-(160,320]-TYWI_C.U._AREA | 1.7707 | 10.3559 | 6894.1746 | 170.9893 | 2969.1761
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH | 1.7707 | 10.42 | 6904.5946 | 169.9366 | 2970.9468
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON | 2.8775 | 16.9348 | 6921.5294 | 169.9137 | 2973.8243
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-VALE_OF_GLAM__RHONDDA_VALLEYS | 4.4269 | 26.1105 | 6947.6399 | 169.5431 | 2978.2511
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(160,320] | 1.5494 | 9.1414 | 6956.7813 | 169.492 | 2979.8005
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-WESTERN-EPOXY_RESIN | 1.7707 | 10.4474 | 6967.2288 | 169.491 | 2981.5713
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-CENTRAL-NONE | 1.5494 | 9.1564 | 6976.3851 | 169.2155 | 2983.1207
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(120,160]-ALWEN_/_DEE-DENBIGH_ALWEN | 2.4348 | 14.396 | 6990.7811 | 169.1284 | 2985.5554
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | 1.7707 | 10.4759 | 7001.257 | 169.0309 | 2987.3262
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE | 1.7707 | 10.4762 | 7011.7332 | 169.0255 | 2989.0969
DIAM_LT_320-FERROUS_1-<=320mm-B05_1890-1881_1900-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 1.7707 | 10.4827 | 7022.2158 | 168.9206 | 2990.8676
DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PENDINE | 1.7707 | 10.5321 | 7032.748 | 168.1275 | 2992.6384
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-POLYURETHANE-(160,320] | 1.9921 | 11.891 | 7044.639 | 167.529 | 2994.6305
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1941_1960 | 2.6561 | 15.8616 | 7060.5005 | 167.4561 | 2997.2866
DIAM_LT_320-FERROUS_1-<=320mm-B05_1890-1881_1900-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 1.7707 | 10.597 | 7071.0975 | 167.0987 | 2999.0573
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-SOUTH_MEIRIONNYDD | 1.9921 | 11.9533 | 7083.0508 | 166.6556 | 3001.0494
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-CYNON | 1.5494 | 9.3209 | 7092.3717 | 166.2292 | 3002.5988
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-CLWYD_COASTAL-ABERGELE__RHYL_GLASCOED-ST ASAPH 10 GAP | 2.8775 | 17.3176 | 7109.6893 | 166.1578 | 3005.4763
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON | 15.494 | 93.3489 | 7203.0382 | 165.9795 | 3020.9703
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PENCOED__BRIDGEND_VALLEYS | 2.4348 | 14.7469 | 7217.7851 | 165.104 | 3023.405
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(120,160]-PONTSTICILL_LOW_LEVEL | 2.8775 | 17.4317 | 7235.2168 | 165.0699 | 3026.2825
DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120] | 2.2134 | 13.4444 | 7248.6612 | 164.6359 | 3028.4959
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | 4.2055 | 25.5916 | 7274.2528 | 164.3317 | 3032.7014
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE | 1.7707 | 10.7973 | 7285.0502 | 163.9981 | 3034.4722
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-WESTERN-NONE-(120,160]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH | 1.7707 | 10.8108 | 7295.861 | 163.7938 | 3036.2429
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-NORTHERN-CEMENT_MORTAR | 2.2134 | 13.5213 | 7309.3822 | 163.6997 | 3038.4564
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON | 2.2134 | 13.5904 | 7322.9727 | 162.8665 | 3040.6698
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON | 7.747 | 47.8008 | 7370.7735 | 162.0684 | 3048.4168
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | 3.0988 | 19.1257 | 7389.8992 | 162.0225 | 3051.5156
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(0,70]-TYWI_C.U._AREA | 1.5494 | 9.5909 | 7399.4901 | 161.5486 | 3053.065
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA | 3.3201 | 20.563 | 7420.0532 | 161.4617 | 3056.3851
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(120,160] | 1.9921 | 12.3438 | 7432.397 | 161.3829 | 3058.3772
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON | 2.6561 | 16.5905 | 7448.9875 | 160.0989 | 3061.0333
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-WESTERN-EPOXY_RESIN-(120,160] | 1.7707 | 11.0755 | 7460.063 | 159.8793 | 3062.8041
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-EPOXY_RESIN-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL-WEOBLEY SOUTH-NORTON PRV | 1.7707 | 11.0923 | 7471.1553 | 159.6373 | 3064.5748
DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-EPOXY_RESIN-(70,120] | 2.2134 | 13.9187 | 7485.074 | 159.0252 | 3066.7882
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120] | 2.4348 | 15.4108 | 7500.4847 | 157.9917 | 3069.223
DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA | 3.3201 | 21.0209 | 7521.5056 | 157.9451 | 3072.5432
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(120,160]-PONTSTICILL_LOW_LEVEL | 3.0988 | 19.6385 | 7541.1441 | 157.7917 | 3075.642
DIAM_LT_320-FERROUS_1-<=320mm-B04_1880-PRE_1880-WESTERN-NONE | 1.5494 | 9.8239 | 7550.9681 | 157.717 | 3077.1914
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | 1.9921 | 12.6457 | 7563.6138 | 157.5308 | 3079.1834
DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(120,160] | 2.4348 | 15.4688 | 7579.0826 | 157.3986 | 3081.6182
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM | 1.7707 | 11.3218 | 7590.4044 | 156.4009 | 3083.3889
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_WEST | 2.2134 | 14.1971 | 7604.6015 | 155.9075 | 3085.6024
DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | 2.2134 | 14.1993 | 7618.8008 | 155.8824 | 3087.8158
DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-POLYURETHANE | 1.9921 | 12.7871 | 7631.5879 | 155.789 | 3089.8079
DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(120,160] | 1.9921 | 12.8048 | 7644.3927 | 155.5729 | 3091.8
DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-CENTRAL | 2.8775 | 18.5816 | 7662.9743 | 154.8551 | 3094.6774
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-CLWYD_COASTAL-PRESTATYN_GLASCOED__TRECASTELL | 1.7707 | 11.4741 | 7674.4484 | 154.3258 | 3096.4482
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL | 1.7707 | 11.4931 | 7685.9415 | 154.0699 | 3098.2189
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(160,320]-TYWI_C.U._AREA | 3.7628 | 24.7813 | 7710.7228 | 151.8413 | 3101.9817
DIAM_GT_320-STEEL->320mm and <=450mm-B07_1910-1901_1920-WESTERN-NONE-(320,450]-TYWI_C.U._AREA-BRYNGWYN-TWYNLLANAN-CEFN BEDW GOWER INPUT | 1.3281 | 8.7748 | 7719.4976 | 151.3498 | 3103.3098
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-LLANELLI_FELINDRE | 1.7707 | 11.7282 | 7731.2258 | 150.9819 | 3105.0805
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAPEL_DEWI | 2.6561 | 17.595 | 7748.8207 | 150.9586 | 3107.7367
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-BETTWS LLANGYBI AND LLANDDEWI BREFI-BETTWS BLEDRWS | 1.5494 | 10.2832 | 7759.1039 | 150.6736 | 3109.2861
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-CEMENT_MORTAR-(70,120]-TYWI_C.U._AREA | 1.7707 | 11.8543 | 7770.9582 | 149.375 | 3111.0568
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-EPOXY_RESIN-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 1.9921 | 13.3802 | 7784.3384 | 148.883 | 3113.0489
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O | 2.4348 | 16.4186 | 7800.7571 | 148.2933 | 3115.4837
DIAM_LT_320-STEEL-<=320mm-B11_1950-1941_1960-WESTERN-NONE | 1.7707 | 11.9505 | 7812.7075 | 148.1737 | 3117.2544
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-BOLTON_HILL | 2.8775 | 19.435 | 7832.1425 | 148.0556 | 3120.1319
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-WHITBOURNE-WHITBOURNE-WARRENWOOD-STOKE LACY | 1.7707 | 11.9691 | 7844.1116 | 147.943 | 3121.9026
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120] | 1.7707 | 11.9868 | 7856.0983 | 147.7249 | 3123.6733
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(70,120] | 1.9921 | 13.5533 | 7869.6516 | 146.9819 | 3125.6654
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | 3.0988 | 21.1324 | 7890.7839 | 146.6377 | 3128.7642
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-CEMENT_MORTAR | 1.9921 | 13.5937 | 7904.3777 | 146.5446 | 3130.7563
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 1.7707 | 12.0951 | 7916.4727 | 146.402 | 3132.5271
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-POLYURETHANE-(120,160] | 1.5494 | 10.605 | 7927.0777 | 146.1012 | 3134.0765
DIAM_GT_320-AC->450mm and <=610mm-B12_1960-1961_1980-NORTHERN-NONE-(450,610]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-YNYS MON SOSI TM-AREA FED BY S/SUPPLY 3B100F02 | 0.66403 | 4.5664 | 7931.6441 | 145.415 | 3134.7405
DIAM_LT_320-FERROUS_1-<=320mm-B04_1880-1881_1900-CENTRAL-NONE | 1.9921 | 13.7605 | 7945.4047 | 144.7679 | 3136.7326
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(120,160] | 1.5494 | 10.7075 | 7956.1122 | 144.7028 | 3138.282
DIAM_GT_320-FERROUS_1->450mm and <=610mm-B09_1930-1921_1940-CENTRAL-NONE-(450,610]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF | 0.66403 | 4.594 | 7960.7061 | 144.5439 | 3138.946
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_HEATH_&_LLANISHEN | 1.5494 | 10.7329 | 7971.439 | 144.3601 | 3140.4954
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(0,70] | 2.2134 | 15.3668 | 7986.8058 | 144.0397 | 3142.7088
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(120,160]-PEMBROKESHIRE-BOLTON_HILL | 3.0988 | 21.5387 | 8008.3445 | 143.871 | 3145.8076
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(70,120] | 2.2134 | 15.389 | 8023.7335 | 143.8321 | 3148.0211
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-WESTERN-CEMENT_MORTAR-(70,120]-TYWI_C.U._AREA | 2.2134 | 15.4169 | 8039.1504 | 143.5711 | 3150.2345
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120] | 1.9921 | 13.9286 | 8053.0791 | 143.021 | 3152.2266
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE | 2.4348 | 17.0554 | 8070.1345 | 142.7566 | 3154.6613
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960 | 1.5494 | 10.8718 | 8081.0062 | 142.5161 | 3156.2107
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 2.8775 | 20.2435 | 8101.2497 | 142.1426 | 3159.0882
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-VOWCHURCH-VOWCHURCH-BRAMPTON SR | 3.5415 | 24.9547 | 8126.2044 | 141.9165 | 3162.6297
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF | 3.0988 | 21.9722 | 8148.1766 | 141.0329 | 3165.7285
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-EPOXY_RESIN-(120,160] | 1.7707 | 12.6407 | 8160.8173 | 140.0826 | 3167.4992
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(120,160] | 1.7707 | 12.6438 | 8173.4611 | 140.0478 | 3169.27
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE | 5.5336 | 39.7727 | 8213.2338 | 139.1298 | 3174.8035
DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1961_1980-EASTERN-NONE | 1.5494 | 11.2086 | 8224.4424 | 138.2337 | 3176.3529
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL | 8.411 | 60.8503 | 8285.2927 | 138.2248 | 3184.764
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-WHITBOURNE-WHITBOURNE | 1.9921 | 14.4172 | 8299.71 | 138.1739 | 3186.756
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM | 1.5494 | 11.2162 | 8310.9262 | 138.1393 | 3188.3054
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(120,160]-HEREFORD_C.U._AREA-DUNFIELD_CROSSWAYS-CROSSWAYS SOUTH | 1.9921 | 14.4313 | 8325.3575 | 138.0392 | 3190.2975
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | 2.2134 | 16.0524 | 8341.4099 | 137.888 | 3192.511
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-POLYURETHANE-(70,120]-PONTSTICILL_LOW_LEVEL | 1.7707 | 12.8732 | 8354.283 | 137.553 | 3194.2817
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-WESTERN-EPOXY_RESIN | 1.5494 | 11.3094 | 8365.5924 | 137.001 | 3195.8311
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL | 3.5415 | 26.063 | 8391.6554 | 135.8817 | 3199.3726
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1941_1960-WESTERN-NONE | 2.2134 | 16.3005 | 8407.9559 | 135.7889 | 3201.586
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PENDINE-CROSSHANDS RES OUTLETS-X HANDS RES | 3.5415 | 26.252 | 8434.208 | 134.9034 | 3205.1275
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__SOUTH_BROOMY_HILL_ | 1.5494 | 11.5111 | 8445.719 | 134.6009 | 3206.6769
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL | 1.7707 | 13.2373 | 8458.9563 | 133.7696 | 3208.4476
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | 4.6482 | 35.1753 | 8494.1316 | 132.1439 | 3213.0958
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(160,320]-HEREFORD_C.U._AREA | 1.7707 | 13.4106 | 8507.5422 | 132.0401 | 3214.8666
DIAM_LT_320-FERROUS_1-<=320mm-B03_1870-PRE_1880-WESTERN-NONE | 1.9921 | 15.0976 | 8522.6398 | 131.9473 | 3216.8587
DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(120,160] | 1.5494 | 11.7806 | 8534.4204 | 131.5209 | 3218.4081
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH | 2.2134 | 16.8454 | 8551.2658 | 131.3968 | 3220.6215
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | 3.7628 | 28.8422 | 8580.108 | 130.4625 | 3224.3843
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT | 1.5494 | 11.9058 | 8592.0139 | 130.1379 | 3225.9337
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | 2.8775 | 22.1184 | 8614.1323 | 130.0931 | 3228.8112
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-DUNFIELD_CROSSWAYS-CROSSWAYS SOUTH | 4.6482 | 35.888 | 8650.0204 | 129.5194 | 3233.4594
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-CLWYD_COASTAL-PRESTATYN_GLASCOED__TRECASTELL | 1.7707 | 13.7104 | 8663.7307 | 129.1537 | 3235.2301
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | 5.0909 | 39.4897 | 8703.2204 | 128.9168 | 3240.321
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAPEL_DEWI-MAENIEUAN OUTLETS-MADOX TO TRELECH | 1.5494 | 12.0307 | 8715.2511 | 128.7871 | 3241.8704
DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | 2.8775 | 22.3889 | 8737.64 | 128.5219 | 3244.7479
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-EASTERN | 4.4269 | 34.5136 | 8772.1536 | 128.264 | 3249.1747
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-WESTERN-CEMENT_MORTAR | 2.2134 | 17.3298 | 8789.4833 | 127.7241 | 3251.3882
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | 1.9921 | 15.725 | 8805.2083 | 126.683 | 3253.3802
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-NORTHERN | 1.9921 | 15.7391 | 8820.9475 | 126.5689 | 3255.3723
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(160,320]-MID_-_SOUTH_CEREDIGION | 1.5494 | 12.3368 | 8833.2842 | 125.5922 | 3256.9217
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-WESTERN-NONE | 1.9921 | 15.9112 | 8849.1955 | 125.1998 | 3258.9138
DIAM_LT_320-FERROUS_2-<=320mm-B16_2000-2001_2020-WESTERN-EPOXY_RESIN-(120,160] | 1.9921 | 15.9136 | 8865.1091 | 125.1809 | 3260.9059
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(160,320]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON | 1.9921 | 15.9202 | 8881.0294 | 125.129 | 3262.898
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-LLYSWEN-LLYSWEN-LLYSWEN TO LLANSTEPHAN | 2.2134 | 17.7308 | 8898.7602 | 124.835 | 3265.1114
DIAM_LT_320 | 2.6561 | 21.3205 | 8920.0807 | 124.5804 | 3267.7675
DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-LLANELLI_FELINDRE | 1.7707 | 14.3069 | 8934.3876 | 123.7684 | 3269.5383
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-POLYURETHANE | 1.5494 | 12.5632 | 8946.9508 | 123.3284 | 3271.0877
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-CENTRAL | 1.5494 | 12.5895 | 8959.5402 | 123.0713 | 3272.6371
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_EAST | 1.7707 | 14.3902 | 8973.9304 | 123.0522 | 3274.4078
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL | 2.2134 | 17.9941 | 8991.9245 | 123.0086 | 3276.6212
DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120] | 5.0909 | 41.4749 | 9033.3994 | 122.7462 | 3281.7121
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-WESTERN-NONE | 1.9921 | 16.2434 | 9049.6428 | 122.6398 | 3283.7042
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(120,160]-TALYBONT-ABERGAVENNY__CWMTILLERY | 1.7707 | 14.4877 | 9064.1304 | 122.2243 | 3285.4749
DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-PENARTH__BARRY | 1.5494 | 12.6912 | 9076.8216 | 122.0845 | 3287.0243
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-POLYURETHANE | 1.5494 | 12.6937 | 9089.5153 | 122.0607 | 3288.5737
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(160,320]-PONTSTICILL_LOW_LEVEL | 1.7707 | 14.5164 | 9104.0317 | 121.9822 | 3290.3445
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF | 1.7707 | 14.5274 | 9118.5592 | 121.8897 | 3292.1152
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-DAFEN__FELINDRE | 1.7707 | 14.6098 | 9133.169 | 121.202 | 3293.886
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | 1.9921 | 16.4508 | 9149.6198 | 121.0932 | 3295.8781
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-POLYURETHANE-(70,120]-TYWI_C.U._AREA | 2.4348 | 20.1094 | 9169.7292 | 121.0764 | 3298.3128
DIAM_LT_320-FERROUS_2-<=320mm-B16_2000-2001_2020-WESTERN-EPOXY_RESIN-(70,120] | 1.7707 | 14.6353 | 9184.3645 | 120.991 | 3300.0836
DIAM_LT_320-COPPER-<=320mm | 1.5494 | 12.851 | 9197.2155 | 120.5665 | 3301.633
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160] | 3.5415 | 29.4033 | 9226.6188 | 120.4453 | 3305.1745
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD | 4.8695 | 40.5141 | 9267.1329 | 120.1938 | 3310.044
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(120,160]-NORTH_ERYRI_/_YNYS_MON-EAST_ANGLESEY_CEFNI | 1.9921 | 16.5842 | 9283.7171 | 120.1196 | 3312.0361
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-EASTERN-NONE | 1.9921 | 16.6467 | 9300.3638 | 119.6686 | 3314.0282
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-ELAN_/_BUILTH-ELAN | 1.5494 | 13.0607 | 9313.4244 | 118.6311 | 3315.5776
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | 1.5494 | 13.0866 | 9326.5111 | 118.3955 | 3317.127
DIAM_LT_320-FERROUS_1-<=320mm-B04_1880 | 1.5494 | 13.0934 | 9339.6044 | 118.3347 | 3318.6764
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-WESTERN | 2.2134 | 18.7127 | 9358.3171 | 118.2849 | 3320.8898
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 3.5415 | 30.0272 | 9388.3443 | 117.9428 | 3324.4313
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-CEFN BRYN OUTLETS TO S W GOWER | 1.7707 | 15.1447 | 9403.489 | 116.9214 | 3326.202
DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120] | 1.5494 | 13.2676 | 9416.7566 | 116.7806 | 3327.7514
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN | 1.7707 | 15.2255 | 9431.9821 | 116.3012 | 3329.5222
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-NORTHERN-CEMENT_MORTAR-(70,120] | 4.4269 | 38.2678 | 9470.2499 | 115.681 | 3333.949
DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120] | 3.7628 | 32.8094 | 9503.0593 | 114.6875 | 3337.7119
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(70,120] | 2.2134 | 19.3447 | 9522.404 | 114.4203 | 3339.9253
DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120] | 1.5494 | 13.5675 | 9535.9715 | 114.1997 | 3341.4747
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | 1.9921 | 17.4503 | 9553.4218 | 114.1575 | 3343.4668
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN | 4.8695 | 42.7242 | 9596.146 | 113.9761 | 3348.3363
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-NORTHERN-NONE | 1.9921 | 17.5338 | 9613.6798 | 113.6141 | 3350.3284
DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-EASTERN-CEMENT_MORTAR-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 3.0988 | 27.2936 | 9640.9734 | 113.5357 | 3353.4272
DIAM_LT_320-ALKATHENE-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA | 2.4348 | 21.4541 | 9662.4275 | 113.4874 | 3355.862
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL | 3.9842 | 35.1541 | 9697.5816 | 113.3345 | 3359.8461
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION | 1.7707 | 15.6574 | 9713.239 | 113.0931 | 3361.6169
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN | 1.7707 | 15.6579 | 9728.8969 | 113.0897 | 3363.3876
DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-WESTERN-CEMENT_MORTAR-(120,160]-TYWI_C.U._AREA | 3.3201 | 29.4948 | 9758.3917 | 112.5669 | 3366.7078
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120] | 3.3201 | 29.6322 | 9788.0239 | 112.0452 | 3370.0279
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | 2.2134 | 19.7873 | 9807.8112 | 111.861 | 3372.2413
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-NORTHERN-CEMENT_MORTAR | 1.9921 | 17.8376 | 9825.6489 | 111.6788 | 3374.2334
DIAM_GT_320-AC->610mm-B13_1970-1961_1980-NORTHERN-NONE-(610,1.7e+03]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON-BUCKLEY LIVERPOOL ROAD-EWLOE/HAWARDEN. | 0.66403 | 5.9835 | 9831.6324 | 110.976 | 3374.8974
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900 | 1.7707 | 16.0002 | 9847.6326 | 110.67 | 3376.6682
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(120,160] | 1.7707 | 16.0013 | 9863.6339 | 110.6623 | 3378.4389
DIAM_LT_320-PLASTIC_PE-<=320mm-B17_2010-2001_2020-NORTHERN-NONE-(0,70]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | 1.5649 | 14.1527 | 9877.7867 | 110.5703 | 3380.0038
DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-CENTRAL-CEMENT_MORTAR-(70,120] | 1.5494 | 14.034 | 9891.8207 | 110.4033 | 3381.5532
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120] | 2.8775 | 26.1909 | 9918.0116 | 109.8646 | 3384.4307
DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | 3.0988 | 28.2314 | 9946.243 | 109.7641 | 3387.5295
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(70,120] | 1.5494 | 14.1309 | 9960.3739 | 109.6463 | 3389.0789
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-CENTRAL-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 1.5494 | 14.1355 | 9974.5094 | 109.6106 | 3390.6283
DIAM_LT_320-PLASTIC_PE-<=320mm-B18_2020-2021_ONWARDS-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | 2.0387 | 18.6445 | 9993.1539 | 109.3481 | 3392.667
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN | 1.7707 | 16.2038 | 10009.3577 | 109.2794 | 3394.4377
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120] | 5.9763 | 54.8185 | 10064.1762 | 109.0189 | 3400.414
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-EASTERN-NONE | 1.7707 | 16.3283 | 10080.5046 | 108.4461 | 3402.1847
DIAM_LT_320-AC-<=320mm-B14_1980 | 1.5494 | 14.3958 | 10094.9004 | 107.6283 | 3403.7341
DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA | 1.5494 | 14.4671 | 10109.3675 | 107.0984 | 3405.2835
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920 | 1.5494 | 14.4806 | 10123.848 | 106.9985 | 3406.8329
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON | 2.4348 | 22.8349 | 10146.6829 | 106.6251 | 3409.2677
DIAM_LT_320-ALKATHENE-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE | 2.4348 | 22.8675 | 10169.5505 | 106.4728 | 3411.7025
DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-CENTRAL-NONE-(70,120]-CYNON-ABERDARE_HIRWAUN__PONSTICILL | 1.5494 | 14.5531 | 10184.1036 | 106.4653 | 3413.2519
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | 2.4348 | 22.8833 | 10206.9869 | 106.3995 | 3415.6867
DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120] | 1.9921 | 18.8064 | 10225.7933 | 105.9259 | 3417.6787
DIAM_LT_320-PLASTIC_PE-<=320mm-B17_2010-2001_2020-NORTHERN-NONE-(0,70]-ALWEN_/_DEE | 1.7729 | 16.8724 | 10242.6657 | 105.0787 | 3419.4517
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(120,160] | 2.2134 | 21.1255 | 10263.7912 | 104.7753 | 3421.6651
DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE | 1.5494 | 14.803 | 10278.5942 | 104.6678 | 3423.2145
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-NONE | 3.5415 | 34.0653 | 10312.6595 | 103.9617 | 3426.756
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-CENTRAL-NONE | 1.9921 | 19.1624 | 10331.8219 | 103.958 | 3428.7481
DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-EASTERN-CEMENT_MORTAR-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN | 2.2134 | 21.4018 | 10353.2237 | 103.4226 | 3430.9615
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-NORTHERN | 2.4348 | 23.5656 | 10376.7893 | 103.3187 | 3433.3963
DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-WESTERN | 2.8775 | 27.9845 | 10404.7738 | 102.8232 | 3436.2737
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE | 1.9921 | 19.3949 | 10424.1688 | 102.7117 | 3438.2658
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-CROSSROADS TO CRUGIAU AND TREGAMMON | 2.4348 | 23.8648 | 10448.0335 | 102.0236 | 3440.7006
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-CENTRAL | 1.5494 | 15.2383 | 10463.2718 | 101.6782 | 3442.25
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAERAU__YSTRADFELLTE | 1.5494 | 15.3355 | 10478.6073 | 101.0335 | 3443.7994
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-WHITBOURNE-WHITBOURNE | 2.2134 | 21.9832 | 10500.5905 | 100.6875 | 3446.0128
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-POLYURETHANE | 2.2134 | 22.0264 | 10522.6169 | 100.4899 | 3448.2262
DIAM_LT_320-FERROUS_1-<=320mm-B03_1870-PRE_1880 | 1.7707 | 17.6455 | 10540.2623 | 100.3512 | 3449.997
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | 3.0988 | 30.9835 | 10571.2458 | 100.0146 | 3453.0958
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH | 2.6561 | 26.7185 | 10597.9643 | 99.411 | 3455.7519
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-POLYURETHANE | 3.5415 | 35.6343 | 10633.5986 | 99.384 | 3459.2934
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(0,70] | 1.9921 | 20.0599 | 10653.6586 | 99.3066 | 3461.2855
DIAM_LT_320-STEEL-<=320mm | 3.9842 | 40.1967 | 10693.8553 | 99.1169 | 3465.2696
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-NORTHERN | 3.3201 | 33.5636 | 10727.4189 | 98.921 | 3468.5898
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | 1.9921 | 20.164 | 10747.5828 | 98.7942 | 3470.5819
DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-PEMBROKESHIRE | 1.5494 | 15.7861 | 10763.3689 | 98.1497 | 3472.1313
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-EASTERN | 1.7707 | 18.0678 | 10781.4367 | 98.0055 | 3473.902
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-EASTERN-NONE | 2.2134 | 22.6193 | 10804.056 | 97.8557 | 3476.1154
DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(70,120] | 3.3201 | 34.3908 | 10838.4469 | 96.5415 | 3479.4356
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW | 2.4348 | 25.2714 | 10863.7182 | 96.345 | 3481.8704
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-BLAENAU_FFESTINIOG-BLAENAU_GARREGLWYD | 1.5494 | 16.1228 | 10879.841 | 96.0999 | 3483.4198
DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1961_1980-NORTHERN-NONE | 2.4348 | 25.6375 | 10905.4786 | 94.969 | 3485.8545
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN | 2.4348 | 25.6412 | 10931.1198 | 94.9554 | 3488.2893
DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(160,320] | 1.5494 | 16.385 | 10947.5048 | 94.5619 | 3489.8387
DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | 6.6403 | 70.404 | 11017.9088 | 94.3169 | 3496.479
DIAM_LT_320-STEEL-<=320mm-B11_1950-1941_1960 | 1.7707 | 18.8485 | 11036.7573 | 93.9459 | 3498.2497
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | 1.5494 | 16.4983 | 11053.2556 | 93.9129 | 3499.7991
DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-WESTERN-CEMENT_MORTAR-(70,120]-TYWI_C.U._AREA | 2.4348 | 26.332 | 11079.5876 | 92.4644 | 3502.2339
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-EASTERN-NONE | 1.5494 | 16.8962 | 11096.4838 | 91.7009 | 3503.7833
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-CENTRAL-NONE | 1.9921 | 21.7692 | 11118.253 | 91.5094 | 3505.7754
DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(120,160]-TALYBONT | 1.5494 | 16.9566 | 11135.2096 | 91.3744 | 3507.3248
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960 | 2.2134 | 24.2962 | 11159.5059 | 91.1017 | 3509.5382
DIAM_GT_320-FERROUS_1->320mm and <=450mm-B08_1920-1901_1920-NORTHERN-NONE-(320,450]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT VALLEY TRUNK-AREA FED BY S/SUPPLY 3SC20M18 | 0.88537 | 9.7304 | 11169.2363 | 90.9901 | 3510.4236
DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA-BRYNGWYN | 1.7707 | 19.6227 | 11188.859 | 90.2395 | 3512.1943
DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1961_1980-EASTERN-CEMENT_MORTAR | 1.5494 | 17.4504 | 11206.3093 | 88.789 | 3513.7437
DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-WESTERN-CEMENT_MORTAR-(160,320]-TYWI_C.U._AREA | 4.8695 | 55.0406 | 11261.3499 | 88.4719 | 3518.6133
DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-NORTHERN-NONE | 1.7707 | 20.0475 | 11281.3974 | 88.3272 | 3520.384
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(120,160] | 1.7707 | 20.0769 | 11301.4744 | 88.1979 | 3522.1547
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN | 3.7628 | 42.6733 | 11344.1477 | 88.1776 | 3525.9176
DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | 2.2134 | 25.1317 | 11369.2794 | 88.073 | 3528.131
DIAM_LT_320-PLASTIC_PE-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(0,70] | 1.5494 | 17.6289 | 11386.9083 | 87.8898 | 3529.6804
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-WESTERN | 2.6561 | 30.5232 | 11417.4315 | 87.0195 | 3532.3365
DIAM_LT_320-STEEL-<=320mm-B09_1930-1921_1940-WESTERN-BITUMEN | 1.5494 | 17.8157 | 11435.2472 | 86.9683 | 3533.8859
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(120,160] | 1.5494 | 17.8249 | 11453.0721 | 86.9235 | 3535.4353
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960 | 2.8775 | 33.1212 | 11486.1932 | 86.8766 | 3538.3128
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-NORTHERN-NONE | 2.2134 | 25.4922 | 11511.6855 | 86.8275 | 3540.5262
DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 2.6561 | 30.8484 | 11542.5339 | 86.1022 | 3543.1823
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(120,160] | 1.7707 | 20.594 | 11563.1279 | 85.9834 | 3544.9531
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120] | 2.8775 | 33.5952 | 11596.7231 | 85.6508 | 3547.8305
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE | 1.7707 | 20.9275 | 11617.6506 | 84.6133 | 3549.6013
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-EPOXY_RESIN-(160,320] | 1.9921 | 23.5932 | 11641.2438 | 84.4347 | 3551.5933
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-NONE | 2.2134 | 26.229 | 11667.4728 | 84.3886 | 3553.8068
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-CLWYD_COASTAL-ABERGELE__RHYL_GLASCOED | 1.9921 | 23.6503 | 11691.1231 | 84.2309 | 3555.7989
DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | 4.2055 | 50.1718 | 11741.2949 | 83.8222 | 3560.0044
DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960 | 1.7707 | 21.1322 | 11762.4271 | 83.7935 | 3561.7751
DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1981_2000-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON | 1.7707 | 21.2098 | 11783.6369 | 83.4869 | 3563.5459
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120] | 3.3201 | 39.8578 | 11823.4948 | 83.2996 | 3566.866
DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-EASTERN-CEMENT_MORTAR-(120,160] | 3.3201 | 40.1473 | 11863.6421 | 82.699 | 3570.1861
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120] | 2.4348 | 29.5693 | 11893.2114 | 82.3411 | 3572.6209
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | 3.0988 | 37.6847 | 11930.8961 | 82.2296 | 3575.7197
DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CRAY__CLYDACH | 3.3201 | 40.5199 | 11971.416 | 81.9386 | 3579.0399
DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE | 3.7628 | 45.9958 | 12017.4118 | 81.8082 | 3582.8027
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL | 2.6561 | 32.4763 | 12049.888 | 81.7863 | 3585.4588
DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1981_2000-NORTHERN-NONE-(70,120] | 5.5336 | 68.6514 | 12118.5394 | 80.6039 | 3590.9924
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL | 2.2134 | 27.5234 | 12146.0628 | 80.42 | 3593.2058
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAPEL_DEWI | 2.6561 | 33.3032 | 12179.366 | 79.7555 | 3595.8619
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(160,320] | 2.6561 | 33.8449 | 12213.2109 | 78.4791 | 3598.518
DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PRESELI_SUPPLY | 1.5494 | 19.841 | 12233.0519 | 78.0907 | 3600.0674
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE | 1.9921 | 25.8013 | 12258.8532 | 77.2087 | 3602.0595
DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL | 1.9921 | 25.992 | 12284.8452 | 76.6422 | 3604.0516
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN | 3.9842 | 52.2135 | 12337.0588 | 76.3053 | 3608.0358
DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD | 1.7707 | 23.4716 | 12360.5303 | 75.4421 | 3609.8065
DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960 | 1.5494 | 20.7141 | 12381.2444 | 74.7994 | 3611.3559
DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-POLYURETHANE | 1.5494 | 20.7452 | 12401.9896 | 74.687 | 3612.9053
DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1961_1980-WESTERN-NONE | 1.5494 | 20.7475 | 12422.7371 | 74.6789 | 3614.4547
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(120,160]-PEMBROKESHIRE | 1.7707 | 24.0017 | 12446.7388 | 73.7758 | 3616.2254
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(160,320]-SLUVAD__COURT_FARM__LLWYNON | 1.5494 | 21.1465 | 12467.8853 | 73.2697 | 3617.7748
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940 | 2.2134 | 30.3184 | 12498.2037 | 73.0062 | 3619.9883
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1941_1960-EASTERN-NONE | 1.5494 | 21.2245 | 12519.4282 | 73.0006 | 3621.5377
DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL | 1.5494 | 21.2558 | 12540.6839 | 72.8932 | 3623.0871
DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PRESELI_SUPPLY | 1.5494 | 21.2774 | 12561.9614 | 72.8189 | 3624.6365
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(120,160] | 2.2134 | 30.5587 | 12592.5201 | 72.4319 | 3626.8499
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | 3.7628 | 51.9944 | 12644.5145 | 72.3698 | 3630.6127
DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-EASTERN-CEMENT_MORTAR-(70,120] | 2.4348 | 34.0614 | 12678.576 | 71.4818 | 3633.0475
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960 | 1.9921 | 27.9577 | 12706.5337 | 71.2535 | 3635.0396
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(0,70]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | 1.9921 | 27.9716 | 12734.5053 | 71.2181 | 3637.0317
DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(160,320]-TALYBONT-ABERGAVENNY__CWMTILLERY | 1.7707 | 24.8863 | 12759.3916 | 71.1533 | 3638.8024
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-NORTHERN | 1.5494 | 21.7808 | 12781.1724 | 71.136 | 3640.3518
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-WESTERN-NONE | 1.9921 | 28.0427 | 12809.2151 | 71.0377 | 3642.3439
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN | 4.4269 | 62.7377 | 12871.9528 | 70.5614 | 3646.7708
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE | 2.2134 | 31.4827 | 12903.4355 | 70.3061 | 3648.9842
DIAM_LT_320-FERROUS_1-<=320mm-B05_1890-1881_1900-CENTRAL | 1.9921 | 28.6525 | 12932.088 | 69.5257 | 3650.9763
DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | 2.2134 | 31.9318 | 12964.0198 | 69.3174 | 3653.1897
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-WESTERN | 2.4348 | 35.2546 | 12999.2745 | 69.0625 | 3655.6245
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(0,70] | 2.4348 | 35.262 | 13034.5365 | 69.0479 | 3658.0592
DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(160,320] | 1.7707 | 26.0128 | 13060.5493 | 68.072 | 3659.83
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-EPOXY_RESIN | 1.9921 | 29.3132 | 13089.8625 | 67.9586 | 3661.8221
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-CENTRAL-NONE | 2.4348 | 35.8787 | 13125.7412 | 67.8613 | 3664.2568
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE | 1.9921 | 29.5487 | 13155.2899 | 67.417 | 3666.2489
DIAM_LT_320-FERROUS_1-<=320mm | 7.3043 | 108.5588 | 13263.8487 | 67.2844 | 3673.5532
DIAM_GT_320-STEEL->450mm and <=610mm-B07_1910-1901_1920 | 0.66403 | 9.9824 | 13273.831 | 66.5203 | 3674.2173
DIAM_LT_320-PLASTIC_PVC-<=320mm | 1.9921 | 30.0647 | 13303.8957 | 66.26 | 3676.2094
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-NORTHERN-NONE | 2.2134 | 33.5288 | 13337.4245 | 66.0157 | 3678.4228
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160]-NORTH_ERYRI_/_YNYS_MON | 1.9921 | 30.3214 | 13367.7459 | 65.6991 | 3680.4149
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON | 1.9921 | 30.3623 | 13398.1082 | 65.6105 | 3682.407
DIAM_LT_320-STEEL-<=320mm-B12_1960-1961_1980 | 1.7707 | 27.26 | 13425.3682 | 64.9575 | 3684.1777
DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | 1.7707 | 27.3571 | 13452.7253 | 64.7269 | 3685.9484
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA | 1.5494 | 24.0168 | 13476.7421 | 64.5132 | 3687.4978
DIAM_GT_320-AC->320mm and <=450mm-B12_1960 | 0.88537 | 13.8486 | 13490.5907 | 63.9322 | 3688.3832
DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PENCOED__BRIDGEND_VALLEYS | 1.7707 | 27.7444 | 13518.3351 | 63.8235 | 3690.154
DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | 1.9921 | 31.2392 | 13549.5743 | 63.7687 | 3692.146
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-EAST_ANGLESEY_CEFNI | 2.6561 | 41.7554 | 13591.3297 | 63.6113 | 3694.8021
DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-CENTRAL | 1.7707 | 28.3183 | 13619.648 | 62.53 | 3696.5729
DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-CENTRAL-CEMENT_MORTAR-(70,120] | 2.8775 | 46.2273 | 13665.8753 | 62.2459 | 3699.4503
DIAM_LT_320-FERROUS_2-<=320mm-B15_1990-1981_2000-EASTERN-CEMENT_MORTAR-(70,120] | 1.5494 | 25.632 | 13691.5073 | 60.4479 | 3700.9997
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE | 2.2134 | 36.6301 | 13728.1374 | 60.4265 | 3703.2132
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE | 1.9921 | 34.1532 | 13762.2906 | 58.3279 | 3705.2053
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA | 2.2134 | 38.0996 | 13800.3902 | 58.0958 | 3707.4187
DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1981_2000-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON | 3.0988 | 53.5777 | 13853.9679 | 57.8375 | 3710.5175
DIAM_GT_320-FERROUS_2->320mm and <=450mm-B13_1970-1961_1980-EASTERN-NONE-(320,450]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_SW__RISCA__ABERCARN | 0.66403 | 11.5111 | 13865.4791 | 57.6857 | 3711.1815
DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM | 2.2134 | 38.5794 | 13904.0584 | 57.3734 | 3713.3949
DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN | 1.9921 | 34.7339 | 13938.7924 | 57.3527 | 3715.387
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980 | 2.4348 | 42.8351 | 13981.6274 | 56.8406 | 3717.8218
DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980 | 1.9921 | 35.3402 | 14016.9676 | 56.3688 | 3719.8139
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-ELAN_/_BUILTH-ELAN | 1.5494 | 27.6563 | 14044.6239 | 56.0234 | 3721.3633
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE | 1.7707 | 31.7224 | 14076.3463 | 55.82 | 3723.134
DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL | 1.7707 | 31.9332 | 14108.2795 | 55.4514 | 3724.9048
DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-NONE | 1.9921 | 36.3621 | 14144.6416 | 54.7846 | 3726.8969
DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1961_1980-CENTRAL | 1.9921 | 37.2625 | 14181.9042 | 53.4608 | 3728.8889
DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(160,320] | 1.9921 | 37.4145 | 14219.3187 | 53.2436 | 3730.881
DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-NORTHERN | 1.5494 | 29.3309 | 14248.6496 | 52.8248 | 3732.4304
DIAM_LT_320-FERROUS_1-<=320mm-B05_1890-1881_1900 | 1.7707 | 33.7739 | 14282.4235 | 52.4294 | 3734.2012
DIAM_LT_320-FERROUS_2-<=320mm-B17_2010-2001_2020 | 2.7389 | 52.7717 | 14335.1952 | 51.9008 | 3736.9401
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(160,320]-PONTSTICILL_HIGH_LEVEL/HEADS_O | 1.7707 | 34.6583 | 14369.8535 | 51.0914 | 3738.7108
DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(160,320] | 1.7707 | 34.6605 | 14404.514 | 51.0882 | 3740.4815
DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(160,320] | 2.2134 | 43.5157 | 14448.0297 | 50.8651 | 3742.695
DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 3.0988 | 61.1432 | 14509.1728 | 50.6811 | 3745.7938
DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1981_2000-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN | 2.4348 | 49.0382 | 14558.211 | 49.6505 | 3748.2285
DIAM_GT_320-FERROUS_1->320mm and <=450mm-B06_1900-1881_1900 | 0.66403 | 13.4468 | 14571.6577 | 49.3821 | 3748.8926
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE | 3.0988 | 62.8585 | 14634.5163 | 49.298 | 3751.9914
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-WESTERN-NONE-(160,320]-TYWI_C.U._AREA | 1.7707 | 36.0808 | 14670.5971 | 49.0771 | 3753.7621
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(160,320] | 1.5494 | 31.5964 | 14702.1934 | 49.0373 | 3755.3115
DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-CENTRAL | 1.7707 | 36.5938 | 14738.7873 | 48.3891 | 3757.0823
DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION | 1.5494 | 32.1731 | 14770.9604 | 48.1582 | 3758.6317
DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-WESTERN-NONE-(0,70]-TYWI_C.U._AREA | 2.4348 | 51.0261 | 14821.9865 | 47.7162 | 3761.0664
DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-WESTERN-CEMENT_MORTAR | 2.6561 | 56.6301 | 14878.6167 | 46.9028 | 3763.7225
DIAM_LT_320-FERROUS_2-<=320mm-B16_2000-2001_2020-CENTRAL | 2.2134 | 47.5942 | 14926.2108 | 46.5063 | 3765.936
DIAM_LT_320-PLASTIC_PE-<=320mm-B18_2020-2021_ONWARDS | 2.3314 | 50.2376 | 14976.4484 | 46.407 | 3768.2673
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW | 2.4348 | 52.6369 | 15029.0854 | 46.2559 | 3770.7021
DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-CENTRAL-NONE-(70,120] | 2.6561 | 57.8231 | 15086.9085 | 45.9352 | 3773.3582
DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-WESTERN | 2.4348 | 55.1419 | 15142.0504 | 44.1546 | 3775.793
DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1981_2000-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN | 1.5494 | 35.3496 | 15177.4 | 43.8308 | 3777.3424
DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-NORTHERN-CEMENT_MORTAR | 1.9921 | 45.4796 | 15222.8796 | 43.8018 | 3779.3345
DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN | 2.2134 | 50.5648 | 15273.4444 | 43.7741 | 3781.5479
DIAM_GT_320-FERROUS_2->320mm and <=450mm-B13_1970-1961_1980-NORTHERN-CEMENT_MORTAR-(320,450]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON | 0.88537 | 20.4083 | 15293.8527 | 43.3829 | 3782.4333
DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980 | 1.5494 | 36.2423 | 15330.095 | 42.7511 | 3783.9827
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-CLWYD_COASTAL-ABERGELE__RHYL_GLASCOED | 1.9921 | 46.7691 | 15376.8642 | 42.594 | 3785.9748
DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-NORTHERN-NONE | 1.7707 | 41.9468 | 15418.811 | 42.214 | 3787.7455
DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL | 2.2134 | 52.5275 | 15471.3385 | 42.1385 | 3789.9589
DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-CENTRAL-CEMENT_MORTAR-(120,160] | 1.9921 | 47.2749 | 15518.6134 | 42.1383 | 3791.951
DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-CENTRAL-CEMENT_MORTAR-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 3.9842 | 95.509 | 15614.1224 | 41.7151 | 3795.9352
DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(160,320]-SLUVAD__COURT_FARM__LLWYNON | 1.7707 | 42.876 | 15656.9984 | 41.2992 | 3797.7059
DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1981_2000-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | 2.4348 | 59.1171 | 15716.1155 | 41.1856 | 3800.1407
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-EAST_ANGLESEY_CEFNI | 1.5494 | 37.6667 | 15753.7822 | 41.1345 | 3801.6901
DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980 | 1.7707 | 43.4313 | 15797.2135 | 40.7711 | 3803.4609
DIAM_LT_320-PLASTIC_PE-<=320mm-B17_2010-2001_2020-CENTRAL-NONE | 2.0212 | 49.6067 | 15846.8202 | 40.7454 | 3805.4821
DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL | 3.3201 | 82.3161 | 15929.1363 | 40.334 | 3808.8022
DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-LLANELLI_FELINDRE | 2.8775 | 71.6533 | 16000.7896 | 40.1581 | 3811.6797
DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(70,120] | 4.6482 | 116.0447 | 16116.8343 | 40.0553 | 3816.3279
DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1961_1980-CENTRAL-CEMENT_MORTAR-(70,120] | 2.6561 | 66.866 | 16183.7003 | 39.7229 | 3818.984
DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW | 1.5494 | 39.1894 | 16222.8897 | 39.5361 | 3820.5334
DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1981_2000-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | 6.4189 | 163.0006 | 16385.8903 | 39.3799 | 3826.9524
DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000 | 1.7707 | 45.0118 | 16430.9021 | 39.3395 | 3828.7231
DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN | 1.5494 | 39.6473 | 16470.5494 | 39.0796 | 3830.2725
DIAM_LT_320-FERROUS_2-<=320mm-B15_1990-1981_2000-NORTHERN-CEMENT_MORTAR-(70,120] | 1.5494 | 40.982 | 16511.5314 | 37.8069 | 3831.8219
DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1961_1980-NORTHERN-NONE-(70,120] | 1.5494 | 41.7981 | 16553.3295 | 37.0686 | 3833.3713
DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-EASTERN | 1.5494 | 41.8074 | 16595.1369 | 37.0604 | 3834.9207
DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-CENTRAL-NONE-(160,320] | 1.9921 | 55.4374 | 16650.5743 | 35.934 | 3836.9128
DIAM_GT_320-FERROUS_2->320mm and <=450mm-B16_2000-2001_2020-EASTERN-EPOXY_RESIN-(320,450]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL | 0.66403 | 18.707 | 16669.2813 | 35.4963 | 3837.5768
DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(160,320] | 1.5494 | 44.4028 | 16713.6841 | 34.8942 | 3839.1262
DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(70,120] | 3.7628 | 108.6284 | 16822.3126 | 34.6394 | 3842.889
DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1981_2000-NORTHERN-NONE | 1.9921 | 59.0725 | 16881.3851 | 33.7227 | 3844.8811
DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-CENTRAL-NONE-(120,160] | 1.5494 | 47.0148 | 16928.3999 | 32.9556 | 3846.4305
DIAM_GT_320-FERROUS_1->450mm and <=610mm-B12_1960-1961_1980-EASTERN-NONE-(450,610] | 0.66403 | 20.4383 | 16948.8381 | 32.4895 | 3847.0946
DIAM_GT_320-FERROUS_1->320mm and <=450mm-B12_1960-1961_1980 | 0.88537 | 27.5945 | 16976.4326 | 32.0851 | 3847.9799
DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-EASTERN-CEMENT_MORTAR-(160,320] | 2.6561 | 82.9268 | 17059.3594 | 32.0296 | 3850.636
DIAM_LT_320-PLASTIC_PE-<=320mm-B17_2010-2001_2020-WESTERN-NONE-(0,70] | 2.3718 | 74.3294 | 17133.6888 | 31.9089 | 3853.0078
DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAPEL_DEWI | 2.4348 | 76.9935 | 17210.6823 | 31.6231 | 3855.4426
DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-CENTRAL-NONE-(70,120] | 2.2134 | 69.9955 | 17280.6777 | 31.6225 | 3857.656
DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-EASTERN-NONE | 2.4348 | 77.0763 | 17357.754 | 31.5891 | 3860.0908
DIAM_GT_320-FERROUS_2->320mm and <=450mm-B13_1970-1961_1980-EASTERN | 0.66403 | 21.1797 | 17378.9337 | 31.3521 | 3860.7548
DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-EASTERN-NONE-(160,320]-HEREFORD_C.U._AREA | 1.5494 | 49.9136 | 17428.8474 | 31.0416 | 3862.3042
DIAM_LT_320-FERROUS_2-<=320mm | 1.9277 | 62.4075 | 17491.2549 | 30.8883 | 3864.2319
DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(120,160]-TALYBONT-ABERGAVENNY__CWMTILLERY | 3.3201 | 107.8409 | 17599.0958 | 30.7874 | 3867.552
DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY | 3.5415 | 115.4523 | 17714.548 | 30.6749 | 3871.0935
DIAM_GT_320-FERROUS_1->320mm and <=450mm-B06_1900-1901_1920 | 0.66403 | 22.1351 | 17736.6831 | 29.9989 | 3871.7575
DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 2.6561 | 88.6929 | 17825.3761 | 29.9473 | 3874.4136
DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | 2.2134 | 73.9578 | 17899.3339 | 29.9283 | 3876.6271
DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1981_2000-WESTERN-NONE | 1.5494 | 52.3607 | 17951.6945 | 29.5909 | 3878.1765
DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-WESTERN-CEMENT_MORTAR | 1.7707 | 61.5452 | 18013.2398 | 28.7714 | 3879.9472
DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(160,320] | 2.2134 | 78.4374 | 18091.6772 | 28.219 | 3882.1606
DIAM_LT_320-FERROUS_2-<=320mm-B11_1950-1941_1960-WESTERN | 2.2134 | 78.6264 | 18170.3035 | 28.1512 | 3884.3741
DIAM_LT_320-FERROUS_2-<=320mm-B16_2000-2001_2020 | 2.6561 | 94.9469 | 18265.2504 | 27.9747 | 3887.0302
DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-CENTRAL-NONE | 2.6561 | 96.4789 | 18361.7293 | 27.5305 | 3889.6863
DIAM_LT_320-FERROUS_2-<=320mm-B15_1990-1981_2000-EASTERN-CEMENT_MORTAR-(160,320] | 1.5494 | 56.4909 | 18418.2203 | 27.4274 | 3891.2357
DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(0,70] | 2.2134 | 80.8626 | 18499.0828 | 27.3727 | 3893.4491
DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-WESTERN-CEMENT_MORTAR-(160,320]-TYWI_C.U._AREA | 1.5494 | 57.3505 | 18556.4333 | 27.0163 | 3894.9985
DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD | 1.7707 | 65.5636 | 18621.9969 | 27.008 | 3896.7693
DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-WESTERN-NONE-(0,70] | 1.5494 | 57.7485 | 18679.7454 | 26.8301 | 3898.3187
DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000 | 1.5494 | 58.3389 | 18738.0843 | 26.5586 | 3899.8681
DIAM_LT_320-PLASTIC_PE-<=320mm-B14_1980-1981_2000-EASTERN-NONE-(120,160] | 2.4348 | 91.7673 | 18829.8516 | 26.532 | 3902.3028
DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN | 1.5494 | 58.8033 | 18888.6549 | 26.3488 | 3903.8522
DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA | 2.4348 | 93.8772 | 18982.5322 | 25.9357 | 3906.287
DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-NORTHERN-NONE-(70,120] | 3.7628 | 145.3049 | 19127.8371 | 25.8961 | 3910.0498
DIAM_LT_320-PLASTIC_PVC-<=320mm-B16_2000-2001_2020 | 1.7707 | 68.5366 | 19196.3737 | 25.8364 | 3911.8206
DIAM_GT_320-FERROUS_2->320mm and <=450mm-B15_1990-1981_2000-EASTERN-CEMENT_MORTAR-(320,450] | 1.1067 | 43.6626 | 19240.0363 | 25.347 | 3912.9273
DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | 2.4348 | 96.6922 | 19336.7285 | 25.1806 | 3915.3621
DIAM_LT_320-PLASTIC_PE-<=320mm-B14_1980-1981_2000 | 3.0988 | 123.6303 | 19460.3588 | 25.065 | 3918.4609
DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | 2.6561 | 107.1434 | 19567.5022 | 24.7903 | 3921.117
DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-CENTRAL-NONE-(120,160] | 1.7707 | 71.502 | 19639.0041 | 24.765 | 3922.8877
DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-CENTRAL-NONE | 1.5494 | 63.2957 | 19702.2998 | 24.4788 | 3924.4371
DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000 | 1.5494 | 63.6539 | 19765.9537 | 24.341 | 3925.9865
DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(120,160] | 1.7707 | 75.2 | 19841.1537 | 23.5471 | 3927.7573
DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | 3.3201 | 146.601 | 19987.7547 | 22.6475 | 3931.0774
DIAM_GT_320-FERROUS_1->450mm and <=610mm-B11_1950-1941_1960 | 0.66403 | 29.4214 | 20017.1761 | 22.5696 | 3931.7414
DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PRESELI_SUPPLY | 1.9921 | 88.3699 | 20105.546 | 22.5426 | 3933.7335
DIAM_GT_320-FERROUS_2->320mm and <=450mm-B13_1970-1961_1980 | 0.66403 | 29.5641 | 20135.11 | 22.4607 | 3934.3975
DIAM_GT_320-FERROUS_1->450mm and <=610mm | 1.5494 | 70.762 | 20205.8721 | 21.8959 | 3935.9469
DIAM_LT_320-PLASTIC_PE-<=320mm | 3.4398 | 158.6537 | 20364.5257 | 21.6811 | 3939.3867
DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-WESTERN-NONE-(70,120] | 3.7628 | 176.8226 | 20541.3483 | 21.2802 | 3943.1496
DIAM_GT_320-FERROUS_1->450mm and <=610mm-B07_1910-1901_1920 | 0.66403 | 31.2287 | 20572.5771 | 21.2634 | 3943.8136
DIAM_LT_320-PLASTIC_PE-<=320mm-B17_2010-2001_2020-CENTRAL-NONE-(70,120] | 2.0526 | 98.4205 | 20670.9976 | 20.8553 | 3945.8662
DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-EASTERN-NONE-(0,70] | 2.6561 | 127.7897 | 20798.7873 | 20.785 | 3948.5223
DIAM_GT_320-FERROUS_2->320mm and <=450mm-B13_1970-1961_1980-WESTERN | 0.66403 | 33.3787 | 20832.1659 | 19.8938 | 3949.1863
DIAM_LT_320-PLASTIC_PE-<=320mm-B17_2010-2001_2020-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | 2.5527 | 130.4877 | 20962.6536 | 19.5627 | 3951.739
DIAM_GT_320-FERROUS_1->320mm and <=450mm-B08_1920-1921_1940 | 0.66403 | 34.0957 | 20996.7493 | 19.4754 | 3952.403
DIAM_LT_320-PLASTIC_PE-<=320mm-B17_2010-2001_2020-EASTERN-NONE-(70,120] | 4.1458 | 219.3154 | 21216.0647 | 18.9034 | 3956.5488
DIAM_LT_320-FERROUS_2-<=320mm-B15_1990-1981_2000-CENTRAL-CEMENT_MORTAR | 1.9921 | 105.7431 | 21321.8077 | 18.8389 | 3958.5409
DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-WESTERN-NONE-(120,160] | 1.7707 | 97.016 | 21418.8237 | 18.2521 | 3960.3117
DIAM_LT_320-PLASTIC_PE-<=320mm-B17_2010-2001_2020-WESTERN-NONE-(70,120] | 2.2255 | 125.9134 | 21544.7372 | 17.6751 | 3962.5372
DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-WESTERN-NONE | 2.4348 | 141.262 | 21685.9991 | 17.2359 | 3964.972
DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-NORTHERN-NONE-(70,120] | 1.7707 | 103.6776 | 21789.6767 | 17.0793 | 3966.7427
DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-WESTERN-NONE | 1.5494 | 91.3193 | 21880.996 | 16.9668 | 3968.2921
DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA | 1.5494 | 91.4897 | 21972.4857 | 16.9352 | 3969.8415
DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN | 2.4348 | 144.8952 | 22117.3808 | 16.8037 | 3972.2763
DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-WESTERN-NONE-(120,160] | 2.8775 | 174.1763 | 22291.5572 | 16.5204 | 3975.1537
DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA | 1.7707 | 110.2674 | 22401.8246 | 16.0586 | 3976.9245
DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | 5.5336 | 346.2703 | 22748.0949 | 15.9805 | 3982.4581
DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-EASTERN-NONE-(120,160] | 3.0988 | 200.9577 | 22949.0526 | 15.4202 | 3985.5569
DIAM_GT_320-FERROUS_2->320mm and <=450mm-B16_2000-2001_2020 | 0.66403 | 43.3081 | 22992.3607 | 15.3327 | 3986.2209
DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-EASTERN-NONE-(70,120] | 4.8695 | 318.6634 | 23311.0241 | 15.2811 | 3991.0904
DIAM_LT_320-PLASTIC_PE-<=320mm-B17_2010-2001_2020-NORTHERN-NONE | 2.4348 | 159.473 | 23470.4971 | 15.2676 | 3993.5252
DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-NORTHERN-NONE-(70,120]-ALWEN_/_DEE | 1.5494 | 103.112 | 23573.6091 | 15.0264 | 3995.0746
DIAM_GT_320-FERROUS_1->450mm and <=610mm-B08_1920 | 0.66403 | 44.2272 | 23617.8364 | 15.014 | 3995.7386
DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-NORTHERN | 1.5494 | 105.38 | 23723.2164 | 14.703 | 3997.288
DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-NORTHERN-NONE-(160,320] | 1.7707 | 120.8574 | 23844.0738 | 14.6515 | 3999.0588
DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(120,160] | 3.0988 | 219.959 | 24064.0329 | 14.0881 | 4002.1576
DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-WESTERN-NONE-(70,120] | 1.5494 | 113.3497 | 24177.3826 | 13.6692 | 4003.707
DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | 2.4348 | 183.4648 | 24360.8473 | 13.2711 | 4006.1417
DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL | 1.7707 | 139.885 | 24500.7323 | 12.6586 | 4007.9125
DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL | 2.8775 | 249.1136 | 24749.8459 | 11.5508 | 4010.7899
DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-WESTERN-NONE | 1.5494 | 139.651 | 24889.4969 | 11.0948 | 4012.3393
DIAM_GT_320-STEEL->320mm and <=450mm | 1.1067 | 100.2912 | 24989.7882 | 11.035 | 4013.4461
DIAM_LT_320-FERROUS_2-<=320mm-B15_1990-1981_2000-WESTERN-CEMENT_MORTAR | 1.9921 | 183.5565 | 25173.3446 | 10.8527 | 4015.4381
DIAM_GT_320-FERROUS_1->320mm and <=450mm | 1.3281 | 122.4038 | 25295.7485 | 10.8498 | 4016.7662
DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-NORTHERN-NONE-(70,120] | 2.8775 | 280.7902 | 25576.5386 | 10.2477 | 4019.6437
DIAM_LT_320-FERROUS_2-<=320mm-B15_1990-1981_2000 | 2.2134 | 222.9507 | 25799.4893 | 9.9279 | 4021.8571
DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-NORTHERN-NONE | 2.6561 | 272.8248 | 26072.3142 | 9.7356 | 4024.5132
DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-NORTHERN-NONE | 1.9921 | 209.9392 | 26282.2534 | 9.4889 | 4026.5053
DIAM_LT_320-PLASTIC_PE-<=320mm-B17_2010-2001_2020-NORTHERN-NONE-(70,120] | 1.7763 | 199.5654 | 26481.8187 | 8.9011 | 4028.2816
DIAM_LT_320-PLASTIC_PE-<=320mm-B17_2010-2001_2020-EASTERN-NONE | 1.5769 | 194.471 | 26676.2897 | 8.1086 | 4029.8585
DIAM_GT_320-FERROUS_2->320mm and <=450mm-B14_1980-1981_2000 | 0.66403 | 96.7943 | 26773.0841 | 6.8602 | 4030.5225
DIAM_GT_320-FERROUS_2->320mm and <=450mm-B15_1990-1981_2000 | 0.66403 | 97.9906 | 26871.0746 | 6.7765 | 4031.1866
DIAM_GT_320 | 1.5494 | 581.7686 | 27452.8432 | 2.6633 | 4032.736
DIAM_GT_320-FERROUS_2 | 0.66403 | 314.9393 | 27767.7825 | 2.1084 | 4033.4
LENGTH RECONCILE | 0 | 107.4175 | 27875.2 | 0 | 4033.4

## Pivot_All Mains
Sum of Average of bursts_year | Column Labels
Row Labels | 1 | 2 | 3 | 4 | 5 | Grand Total
DIAM_GT_320 | 22.1343 | 3.7628 | 0.66403 | 5.0909 | 3.0988 | 34.7508
DIAM_LT_320 | 748.3677 | 816.3123 | 1023.7106 | 649.7246 | 760.5339 | 3998.6492
Grand Total | 770.502 | 820.0752 | 1024.3746 | 654.8155 | 763.6327 | 4033.4

## Pivot_All Mains Pasted Outputs
Sum of Sum of LENGTH_KM | 1 | 2 | 3 | 4 | 5 | Grand Total
DIAM_GT_320 | 1866.1175 | 23.1549 | 2.3707 | 6.1369 | 2.42 | 1900.2 | Line CW20.2
DIAM_LT_320 | 17128.0531 | 4497.4552 | 3026.1043 | 935.3763 | 388.011 | 25975 | Line CW20.1
Grand Total | 18994.1706 | 4520.6101 | 3028.475 | 941.5131 | 390.4311 | 27875.2 |  | matches APR23
Sum of Average of bursts_year | 1 | 2 | 3 | 4 | 5 | Grand Total
DIAM_GT_320 | 22.1343 | 3.7628 | 0.66403 | 5.0909 | 3.0988 | 34.7508 | Line CW20.11
DIAM_LT_320 | 748.3677 | 816.3123 | 1023.7106 | 649.7246 | 760.5339 | 3998.6492 | Line CW20.9
Grand Total | 770.502 | 820.0752 | 1024.3746 | 654.8155 | 763.6327 | 4033.4 | Line CW20.12 | matches 5yr ave APR 19 to 23
DIAM_LT_320 | 65.94% | 17.31% | 11.65% | 3.601% | 1.494% | 100% | length share
DIAM_GT_320 | 98.21% | 1.219% | 0.1248% | 0.323% | 0.1274% | 100% | length share

## Cohort Table_MainsAge>5
|  |  | Primary | Primary | Secondary |  | Primary | Secondary
COHORT_REF | COHORT_ID | GROUP | ASSET_MATERIAL_BIN | DATE_INSTALL_BIN_20YRS | DATE_INSTALL_BIN | DIAM_>GT or < LT 320mm | DIAM_BIN_PRIMARY | DIAM_BIN_SECOND | Sum of LENGTH_KM | Average of bursts_year | Average of bursts_1000km_year | CONDITION_GRADE
1 | DIAM_LT_320 | DIAM_LT_320 | [6 empty] | 21.3205 | 2.6561 | 124.5804 | 1
2 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | [6 empty] | 5.8399 | 1.9921 | 341.1168 | 3
3 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-CENTRAL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 5.2457 | 1.5494 | 295.3669 | 3
4 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(0,70]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1921_1940 | B09_1930 |  | <=320mm | (0,70] | 4.1092 | 1.5494 | 377.0549 | 3
5 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1921_1940 | B09_1930 |  | <=320mm | (120,160] | 3.5494 | 2.6561 | 748.3179 | 4
6 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF-TREFOREST-TREFOREST IND. EST. WEST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B09_1930 |  | <=320mm | (120,160] | 1.5931 | 3.0988 | 1945.1179 | 5
7 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(160,320] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1921_1940 | B09_1930 |  | <=320mm | (160,320] | 16.385 | 1.5494 | 94.5619 | 1
8 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 6.9185 | 1.7707 | 255.942 | 3
9 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RHYMNEY__BARGOED-WINDSOR HOTEL-THE GARTH ABERTRIDWR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 0.77481 | 1.9921 | 2571.0789 | 5
10 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 12.9324 | 4.4269 | 342.3085 | 3
11 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__RUMNEY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 1.902 | 1.5494 | 814.613 | 4
12 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-VALE_OF_GLAM__RHONDDA_VALLEYS-LILLYPOT RESERVOIR-WELSH ST DONATS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 1.0857 | 2.6561 | 2446.4234 | 5
13 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-EASTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 12.7852 | 2.4348 | 190.4367 | 2
14 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(0,70]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1921_1940 | B09_1930 |  | <=320mm | (0,70] | 3.8631 | 1.5494 | 401.0745 | 3
15 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(0,70]-TALYBONT-ABERGAVENNY__CWMTILLERY-PONTYPOOL TDMA-AREA FED BY SUB SUPPLY SYSTEM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B09_1930 |  | <=320mm | (0,70] | 0.83958 | 1.9921 | 2372.7288 | 5
16 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(120,160]-TALYBONT-ABERGAVENNY__CWMTILLERY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1921_1940 | B09_1930 |  | <=320mm | (120,160] | 1.8673 | 1.5494 | 829.7712 | 4
17 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 13.5533 | 1.9921 | 146.9819 | 2
18 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(70,120]-ELAN_/_BUILTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 0.71939 | 1.7707 | 2461.4429 | 5
19 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 11.2162 | 1.5494 | 138.1393 | 2
20 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM-ST BRIDES ROAD-MAGOR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 2.5896 | 2.4348 | 940.2154 | 4
21 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-PONTYPOOL TDMA-AREA FED BY SUB SUPPLY SYSTEM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 1.6552 | 1.5494 | 936.0783 | 4
22 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(0,70]-ALWEN_/_DEE-DENBIGH_ALWEN-MEIFOD-1104 FOELAS (G10) | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B09_1930 |  | <=320mm | (0,70] | 0.68782 | 3.0988 | 4505.2726 | 5
23 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-BEUDY MAWR-BEUDY MAWR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B09_1930 |  | <=320mm | (0,70] | 0.82088 | 3.5415 | 4314.247 | 5
24 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-BUTLINS-LLANGYBI - BODOWEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B09_1930 |  | <=320mm | (0,70] | 0.57811 | 3.5415 | 6125.9846 | 5
25 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1921_1940 | B09_1930 |  | <=320mm | (120,160] | 8.5262 | 1.5494 | 181.7212 | 2
26 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 11.6219 | 4.2055 | 361.8617 | 3
27 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 8.0434 | 2.4348 | 302.7043 | 3
28 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-CONWY-GYFFIN-CASTLE VIEW | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 0.050541 | 1.5494 | 30656.1546 | 5
29 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT & GORSWEN TRUNK-OUTLET LLANGERNYW SRV | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 2.7041 | 2.8775 | 1064.098 | 5
30 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 4.7678 | 1.7707 | 371.3969 | 3
31 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-CEMAES-CEMAES BAY VILLAGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 2.3822 | 1.7707 | 743.3376 | 4
32 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-WESTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 4.1556 | 1.5494 | 372.8448 | 3
33 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1921_1940 | B09_1930 |  | <=320mm | (0,70] | 6.1077 | 2.6561 | 434.878 | 3
34 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-LLANLLWNI-BELL VUE TO LLANYBYDDER | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B09_1930 |  | <=320mm | (0,70] | 2.1487 | 4.2055 | 1957.2115 | 5
35 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-WESTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 2.8808 | 1.7707 | 614.6761 | 4
36 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 15.6574 | 1.7707 | 113.0931 | 1
37 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-GORLLWYN RHOS TREALAU-RHOS RES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 3.2204 | 3.3201 | 1030.9672 | 5
38 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-BETTWS LLANGYBI AND LLANDDEWI BREFI-BETTWS BLEDRWS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 10.2832 | 1.5494 | 150.6736 | 2
39 | DIAM_LT_320-AC-<=320mm-B09_1930-1921_1940-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-DERI GOCH PS TO RHOSYMRYSON SR-CAPEL Y GROES TO LLANWNEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 4.8674 | 1.5494 | 318.3244 | 3
40 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 11.2804 | 2.4348 | 215.8407 | 2
41 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-EASTERN-NONE-(0,70]-ELAN_/_BUILTH-BUILTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1921_1940 | B10_1940 |  | <=320mm | (0,70] | 1.4022 | 1.5494 | 1104.9859 | 5
42 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-NORTHERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 9.4721 | 1.9921 | 210.3098 | 2
43 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1921_1940 | B10_1940 |  | <=320mm | (0,70] | 6.1236 | 2.8775 | 469.8966 | 3
44 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(0,70]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1921_1940 | B10_1940 |  | <=320mm | (0,70] | 1.5846 | 1.7707 | 1117.4688 | 5
45 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1921_1940 | B10_1940 |  | <=320mm | (120,160] | 4.6256 | 2.2134 | 478.5221 | 3
46 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(120,160]-ALWEN_/_DEE-DENBIGH_ALWEN-ALWEN TO PEN Y COED & ACCRE TRUNK-ACCRE PUMPING STATION | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B10_1940 |  | <=320mm | (120,160] | 3.012 | 1.9921 | 661.388 | 4
47 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(120,160]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-GWYTHERIN-GWYTHERIN RESOUTLET (R00) | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B10_1940 |  | <=320mm | (120,160] | 2.8529 | 1.9921 | 698.2568 | 4
48 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 3.7616 | 1.7707 | 470.7388 | 3
49 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-ALWEN TO PEN Y COED & ACCRE TRUNK-ERYRYS PUMPING STATION | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 4.4887 | 1.5494 | 345.1774 | 3
50 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-LLANGWYFAN-WAEN ABERWHEELER GEINAS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 3.5935 | 2.8775 | 800.7289 | 4
51 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 3.4417 | 2.2134 | 643.1134 | 4
52 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 3.4514 | 1.9921 | 577.1877 | 4
53 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-BRYN BEDDAU SOUTH-BICELL RESERVOIR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 2.0079 | 3.0988 | 1543.3199 | 5
54 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1921_1940 | B10_1940 |  | <=320mm | (0,70] | 1.0706 | 1.7707 | 1654.0103 | 5
55 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1921_1940 | B10_1940 |  | <=320mm | (0,70] | 2.0403 | 1.5494 | 759.4004 | 4
56 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(0,70]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH-CAPEL SEION LLANRHYSTUD-LLANFARIAN VILLAGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B10_1940 |  | <=320mm | (0,70] | 0.60058 | 1.9921 | 3316.958 | 5
57 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(0,70]-PEMBROKESHIRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1921_1940 | B10_1940 |  | <=320mm | (0,70] | 1.7768 | 1.5494 | 872.0114 | 4
58 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 3.2862 | 1.5494 | 471.4828 | 3
59 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 10.772 | 3.5415 | 328.768 | 3
60 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-CRYMYCH-CRYMYCH AT GARN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 1.4875 | 1.9921 | 1339.2198 | 5
61 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-CRYMYCH-PENTREGALAR AT GARN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 3.0278 | 2.8775 | 950.3328 | 4
62 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-NORTH_CEREDIGION | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 5.1362 | 1.5494 | 301.6632 | 3
63 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-NORTH_CEREDIGION-ABERYSTWYTH_BONTGOCH__LOVESGROVE-CEFNLLAN SR OUTLETS-ST DAVIDS RD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 0.37258 | 1.7707 | 4752.6859 | 5
64 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 4.8758 | 1.5494 | 317.7705 | 3
65 | DIAM_LT_320-AC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE-MYNYDD NEWYDD TO FFOREST FACH-BLEAN Y MAES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 3.1898 | 1.5494 | 485.7387 | 3
66 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | [6 empty] | 10.8718 | 1.5494 | 142.5161 | 2
67 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 3.8971 | 1.9921 | 511.1715 | 4
68 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-CENTRAL-NONE-(0,70]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (0,70] | 2.8204 | 1.9921 | 706.3105 | 4
69 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 13.8036 | 4.6482 | 336.7378 | 3
70 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_HEATH_&_LLANISHEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 3.3258 | 3.3201 | 998.2997 | 4
71 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-EASTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1941_1960 | B10_1940 |  | <=320mm | (0,70] | 2.5498 | 1.9921 | 781.276 | 4
72 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-EASTERN-NONE-(0,70]-BRECON_/_PORTIS-PORTIS-PORTIS LOW-LOWER CHAPEL LINE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (0,70] | 1.3053 | 1.7707 | 1356.5295 | 5
73 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-EASTERN-NONE-(0,70]-ELAN_/_BUILTH-BUILTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (0,70] | 0.16572 | 1.5494 | 9349.2358 | 5
74 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-EASTERN-NONE-(0,70]-ELAN_/_BUILTH-BUILTH-BUILTH WELLS-AREA FEED BY 1T810231 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (0,70] | 1.279 | 5.9763 | 4672.6662 | 5
75 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-EASTERN-NONE-(0,70]-ELAN_/_BUILTH-BUILTH-BUILTH WELLS-BUILTH TO CILMERY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (0,70] | 0.35372 | 1.5494 | 4380.2431 | 5
76 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-EASTERN-NONE-(0,70]-ELAN_/_BUILTH-BUILTH-GARTH SR-LLANWRTYD WELLS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (0,70] | 0.69857 | 1.5494 | 2217.9474 | 5
77 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-EASTERN-NONE-(120,160]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL-WESTHIDE HEREFORD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (120,160] | 3.6672 | 1.5494 | 422.5038 | 3
78 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 11.2538 | 1.9921 | 177.0146 | 2
79 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-EASTERN-NONE-(70,120]-PILLETH-PILLETH_KNIGHTON__BLEDDFA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 4.0589 | 1.5494 | 381.7248 | 3
80 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1941_1960 | B10_1940 |  | <=320mm | (0,70] | 8.1131 | 2.4348 | 300.1033 | 3
81 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(0,70]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (0,70] | 1.1018 | 1.5494 | 1406.2892 | 5
82 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (0,70] | 0.90435 | 1.9921 | 2202.7806 | 5
83 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1941_1960 | B10_1940 |  | <=320mm | (120,160] | 12.6438 | 1.7707 | 140.0478 | 2
84 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(120,160]-SOUTH_MEIRIONNYDD-LLWYNGWRIL_GWASTADCOED-GWASTADCOED-HENBLAS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (120,160] | 4.262 | 3.7628 | 882.878 | 4
85 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 19.3447 | 2.2134 | 114.4203 | 1
86 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(70,120]-BARMOUTH-BARMOUTH_-_HARLECH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 3.3617 | 1.9921 | 592.5818 | 4
87 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(70,120]-BARMOUTH-BARMOUTH_-_HARLECH-DYFFRYN TALYBONT LLANBEDR-TALYBONT VILLAGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 0.69619 | 2.6561 | 3815.2261 | 5
88 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 7.6012 | 2.2134 | 291.1954 | 3
89 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-HOLLAND ARMS 9INCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 6.6768 | 1.7707 | 265.2077 | 3
90 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-HOLLAND ARMS 9INCH-DWYRAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 5.1358 | 1.5494 | 301.689 | 3
91 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 10.7973 | 1.7707 | 163.9981 | 2
92 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1941_1960 | B10_1940 |  | <=320mm | (0,70] | 5.3968 | 1.9921 | 369.1243 | 3
93 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (0,70] | 11.3849 | 4.4269 | 388.837 | 3
94 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-CROSSROADS TO CRUGIAU AND TREGAMMON-TREGAMMON WD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (0,70] | 11.0909 | 8.6324 | 778.3277 | 4
95 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-EGLWYSWRW-BRYNBERIAN WD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (0,70] | 1.2282 | 2.2134 | 1802.2405 | 5
96 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-FFYNNON LLAWDDOG-BEULAH TO CWMCOU | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (0,70] | 3.2952 | 4.4269 | 1343.4325 | 5
97 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-NEWQUAY-SYNOD INN TO NEW QUAY 6 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (0,70] | 2.0653 | 7.083 | 3429.5888 | 5
98 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-PENPARC SR TO CARDIGAN SR-PENPARC SOUTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (0,70] | 2.0532 | 5.0909 | 2479.5297 | 5
99 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SARNAU CROSS CONNECTION-SARNAU BPT OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (0,70] | 3.6154 | 3.0988 | 857.1217 | 4
100 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-MAESTIR TO BRYNGARREG-MAESTIR TO BRYNGARREG | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (0,70] | 0.21322 | 1.5494 | 7266.5871 | 5
101 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-NORTH_CEREDIGION | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (0,70] | 0.98235 | 1.5494 | 1577.2454 | 5
102 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (0,70] | 9.9933 | 2.8775 | 287.9384 | 3
103 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-CEFN BRYN OUTLETS TO S W GOWER-PENMAEN WD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (0,70] | 1.3151 | 2.6561 | 2019.7044 | 5
104 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (120,160] | 9.5513 | 2.2134 | 231.7408 | 2
105 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-CEFN BRYN HOUSE-REYNOLDSTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (120,160] | 1.3203 | 1.5494 | 1173.5481 | 5
106 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (120,160] | 7.1162 | 1.7707 | 248.8318 | 2
107 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 18.7472 | 3.3201 | 177.1009 | 2
108 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-BEULAU TO ABERBANC-BLEANGWENLLAN X NCE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 2.9898 | 2.4348 | 814.3504 | 4
109 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-CROSSROADS TO CRUGIAU AND TREGAMMON-TREGAMMON WD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 2.3846 | 6.6403 | 2784.6183 | 5
110 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-FFYNNON LLAWDDOG-FFYNNON LLAWDDDOG SCHEME | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 4.9998 | 3.3201 | 664.0599 | 4
111 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-GWENLLI-PENBONTARBOTHAU BPT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 1.0639 | 1.5494 | 1456.3003 | 5
112 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-HAFOD FELINWYNT-HAFOD FELINWYNT 5 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 3.5242 | 3.3201 | 942.0971 | 4
113 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-HAFOD LLECHRYD-LECHRYD VILLIAGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 1.2023 | 1.7707 | 1472.7799 | 5
114 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-NEWQUAY-SYNOD INN TO NEW QUAY 6 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 5.736 | 2.4348 | 424.4722 | 3
115 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-PENTREGAT CROSS CONNECTION-PENTREGAT RES OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 4.3563 | 2.2134 | 508.0978 | 4
116 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SARNAU CROSS CONNECTION-SARNAU BPT OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 5.0112 | 5.0909 | 1015.9064 | 5
117 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SARNAU CROSS CONNECTION-TANYGROES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 1.9396 | 3.3201 | 1711.7578 | 5
118 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SARNAU CROSS CONNECTION-TRESAITH SCHEME | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 3.1246 | 5.0909 | 1629.2987 | 5
119 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 3.9624 | 2.2134 | 558.6093 | 4
120 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 13.783 | 2.8775 | 208.7678 | 2
121 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 4.8045 | 5.3122 | 1105.6862 | 5
122 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-PORTHYRHYD TO CEFNEITHIN-FOELGASTELL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 0.13471 | 1.9921 | 14788.1964 | 5
123 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-TRAPP BULK EXPORT-PENYBANK/NANTGARDEIG 6 INCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 1.6162 | 1.9921 | 1232.5745 | 5
124 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAPEL_DEWI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 0.50267 | 1.5494 | 3082.3542 | 5
125 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAPEL_DEWI-POLIN TO RHYDARGAEAU-RHYDARGAEAU P S | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 4.0586 | 1.9921 | 490.836 | 3
126 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-LLANELLI_FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 3.5694 | 1.5494 | 434.0778 | 3
127 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 14.803 | 1.5494 | 104.6678 | 1
128 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-CEFN BRYN OUTLETS TO S W GOWER | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 15.1447 | 1.7707 | 116.9214 | 1
129 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-CEFN BRYN OUTLETS TO S W GOWER-OXWICH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 2.5153 | 2.8775 | 1143.9595 | 5
130 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-CEFN BRYN OUTLETS TO S W GOWER-PENMAEN WD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 4.2806 | 8.6324 | 2016.6247 | 5
131 | DIAM_LT_320-AC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 10.4762 | 1.7707 | 169.0255 | 2
132 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | [6 empty] | 33.1212 | 2.8775 | 86.8766 | 1
133 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 19.3949 | 1.9921 | 102.7117 | 1
134 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 1.8729 | 2.6561 | 1418.2103 | 5
135 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(0,70]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 4.2062 | 2.4348 | 578.8498 | 4
136 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 5.4197 | 5.5336 | 1021.0115 | 5
137 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_EAST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 0.9101 | 1.5494 | 1702.4568 | 5
138 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-PENARTH-ST TEILOS PENDINE AND SKOMER RD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 0.29837 | 1.5494 | 5192.8793 | 5
139 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(160,320]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_HEATH_&_LLANISHEN-BLACKOAK ROAD-BLACKOAK ROAD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (160,320] | 0.7559 | 7.9683 | 10541.5364 | 5
140 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 4.7049 | 1.7707 | 376.3609 | 3
141 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-PONTYPRIDD_PONTSTICILL_HIGH-TY GWYN 12INCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 1.3237 | 1.5494 | 1170.5027 | 5
142 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-VALE_OF_GLAM__RHONDDA_VALLEYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 5.0536 | 1.5494 | 306.5938 | 3
143 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 14.3354 | 3.5415 | 247.0445 | 2
144 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__CANTON__CATHAYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 2.4999 | 1.7707 | 708.3125 | 4
145 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_EAST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 4.3021 | 1.5494 | 360.153 | 3
146 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_HEATH_&_LLANISHEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 10.6719 | 2.2134 | 207.4067 | 2
147 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 7.0003 | 1.9921 | 284.572 | 3
148 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 10.1224 | 2.2134 | 218.6656 | 2
149 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(0,70]-ELAN_/_BUILTH-BUILTH-GARTH SR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 5.7607 | 2.8775 | 499.4978 | 3
150 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(0,70]-ELAN_/_BUILTH-BUILTH-GARTH SR-GARTH-BEALAH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 0.67056 | 2.2134 | 3300.8639 | 5
151 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(0,70]-ELAN_/_BUILTH-BUILTH-GARTH SR-TIRABAD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 0.72706 | 2.4348 | 3348.7765 | 5
152 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(0,70]-ELAN_/_BUILTH-ELAN-NEUADD NORTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 2.035 | 1.9921 | 978.9268 | 4
153 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(0,70]-TALYBONT-ABERGAVENNY__CWMTILLERY-PONTYPOOL TDMA-AREA FED BY SUB SUPPLY SYSTEM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 0.1904 | 1.5494 | 8137.7708 | 5
154 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 21.1255 | 2.2134 | 104.7753 | 1
155 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(120,160]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL-WESTHIDE HEREFORD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 0.76275 | 1.5494 | 2031.3397 | 5
156 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(120,160]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL-WESTHIDE NEWTON-WESTHIDE TO NEWTOWN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 3.0441 | 1.7707 | 581.6913 | 4
157 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(120,160]-PILLETH-PILLETH_KNIGHTON__BLEDDFA-LLANGUNLLO LINE-AREA FEED BY 1T810701 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 4.0872 | 2.6561 | 649.8656 | 4
158 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 6.5519 | 1.5494 | 236.4795 | 2
159 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 29.6322 | 3.3201 | 112.0452 | 1
160 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 26.063 | 3.5415 | 135.8817 | 2
161 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 12.5944 | 2.4348 | 193.3212 | 2
162 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN-PONTNEWYDD-MAENDY WAY TOP | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 4.9681 | 1.7707 | 356.4235 | 3
163 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 5.653 | 1.7707 | 313.2388 | 3
164 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-CROSS ASH-THE BOOT NEWCASTLE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 1.7035 | 2.4348 | 1429.2934 | 5
165 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-LLANELLEN 6INCH-LLANELLEN BRIDGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 1.5261 | 4.6482 | 3045.8136 | 5
166 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-WHITBOURNE-WHITBOURNE-RIDGEWAY STIFFORDS BRIDGE-STIFFORDS BRIDGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 0.5745 | 1.7707 | 3082.234 | 5
167 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-EASTERN-POLYURETHANE-(0,70]-BRECON_/_PORTIS-PORTIS-PORTIS LOW-LLANDEW LINE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 0.14504 | 2.2134 | 15260.9132 | 5
168 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 6.2282 | 3.0988 | 497.5396 | 3
169 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-ALWEN_/_DEE-DENBIGH_ALWEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 8.1172 | 5.5336 | 681.7082 | 4
170 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-ALWEN_/_DEE-DENBIGH_ALWEN-ALWEN TO BWLCH GAP | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 2.9132 | 1.5494 | 531.8526 | 4
171 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-ALWEN_/_DEE-DENBIGH_ALWEN-BYLCHAU HIGH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 4.5143 | 2.8775 | 637.4031 | 4
172 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-BALA-BALA-COED TALOG OUTLET-PANT SAER OUTLETS NEW DMA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 0.90111 | 2.2134 | 2456.3299 | 5
173 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 4.8863 | 2.4348 | 498.2891 | 3
174 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-LLEYNHARLECH-BANGOR__CAERNARFON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 0.84518 | 1.7707 | 2095.1046 | 5
175 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 3.6751 | 5.3122 | 1445.4707 | 5
176 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-CWMYSTRADLLYN GAP-CENIN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 0.7125 | 4.2055 | 5902.4448 | 5
177 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-NORTH_ERYRI_/_YNYS_MON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 5.9678 | 2.4348 | 407.9831 | 3
178 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-DEINIOLEN CEFN COCH-ASHTON HOUSE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 0.65502 | 2.8775 | 4392.9363 | 5
179 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-PENTIR BRYNREFAIL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 0.84082 | 1.5494 | 1842.7329 | 5
180 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-NORTH_ERYRI_/_YNYS_MON-SOUTH_ANGLESEY_CWELLYN__MYNYDD-PENMYNYDD CADNANT GAERWEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 0.69039 | 1.7707 | 2564.8303 | 5
181 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70]-SOUTH_MEIRIONNYDD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 3.4271 | 1.7707 | 516.6819 | 4
182 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 25.9641 | 4.6482 | 179.0244 | 2
183 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(120,160]-ALWEN_/_DEE-DENBIGH_ALWEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 14.396 | 2.4348 | 169.1284 | 2
184 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(120,160]-BALA-BALA-ARENIG TRUNK MAINS-LLANERCH ARENIG NEW DMA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 5.6694 | 1.9921 | 351.3731 | 3
185 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(120,160]-BALA-BALA-COED TALOG OUTLET-COED TALOG OUTLET NEW DMA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 2.5251 | 3.3201 | 1314.8417 | 5
186 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(120,160]-CLWYD_COASTAL-ABERGELE__RHYL_GLASCOED-RHUALLT TO BODFARI-0702TREMEIRCHION/BODFARI (R70) | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 2.8584 | 6.1976 | 2168.2312 | 5
187 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(120,160]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 6.7118 | 1.5494 | 230.8461 | 2
188 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(120,160]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-SYCHNANT-MAENHIR PENGROESLON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 1.6524 | 1.5494 | 937.6497 | 4
189 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(120,160]-TYWYN_/_ABERDYFI-BRYNCRUG-ESCUAN ABERDYFI TRUNK-AREA FED BY S/SUPPLY 3H900394 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 4.5654 | 5.3122 | 1163.5831 | 5
190 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 19.9056 | 4.2055 | 211.273 | 2
191 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 7.7878 | 1.7707 | 227.3738 | 2
192 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 25.4566 | 7.3043 | 286.9325 | 3
193 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-ACCRE OUTLET-ACCRE/LLANDEGLA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 4.3715 | 1.7707 | 405.0651 | 3
194 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-CARROG-TYN CEFN TRAFFICLIGHTS. | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 5.9052 | 2.8775 | 487.2735 | 3
195 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-CORWEN GAP-BETTWS GG O/TLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 1.3161 | 2.2134 | 1681.81 | 5
196 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-CORWEN GAP-BETWS GG TYRPEG | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 1.0661 | 2.6561 | 2491.4625 | 5
197 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-LLANGWYFAN-WAEN ABERWHEELER GEINAS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 2.5309 | 1.7707 | 699.6594 | 4
198 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-UWCH Y DRE CYNWYD-LLANDRILLO | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 5.2739 | 1.7707 | 335.7562 | 3
199 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-BALA-BALA-COED TALOG OUTLET-COED TALOG OUTLET NEW DMA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 3.6343 | 2.2134 | 609.0355 | 4
200 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-BALA-BALA-RHYD UCHAF OUTLET-LLWYN IOLYN OUTLET NEW DMA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 5.1114 | 5.9763 | 1169.2081 | 5
201 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-CLWYD_COASTAL-ABERGELE__RHYL_GLASCOED-RHUALLT TO BODFARI-0702TREMEIRCHION/BODFARI (R70) | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 5.1457 | 2.4348 | 473.1679 | 3
202 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-CLWYD_COASTAL-ABERGELE__RHYL_GLASCOED-ST ASAPH 10 GAP | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 17.3176 | 2.8775 | 166.1578 | 2
203 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 18.1773 | 6.8616 | 377.4826 | 3
204 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-BETWS-Y-COED-BETWS Y COED / DOLWYDDELAN VILLAGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 1.8476 | 1.7707 | 958.3924 | 4
205 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-BRYNIAU (CONWY)-BRYNIAU RES OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 10.2625 | 3.5415 | 345.091 | 3
206 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-CERRIG-RHYDLYDAN PENTREFOELAS SRV O/L | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 4.5385 | 1.5494 | 341.3877 | 3
207 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT & GORSWEN MINOR-LLANDDOGED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 0.87424 | 3.7628 | 4304.1014 | 5
208 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT AND GORSWEN GAP-BODRACH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 4.6094 | 11.2885 | 2448.9891 | 5
209 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT AND GORSWEN GAP-MAENAN INLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 3.6985 | 3.3201 | 897.7116 | 4
210 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT VALLEY GAP-EGLWYSBACH TALYCAFN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 2.4545 | 1.5494 | 631.258 | 4
211 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT VALLEY GAP-MAENAN RISING | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 0.81406 | 3.0988 | 3806.5874 | 5
212 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT VALLEY TRUNK-AREA FED BY S/SUPPLY 3SC20M18 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 1.0697 | 4.4269 | 4138.5613 | 5
213 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-LLANFAIRFECHAN-LLANFAIRFECHAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 5.0201 | 4.2055 | 837.7269 | 4
214 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-LLYN CONWY TRUNK-PENMACHNO/LLYN CONWY SILOAM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 3.1168 | 1.5494 | 497.1085 | 3
215 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-PEN TO LLANFAIRFECHAN TRUNK-AREA FED BY S/SUPPLY 30C30A07 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 0.42211 | 1.9921 | 4719.3881 | 5
216 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-LLEYNHARLECH-BANGOR__CAERNARFON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 2.3254 | 1.7707 | 761.4652 | 4
217 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 12.6457 | 1.9921 | 157.5308 | 2
218 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-COED Y FRON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 6.5822 | 1.7707 | 269.0214 | 3
219 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-CWMYSTRADLLYN GAP-CENIN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 1.6539 | 3.5415 | 2141.2289 | 5
220 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-PENRHYNDEUDRAETH-PENRHYD LLANFROTHEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 0.23856 | 2.4348 | 10205.9932 | 5
221 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 13.472 | 3.9842 | 295.7381 | 3
222 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-PENTIR BRYNREFAIL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 4.2656 | 1.7707 | 415.1185 | 3
223 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-WAUNFAWR-WAUNFAWR NEW | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 0.36525 | 3.0988 | 8484.0953 | 5
224 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 10.2107 | 1.7707 | 173.4199 | 2
225 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-HOLLAND ARMS 9INCH-LLYS LEW TO LLANDDANIEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 1.6983 | 2.4348 | 1433.6795 | 5
226 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-SOUTH_ANGLESEY_CWELLYN__MYNYDD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 4.5919 | 1.7707 | 385.6267 | 3
227 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-SOUTH_ANGLESEY_CWELLYN__MYNYDD-CADNANT BEAUMARIS-LLANDEGFAN BOOSTER | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 2.0143 | 1.9921 | 988.9845 | 4
228 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-SOUTH_MEIRIONNYDD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 4.8665 | 2.8775 | 591.2806 | 4
229 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-SOUTH_MEIRIONNYDD-DINAS_MAWDDWY-DINAS MAWDDWY-MALLWYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 2.7764 | 1.7707 | 637.7829 | 4
230 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-SOUTH_MEIRIONNYDD-DOLGELLAU_PEN_Y_CEFN-DOLGELLAU | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 1.6716 | 2.2134 | 1324.0987 | 5
231 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-SOUTH_MEIRIONNYDD-DOLGELLAU_PEN_Y_CEFN-FAIRBOURNE-FAIRBOURNE FRIOG | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 3.8366 | 6.1976 | 1615.3768 | 5
232 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-SOUTH_MEIRIONNYDD-DOLGELLAU_PEN_Y_CEFN-PENYCEFN GAP-BRITHDIR VILLAGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 0.73185 | 1.9921 | 2721.9719 | 5
233 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-SOUTH_MEIRIONNYDD-DOLGELLAU_PEN_Y_CEFN-PENYCEFN GAP-PENCEFN ROAD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 0.41137 | 1.5494 | 3766.4094 | 5
234 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-SOUTH_MEIRIONNYDD-DOLGELLAU_PEN_Y_CEFN-PENYCEFN GAP-PENMAENPOOL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 0.54572 | 4.2055 | 7706.3579 | 5
235 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-SOUTH_MEIRIONNYDD-PENNAL__CORRIS_SEVERN_TRENT-CORRIS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 7.3288 | 3.3201 | 453.0237 | 3
236 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-SOUTH_MEIRIONNYDD-PENNAL__CORRIS_SEVERN_TRENT-CORRIS TALGARTH TRUNK-PLASTALGARTH RES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 0.8293 | 1.9921 | 2402.1206 | 5
237 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 15.2255 | 1.7707 | 116.3012 | 1
238 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-CEMENT_MORTAR-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 5.0757 | 1.9921 | 392.4747 | 3
239 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 15.4357 | 10.1818 | 659.6248 | 4
240 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-BEULAU TO ABERBANC-BLAENGWENLLAN CROSS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 6.9358 | 3.3201 | 478.6972 | 3
241 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-EGLWYSWRW-BRYNBERIAN WD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 2.1834 | 5.3122 | 2432.9572 | 5
242 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-FFYNNON LLAWDDOG-BEULAH TO CWMCOU | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 1.0176 | 2.4348 | 2392.7441 | 5
243 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-HAFOD LLECHRYD-LECHRYD VILLIAGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 1.9164 | 4.6482 | 2425.5116 | 5
244 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-MYNYDD CROGWY TO EGLWYSWRW AND CRYMYCH-POST GWYN BONCATH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 3.7736 | 2.8775 | 762.5192 | 4
245 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-MYNYDD CROGWY TO EGLWYSWRW AND CRYMYCH-POSTGWYN CRYMYCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 0.88567 | 3.0988 | 3498.8277 | 5
246 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-MYNYDD CROGWY TO EGLWYSWRW AND CRYMYCH-STAR PUMPS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 4.7385 | 5.7549 | 1214.499 | 5
247 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-NEWQUAY-SYNOD INN 4 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 2.377 | 5.5336 | 2327.9167 | 5
248 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-PENTREGAT CROSS CONNECTION-BRYNHOFFNANT RHYDLEWIS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 4.8751 | 1.5494 | 317.8212 | 3
249 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-RHOSHILL TO CROSSROADS-PENYBRYN TO CARDIGAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 1.7856 | 5.3122 | 2975.1104 | 5
250 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-RHOSHILL TO CROSSROADS-PENYBRYN TO CILGERRAN WD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 0.96657 | 3.0988 | 3205.9612 | 5
251 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-RHOSYMRYSON TO PENRHYWLLAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 5.4299 | 2.4348 | 448.4022 | 3
252 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-RHOSYMRYSON TO PENRHYWLLAN-HOREB TO FFOSTRASOL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 2.015 | 1.9921 | 988.6146 | 4
253 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SARNAU CROSS CONNECTION-BEULAH SCHEME | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 4.563 | 3.3201 | 727.6227 | 4
254 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SARNAU CROSS CONNECTION-GOGERDDAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 2.5399 | 3.5415 | 1394.367 | 5
255 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SYNOD INN LLANARTH-LLANARTH TO ABERAERON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 1.8191 | 1.5494 | 851.7596 | 4
256 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SYNOD INN SR TO RHOSYMRYSON SR-CROESGWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 1.2196 | 1.5494 | 1270.3725 | 5
257 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SYNOD INN SR TO RHOSYMRYSON SR-GRESFFORDD MOUNT BRANCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 2.4366 | 1.9921 | 817.5819 | 4
258 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 5.5226 | 3.5415 | 641.2737 | 4
259 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-DERI GOCH PS TO RHOSYMRYSON SR-CAPEL Y GROES TO LLANWNEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 1.0864 | 1.5494 | 1426.2433 | 5
260 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-PONTRHYDFENDIGAID-PONTRHYDFENDIGAID NORTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 0.86401 | 1.9921 | 2305.6398 | 5
261 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 7.3259 | 1.9921 | 271.9222 | 3
262 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 22.0138 | 5.9763 | 271.4775 | 3
263 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-BOLTON_HILL-QUARRY LINE-QUARRY LINE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 1.1318 | 1.9921 | 1760.0464 | 5
264 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-BOLTON_HILL-TESCO SOUTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 2.1042 | 1.7707 | 841.5165 | 4
265 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-BOLTON_HILL-TTM OFF PENT PUMPS-DEVON DRIVE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 2.0497 | 2.2134 | 1079.892 | 5
266 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-PENDINE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 1.0571 | 1.5494 | 1465.7602 | 5
267 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-PENDINE-BRANDY HILL TO ST. CLEARS-PWLL TRAPP | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 0.93087 | 3.3201 | 3566.6917 | 5
268 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-PENDINE-BRANDY HILL TO ST. CLEARS-THE SMITHY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 1.4686 | 5.7549 | 3918.6108 | 5
269 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-PRESELI_SUPPLY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 7.6815 | 1.5494 | 201.706 | 2
270 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-PRESELI_SUPPLY-LETTERSTON-LLANGLOFFAN CROSS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 2.4834 | 3.7628 | 1515.2143 | 5
271 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-PRESELI_SUPPLY-PENYGARN TO HOTWELLS-PENYGARN/AMBLESTON 3 INCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 1.3525 | 1.9921 | 1472.9285 | 5
272 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-PRESELI_SUPPLY-PRESELI USL OUTLETS-WISTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 4.7299 | 5.3122 | 1123.1114 | 5
273 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-PRESELI_SUPPLY-TENBY MAIN-PICTON/RHOS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 4.3868 | 3.3201 | 756.8435 | 4
274 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 4.6609 | 1.9921 | 427.4072 | 3
275 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-BRYNGWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 4.401 | 3.9842 | 905.2943 | 4
276 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-BRYNGWYN-SALEM SR OUTLET-SALEM LLANFYNYDD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 1.0648 | 6.4189 | 6028.1478 | 5
277 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-BRYNGWYN-SALEM SR OUTLET-SALEM VILLAGE METER | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 3.3562 | 11.2885 | 3363.5009 | 5
278 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-BRYNGWYN-TRAPP BULK EXPORT-CARMARTHEN RD. LLANDEILO RD. | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 0.25877 | 3.0988 | 11975.2809 | 5
279 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-BRYNGWYN-TRAPP BULK EXPORT-PENYBANK/NANTGARDEIG 6 INCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 0.5771 | 2.8775 | 4986.0489 | 5
280 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-CAERAU__YSTRADFELLTE-RESOLVEN SR OUTLET-GLYN CASTLE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 0.48646 | 2.6561 | 5460.0524 | 5
281 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 2.7111 | 2.2134 | 816.4427 | 4
282 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-CEFN BRYN HOUSE-CEFN BRYN HOUSE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 0.65943 | 2.2134 | 3356.5986 | 5
283 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-MID_-_SOUTH_CEREDIGION-LLECHRYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 9.1075 | 3.0988 | 340.2485 | 3
284 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-MID_-_SOUTH_CEREDIGION-LLECHRYD-EGLWYSWRW-POST GWYN - EGLWYSWRW | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 4.4953 | 4.2055 | 935.5289 | 4
285 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SYNOD INN LLANARTH-LLANARTH TO ABERAERON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 0.80227 | 3.9842 | 4966.1365 | 5
286 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SYNOD INN LLANARTH-LLANARTH VILLAGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 0.34019 | 2.2134 | 6506.4868 | 5
287 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-MID_-_SOUTH_CEREDIGION-LLECHRYD-WAUNLLWYD TO GORLLWYN -CAPEL IWAN TO CENARTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 1.3745 | 2.4348 | 1771.3974 | 5
288 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 7.2639 | 3.0988 | 426.6007 | 3
289 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-DERI GOCH PS TO RHOSYMRYSON SR-FFYNON RHYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 5.5141 | 2.4348 | 441.5523 | 3
290 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 19.8948 | 3.5415 | 178.0107 | 2
291 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-PEMBROKESHIRE-BOLTON_HILL-ROSEPOOL-FOXHILL RES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 0.78737 | 1.5494 | 1967.8161 | 5
292 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 13.0866 | 1.5494 | 118.3955 | 1
293 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-BRYNGWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 7.2026 | 2.2134 | 307.3079 | 3
294 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-BRYNGWYN-BRYNCOCH - PENTWYN-FOLLAND ROAD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 2.488 | 1.5494 | 622.7401 | 4
295 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 8.1666 | 2.6561 | 325.2404 | 3
296 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 5.2894 | 2.4348 | 460.3154 | 3
297 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE-CLASE SR OUTLET TO GWYROSEDD-LLANGYFELACH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 0.52356 | 1.7707 | 3382.126 | 5
298 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(160,320]-MID_-_SOUTH_CEREDIGION | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (160,320] | 12.3368 | 1.5494 | 125.5922 | 2
299 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(160,320]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SYNOD INN SR TO RHOSYMRYSON SR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (160,320] | 6.4782 | 2.4348 | 375.8384 | 3
300 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(160,320]-PEMBROKESHIRE-BOLTON_HILL-ORIELTON TO WOGASTON-ORIELTON WOGASTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (160,320] | 3.0463 | 8.8537 | 2906.3447 | 5
301 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(160,320]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (160,320] | 24.7813 | 3.7628 | 151.8413 | 2
302 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 49.4402 | 9.7391 | 196.9872 | 2
303 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-BEULAU TO ABERBANC-BLAENGWENLLAN CROSS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 4.4493 | 1.5494 | 348.2335 | 3
304 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-CARDIGAN SR OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 2.2792 | 1.9921 | 874.0322 | 4
305 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-EGLWYSWRW-BRYNBERIAN WD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 6.6829 | 4.6482 | 695.5389 | 4
306 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-GORLLWYN HERMON AND TANGLWYST-GORLLWYN TO HERMON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 4.6167 | 2.6561 | 575.33 | 4
307 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-GORLLWYN RHOS TREALAU-GORLLWYN TO RHOS/TREALAU | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 2.6571 | 2.4348 | 916.31 | 4
308 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-GORLLWYN RHOS TREALAU-TREALAU RES OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 8.8023 | 3.3201 | 377.1896 | 3
309 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-HAFOD LLECHRYD-LLANDYGWYDD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 4.1336 | 3.3201 | 803.2068 | 4
310 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-MYNYDD CROGWY TO EGLWYSWRW AND CRYMYCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 7.1176 | 1.9921 | 279.8831 | 3
311 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-MYNYDD CROGWY TO EGLWYSWRW AND CRYMYCH-WAUNYDD TEGRYN WD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 5.8435 | 3.5415 | 606.0506 | 4
312 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-NEWQUAY-SYNOD INN TO NEW QUAY 6 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 2.6072 | 2.6561 | 1018.7787 | 5
313 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-RHOSHILL TO CROSSROADS-RHOSHILL CROSSROADS WD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 3.3337 | 1.5494 | 464.7746 | 3
314 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-RHOSYMRYSON TO PENRHYWLLAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 7.6639 | 1.5494 | 202.1675 | 2
315 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-RHOSYMRYSON TO PENRHYWLLAN-HOREB BANGOR TEIFI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 4.1171 | 1.7707 | 430.0925 | 3
316 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-RHOSYMRYSON TO PENRHYWLLAN-HOREB TO FFOSTRASOL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 7.6949 | 1.5494 | 201.3538 | 2
317 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-RHOSYMRYSON TO PENRHYWLLAN-PENRHIWLLAN SCHEME | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 1.2826 | 3.0988 | 2416.1152 | 5
318 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SARNAU CROSS CONNECTION-BEULAH SCHEME | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 5.5356 | 8.411 | 1519.4514 | 5
319 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SYNOD INN LLANARTH-LLANARTH TO ABERAERON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 2.248 | 1.7707 | 787.6896 | 4
320 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SYNOD INN SR TO RHOSYMRYSON SR-CROESGWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 13.0218 | 6.4189 | 492.9369 | 3
321 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SYNOD INN SR TO RHOSYMRYSON SR-GRESFFORDD MOUNT BRANCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 4.6187 | 4.2055 | 910.5335 | 4
322 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SYNOD INN SR TO RHOSYMRYSON SR-TALGERREG PISGAH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 1.333 | 1.7707 | 1328.3794 | 5
323 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-WAUNLLWYD TO GORLLWYN -CAPEL IWAN TO CENARTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 18.6134 | 5.7549 | 309.1815 | 3
324 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 20.8369 | 7.5257 | 361.1705 | 3
325 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-BETHANIA TO CROSS INN-CROSSINN TO LLANON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 9.2424 | 6.8616 | 742.4058 | 4
326 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-BETHANIA TO CROSS INN-CROSSINN TO LLANRHYSTUD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 5.3651 | 3.7628 | 701.3477 | 4
327 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-BETTWS LLANGYBI AND LLANDDEWI BREFI-LANGYBI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 1.7786 | 1.7707 | 995.5806 | 4
328 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-DERI GOCH PS TO RHOSYMRYSON SR-CAPEL Y GROES TO LLANWNEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 6.3604 | 4.2055 | 661.2062 | 4
329 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-DERI GOCH PS TO RHOSYMRYSON SR-CWRTNEWYDD CWRT FARM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 4.095 | 2.2134 | 540.5169 | 4
330 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-DERI GOCH PS TO RHOSYMRYSON SR-CWRTNEWYDD QUARRY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 7.0326 | 3.9842 | 566.5254 | 4
331 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-DERIGOCH TO ABERAERON-DERI GOCH TO ABERAERON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 2.3651 | 2.4348 | 1029.4778 | 5
332 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-MAESTIR TO BRYNGARREG-BRYNCARREG RES OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 0.37557 | 1.9921 | 5304.2001 | 5
333 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-MAESTIR TO BRYNGARREG-MAESTIR TO BRYNGARREG | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 4.9561 | 4.8695 | 982.5265 | 4
334 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-PENWCH SERVICE RES OUTLET-MAESBEIDIOG TO LLANGWYRYFON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 0.59785 | 2.2134 | 3702.2863 | 5
335 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-PENWCH SERVICE RES OUTLET-PENUWCH TO BWLCHLLAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 0.43483 | 1.5494 | 3563.1939 | 5
336 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-PONTRHYDFENDIGAID-PONTRHYDFENDIGAID LLANAFAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 5.0669 | 2.4348 | 480.5282 | 3
337 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-TREGARON TOWN-LLANIO ROAD TO LLANGEITHO | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 2.5404 | 2.6561 | 1045.5514 | 5
338 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-NORTH_CEREDIGION-ABERYSTWYTH_BONTGOCH__LOVESGROVE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 4.8806 | 1.7707 | 362.8129 | 3
339 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 21.2153 | 4.2055 | 198.2298 | 2
340 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH-FRONGOCH SR OUT-FRONGOCH TO CLARACH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 2.6207 | 1.5494 | 591.2144 | 4
341 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH-MAESNEWYDD TO TRE’RDDOL -MAESNEWYDD TO GLANDYFI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 4.06 | 4.4269 | 1090.3682 | 5
342 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 60.8503 | 8.411 | 138.2248 | 2
343 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL-ADMIRALTY SITE-ADMIRALTY SITE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 3.8853 | 2.6561 | 683.6243 | 4
344 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL-TEMPLETON TO TAVERNSPITE-LLANTEG OFF T/SPITE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 0.524 | 2.2134 | 4224.0656 | 5
345 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PRESELI_SUPPLY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 21.2774 | 1.5494 | 72.8189 | 1
346 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PRESELI_SUPPLY-PENYGARN TO HOTWELLS-PENYGARN/AMBLESTON 3 INCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 5.5288 | 3.7628 | 680.5855 | 4
347 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PRESELI_SUPPLY-PRESELI DOLWEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 6.2263 | 1.5494 | 248.8462 | 2
348 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PRESELI_SUPPLY-PRESELI USL OUTLETS-WISTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 11.9922 | 3.9842 | 332.2289 | 3
349 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 16.4508 | 1.9921 | 121.0932 | 1
350 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 14.2112 | 6.8616 | 482.8322 | 3
351 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-BETTWS-BUTCHERS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 1.5358 | 2.2134 | 1441.1839 | 5
352 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-BETTWS-SCOTCH PINES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 0.63905 | 1.5494 | 2424.539 | 5
353 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-CARMEL AND PENTREGWENLAIS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 5.2919 | 1.9921 | 376.4405 | 3
354 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-MAESTWYNOG-CYNGHORDY OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 10.3974 | 20.8062 | 2001.1007 | 5
355 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-MAESTWYNOG-PANTYBRYN CILYCWM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 0.8953 | 3.3201 | 3708.3945 | 5
356 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-SALEM SR OUTLET-SALEM LLANFYNYDD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 9.9712 | 4.8695 | 488.3614 | 3
357 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-SALEM SR OUTLET-SALEM VILLAGE METER | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 27.0711 | 18.1501 | 670.46 | 4
358 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-TRAPP BULK EXPORT-CWM ISAF TO BETHLEHEM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 4.7513 | 3.3201 | 698.7927 | 4
359 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-TRAPP BULK EXPORT-PENYBANC RHOSMAEN LLANDILO | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 5.3818 | 2.8775 | 534.6643 | 4
360 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-TRAPP BULK EXPORT-PENYBANK/NANTGARDEIG 6 INCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 5.7406 | 1.7707 | 308.4593 | 3
361 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-TRAPP BULK EXPORT-TRAPP 4 INCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 2.3534 | 2.6561 | 1128.6139 | 5
362 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-TWYNLLANAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 15.1152 | 4.2055 | 278.2308 | 3
363 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-TWYNLLANAN-MOUNTPLEASANT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 1.7758 | 2.6561 | 1495.7223 | 5
364 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAPEL_DEWI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 3.5917 | 3.3201 | 924.3808 | 4
365 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAPEL_DEWI-FOEL SR TO RHYDARGAEAU-PENIEL BRONWYDD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 2.1343 | 1.5494 | 725.9432 | 4
366 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CRAY__CLYDACH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 6.3517 | 2.6561 | 418.174 | 3
367 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CRAY__CLYDACH-GURNOS CROSS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 1.9484 | 2.2134 | 1136.037 | 5
368 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-LLANELLI_FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 5.2692 | 1.5494 | 294.049 | 3
369 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 19.6374 | 5.3122 | 270.5157 | 3
370 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-CEFN BRYN HOUSE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 6.2703 | 2.4348 | 388.2996 | 3
371 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-CEFN BRYN HOUSE-BURRY GREEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 7.3366 | 1.5494 | 211.1885 | 2
372 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-CEFN BRYN HOUSE-KENNEXESTONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 2.2098 | 1.7707 | 801.3168 | 4
373 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-CEFN BRYN HOUSE-LLANGENNITH WD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 4.6615 | 1.5494 | 332.3841 | 3
374 | DIAM_LT_320-AC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKEWEN__LLANDARCY_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 8.1282 | 1.5494 | 190.6199 | 2
375 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | [6 empty] | 20.7141 | 1.5494 | 74.7994 | 1
376 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 4.3762 | 1.5494 | 354.0516 | 3
377 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(120,160]-PONTSTICILL_LOW_LEVEL-CAERPHILLY-MORNINGTON MEADOWS-MORNINGTON MEADOW | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (120,160] | 0.52768 | 1.7707 | 3355.7317 | 5
378 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (120,160] | 3.9888 | 1.5494 | 388.4339 | 3
379 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 11.5865 | 2.4348 | 210.1378 | 2
380 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_EAST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 5.9495 | 1.5494 | 260.4244 | 3
381 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-EASTERN-NONE-(0,70]-WHITBOURNE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (0,70] | 2.6991 | 1.5494 | 574.0352 | 4
382 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 7.6225 | 2.4348 | 319.4191 | 3
383 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-EASTERN-NONE-(70,120]-WHITBOURNE-WHITBOURNE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 11.038 | 2.2134 | 200.5272 | 2
384 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1941_1960 | B12_1960 |  | <=320mm | (0,70] | 6.4393 | 1.7707 | 274.9911 | 3
385 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(0,70]-ALWEN_/_DEE-DENBIGH_ALWEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (0,70] | 2.013 | 1.9921 | 989.6024 | 4
386 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(0,70]-ALWEN_/_DEE-DENBIGH_ALWEN-LLANFWROG-1511 LLANFWROG(G50) | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (0,70] | 3.1549 | 2.6561 | 841.8891 | 4
387 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(0,70]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (0,70] | 2.8846 | 2.4348 | 844.0705 | 4
388 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(0,70]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-CERRIG-POINT D TO CERRIG | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (0,70] | 0.75421 | 5.7549 | 7630.3853 | 5
389 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(0,70]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT & GORSWEN MINOR-LLANDDOGED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (0,70] | 3.3292 | 3.0988 | 930.8051 | 4
390 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (0,70] | 2.1655 | 3.5415 | 1635.3805 | 5
391 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-LLANNOR SAETHON TRUNK-AREA FED BY S/SUPPLY 3A401608 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (0,70] | 1.2388 | 2.4348 | 1965.452 | 5
392 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-MYNYTHO WILLIS-SAETHON BACH MYNYTHO PUMPED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (0,70] | 0.67435 | 1.9921 | 2954.0812 | 5
393 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-SYCHNANT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (0,70] | 1.6357 | 1.5494 | 947.2408 | 4
394 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(120,160]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (120,160] | 10.7619 | 3.3201 | 308.509 | 3
395 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 11.9747 | 2.8775 | 240.2944 | 2
396 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-ALWEN TO BWLCH TRUNK-CRICOR SUPPLY FROM ALWEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 2.4038 | 1.5494 | 644.5659 | 4
397 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-MEIFOD-CYFFYLLIOG | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 4.389 | 2.4348 | 554.7392 | 4
398 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON-RHOSESMOR MOEL Y CREO-BABELL TO CAERWYS(RHOS) | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 6.889 | 1.5494 | 224.909 | 2
399 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 8.3517 | 4.6482 | 556.5549 | 4
400 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT & GORSWEN MINOR-LLANDDOGED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 2.0766 | 2.2134 | 1065.9039 | 5
401 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-LLYN CONWY TRUNK-AREA FED BY S/SUPPLY 3SC70B08 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 0.7372 | 1.9921 | 2702.2439 | 5
402 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 12.4928 | 3.5415 | 283.4831 | 3
403 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-CRICCIETH LLANYSTUMDWY-GAERDDU BACH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 2.7469 | 1.5494 | 564.0497 | 4
404 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-MAENLLWYD-MAENLLWYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 1.7608 | 1.5494 | 879.9496 | 4
405 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-SYCHNANT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 4.5657 | 1.5494 | 339.3557 | 3
406 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-SYCHNANT-MAEN HIR BRYNCROES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 5.5027 | 2.6561 | 482.6953 | 3
407 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 17.0554 | 2.4348 | 142.7566 | 2
408 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-BEULAU TO ABERBANC-BLAENGWENLLAN CROSS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (0,70] | 2.1062 | 1.7707 | 840.7483 | 4
409 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (0,70] | 19.435 | 2.8775 | 148.0556 | 2
410 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-BOLTON_HILL-BRAWDY TO FELINWYNT-BRAWDY FELINWYNT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (0,70] | 8.212 | 3.0988 | 377.3509 | 3
411 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-BOLTON_HILL-PLUMSTONE TO BRAWDY-DRUIDSTON CROSS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (0,70] | 3.9411 | 2.2134 | 561.6325 | 4
412 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-PRESELI_SUPPLY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (0,70] | 3.9705 | 1.7707 | 445.9715 | 3
413 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-PRESELI_SUPPLY-CROESFORDD OUTLET-CROESFORDD 4 INCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (0,70] | 1.0068 | 1.5494 | 1538.9112 | 5
414 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE-PRESELI_SUPPLY-HOTWELLS TO LETTERSTON-CO/OP LETTERSTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (0,70] | 5.4127 | 5.0909 | 940.5511 | 4
415 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(120,160]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (120,160] | 6.5979 | 1.5494 | 234.8326 | 2
416 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (120,160] | 4.4696 | 1.5494 | 346.6554 | 3
417 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(160,320] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1941_1960 | B12_1960 |  | <=320mm | (160,320] | 9.1414 | 1.5494 | 169.492 | 2
418 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 9.1606 | 3.5415 | 386.5991 | 3
419 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 35.1541 | 3.9842 | 113.3345 | 1
420 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL-PLUMSTONE TO BRAWDY-DRUIDSTON CROSS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 4.6737 | 2.2134 | 473.5946 | 3
421 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PRESELI_SUPPLY-CROESFORDD OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 6.3562 | 1.9921 | 313.4073 | 3
422 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PRESELI_SUPPLY-CROESFORDD OUTLET-BRYN DERI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 5.3659 | 1.5494 | 288.7468 | 3
423 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PRESELI_SUPPLY-HOTWELLS TO LETTERSTON-CO/OP LETTERSTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 2.9991 | 2.2134 | 738.0322 | 4
424 | DIAM_LT_320-AC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 5.5303 | 2.2134 | 400.2365 | 3
425 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | [6 empty] | 42.8351 | 2.4348 | 56.8406 | 1
426 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 5.9516 | 1.9921 | 334.7156 | 3
427 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-PENARTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 1.4053 | 1.7707 | 1260.0037 | 5
428 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(160,320] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1961_1980 | B12_1960 |  | <=320mm | (160,320] | 9.867 | 1.7707 | 179.4604 | 2
429 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-CYNON-PENDERYN__PONTSTICILL-RHIGOS VILLAGE 8IN & 10IN OUTLETS-RHIGOS VILLAGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 2.4999 | 2.4348 | 973.9494 | 4
430 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-VALE_OF_GLAM__RHONDDA_VALLEYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 6.6847 | 1.5494 | 231.7823 | 2
431 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 12.0951 | 1.7707 | 146.402 | 2
432 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF-PENTREBANE NORTH-PENTREBANE NORTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 0.2747 | 1.5494 | 5640.4063 | 5
433 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH__BARRY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 3.165 | 2.2134 | 699.3514 | 4
434 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 25.8013 | 1.9921 | 77.2087 | 1
435 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1961_1980 | B12_1960 |  | <=320mm | (0,70] | 8.6199 | 2.4348 | 282.4605 | 3
436 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 17.9495 | 3.9842 | 221.9661 | 2
437 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(120,160]-WHITBOURNE-WHITBOURNE-LEYSTERS 8INCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 3.1606 | 2.2134 | 700.3108 | 4
438 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(160,320]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM-PENHOW QUARRY TDMA-PENHOW QUARRY TO HIGHMOOR HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (160,320] | 3.8971 | 3.9842 | 1022.3418 | 5
439 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(160,320]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN-BETTWS EAST-BETTWS EAST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (160,320] | 1.7217 | 3.3201 | 1928.3665 | 5
440 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 31.9332 | 1.7707 | 55.4514 | 1
441 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-PILLETH-PILLETH_KNIGHTON__BLEDDFA-WHITTON BEGGARS BUSH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 5.6352 | 2.2134 | 392.7845 | 3
442 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-PILLETH-PILLETH_KNIGHTON__BLEDDFA-WHITTON BEGGARS BUSH-MAESTREYLOW TO NORTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 0.84929 | 1.7707 | 2084.9713 | 5
443 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 5.3294 | 2.4348 | 456.8574 | 3
444 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-CROSS ASH-THE BOOT NEWCASTLE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 0.28281 | 2.6561 | 9391.9137 | 5
445 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-WHITBOURNE-UPPER_SAPEY-LEYSTER SR 3" OUTLET GAP-THE FOX(SEVERN TRENT) | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 1.0203 | 3.0988 | 3037.1692 | 5
446 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-WHITBOURNE-WHITBOURNE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 21.9832 | 2.2134 | 100.6875 | 1
447 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-WHITBOURNE-WHITBOURNE-LEYSTERS 8INCH-POLE FARM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 5.1526 | 3.5415 | 687.3257 | 4
448 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-WHITBOURNE-WHITBOURNE-WARRENWOOD-HOLLY TREE METER | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 2.8672 | 3.3201 | 1157.98 | 5
449 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-CEMENT_MORTAR-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-BANGOR FROM BRYNIAU-PENRHOS ROAD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 0.8752 | 1.5494 | 1770.3374 | 5
450 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1961_1980 | B12_1960 |  | <=320mm | (0,70] | 3.8801 | 1.9921 | 513.4058 | 4
451 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(0,70]-ALWEN_/_DEE-DENBIGH_ALWEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (0,70] | 3.0928 | 1.7707 | 572.5432 | 4
452 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(0,70]-ALWEN_/_DEE-DENBIGH_ALWEN-BYLCHAU HIGH-1008 BWLCHOUTLET(LLANNEFYDD) ( | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (0,70] | 1.2837 | 3.5415 | 2758.8174 | 5
453 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(0,70]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (0,70] | 0.58756 | 1.7707 | 3013.7165 | 5
454 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (0,70] | 4.7184 | 1.9921 | 422.196 | 3
455 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-BEUDY MAWR-BEUDY MAWR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (0,70] | 1.1418 | 2.4348 | 2132.3727 | 5
456 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-GARNFADRYN-GARNFADRYN RES OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (0,70] | 1.695 | 1.9921 | 1175.2613 | 5
457 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-SAETHON GAP-CAPEL TYDDYN PUMPED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (0,70] | 1.8714 | 1.9921 | 1064.4819 | 5
458 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(0,70]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-RHOSGADFAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (0,70] | 0.17869 | 1.5494 | 8670.9028 | 5
459 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(0,70]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-WAENHIR-PENTIR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (0,70] | 0.20736 | 1.5494 | 7471.9384 | 5
460 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 17.8249 | 1.5494 | 86.9235 | 1
461 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(120,160]-ALWEN_/_DEE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 12.9304 | 2.2134 | 171.1796 | 2
462 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(120,160]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 6.105 | 1.9921 | 326.305 | 3
463 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(120,160]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-CERRIG-CERRIGYDRUDION SRV O/LET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 4.8866 | 1.9921 | 407.6643 | 3
464 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(120,160]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-BUTLINS-LLANGYBI - BODOWEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 2.8464 | 2.8775 | 1010.9265 | 5
465 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(120,160]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-DOLBENMAEN WEST TRUNK -AREA FED BY S/SUPPLY 3A401601 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 2.7145 | 1.5494 | 570.7843 | 4
466 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(120,160]-NORTH_ERYRI_/_YNYS_MON-EAST_ANGLESEY_CEFNI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 5.6395 | 2.2134 | 392.4838 | 3
467 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(120,160]-NORTH_ERYRI_/_YNYS_MON-EAST_ANGLESEY_CEFNI-TREFOR BLAS LLANDDONA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 7.7808 | 1.9921 | 256.0257 | 3
468 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(120,160]-SOUTH_MEIRIONNYDD-DOLGELLAU_PEN_Y_CEFN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 2.4835 | 1.5494 | 623.8862 | 4
469 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(160,320]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-CERRIG-POINT D TO CERRIG | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (160,320] | 3.1411 | 2.8775 | 916.0781 | 4
470 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(160,320]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-LLYN CONWY TRUNK-AREA FED BY S/SUPPLY 3SC70B08 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (160,320] | 9.4852 | 6.4189 | 676.7333 | 4
471 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 26.1909 | 2.8775 | 109.8646 | 1
472 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-CARROG-TY CERRIG 6 INCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 4.2704 | 1.9921 | 466.484 | 3
473 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 15.11 | 3.9842 | 263.6772 | 3
474 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 10.3059 | 5.5336 | 536.9343 | 4
475 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-CERRIG | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 5.5255 | 3.0988 | 560.8154 | 4
476 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-TREFRIW-TREFRIW SERVICE RES. O/LET. | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 0.17521 | 1.5494 | 8843.0359 | 5
477 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 1.4579 | 1.5494 | 1062.7862 | 5
478 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 12.4874 | 3.9842 | 319.0565 | 3
479 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-COED Y FRON-BODWI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 2.3042 | 1.9921 | 864.5273 | 4
480 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-LLANAELHAEARN AND TRALLWYN-TRALLWYN RES OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 2.5272 | 1.7707 | 700.6679 | 4
481 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-MAENLLWYD-MAENLLWYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 4.3518 | 4.4269 | 1017.2558 | 5
482 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-MOEL Y PENMAEN-MOEL PENMAEN RES OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 2.7443 | 1.7707 | 645.2391 | 4
483 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-PENMORFA-PENMORFA RES OUTLET-PRENTEG | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 3.8275 | 1.5494 | 404.8083 | 3
484 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-PENRHYNDEUDRAETH-PENRHYD LLANFROTHEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 0.23962 | 1.7707 | 7389.8561 | 5
485 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-SYCHNANT-MAEN HIR BRYNCROES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 2.0864 | 2.8775 | 1379.1286 | 5
486 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-SYCHNANT-RHOSHIRWAEN HALL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 10.9472 | 3.3201 | 303.2879 | 3
487 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-SYCHNANT-RHYDLIOS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 7.2904 | 1.5494 | 212.5265 | 2
488 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 16.2236 | 2.8775 | 177.3623 | 2
489 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 9.4603 | 2.4348 | 257.3668 | 3
490 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-Y FELINHELI-BUSH RES Y FELINHELI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 1.1638 | 2.2134 | 1901.9409 | 5
491 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-BRYN GWENALLT-BRYNGWENALLT TO LLANDDEUSANT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 1.8271 | 2.2134 | 1211.4455 | 5
492 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 31.4827 | 2.2134 | 70.3061 | 1
493 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1961_1980 | B12_1960 |  | <=320mm | (0,70] | 11.3475 | 3.9842 | 351.1061 | 3
494 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-LLANWNEN TO LLANLLWNI-LLANYBYTHER RES OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (0,70] | 0.39386 | 4.6482 | 11801.6539 | 5
495 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-PONTRHYDFENDIGAID-FFAIR RHOS YSBYTY YSTWYTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (0,70] | 1.9243 | 1.5494 | 805.1905 | 4
496 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-BRYNGWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (0,70] | 0.66632 | 1.9921 | 2989.6891 | 5
497 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-BRYNGWYN-BETTWS-MAESQUERRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (0,70] | 0.56229 | 4.8695 | 8660.1696 | 5
498 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-BRYNGWYN-TRAPP BULK EXPORT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (0,70] | 1.6498 | 2.4348 | 1475.7913 | 5
499 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-BRYNGWYN-TWYNLLANAN-BRYNGLAS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (0,70] | 0.37396 | 1.9921 | 5327.022 | 5
500 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-MID_-_SOUTH_CEREDIGION-LLECHRYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 10.2277 | 1.7707 | 173.1314 | 2
501 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-MID_-_SOUTH_CEREDIGION-LLECHRYD-PENPARC SR TO CARDIGAN SR-PENPARC SOUTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 1.9395 | 3.9842 | 2054.1802 | 5
502 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH-CAPEL SEION LLANRHYSTUD-ABERMAD TO LLANRHYSTUD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 4.1751 | 1.7707 | 424.1171 | 3
503 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH-CAPEL SEION LLANRHYSTUD-CAPEL SEION/LLANRHYSTUD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 2.8445 | 1.5494 | 544.6934 | 4
504 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH-PENYCWM-PENYCWM CAPEL SEION RES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 2.6017 | 2.4348 | 935.828 | 4
505 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 16.4983 | 1.5494 | 93.9129 | 1
506 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-BRYNGWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 4.7251 | 1.7707 | 374.7536 | 3
507 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-DAFEN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 3.0644 | 1.5494 | 505.6124 | 4
508 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 15.6569 | 3.9842 | 254.467 | 3
509 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-DERLWYN-DERLWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 0.95812 | 1.5494 | 1617.1296 | 5
510 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SKEWEN__LLANDARCY_FELINDRE__CRAY-TYDRAW ROAD-MAES YR HAF | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 1.0702 | 1.9921 | 1861.4704 | 5
511 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 4.9067 | 3.5415 | 721.7655 | 4
512 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE-MYNYDD NEWYDD TO FFOREST FACH-IVORITES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 0.2168 | 1.5494 | 7146.8371 | 5
513 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(160,320]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY-SOUTHERNDOWN-OGMORE BY SEA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (160,320] | 0.96763 | 1.7707 | 1829.9774 | 5
514 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(160,320]-TYWI_C.U._AREA-BRYNGWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (160,320] | 1.1116 | 1.5494 | 1393.8638 | 5
515 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 6.1094 | 2.2134 | 362.2998 | 3
516 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-PONTRHYDFENDIGAID-FFAIR RHOS YSBYTY YSTWYTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 1.5759 | 2.8775 | 1825.8725 | 5
517 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 7.7967 | 1.7707 | 227.1137 | 2
518 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH-CAPEL SEION LLANFI AND TRAWSCOED-CAPEL SEION LLANFIHANGEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 9.4923 | 1.9921 | 209.8643 | 2
519 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 2.5565 | 1.5494 | 606.0696 | 4
520 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PENDINE-THREE LORDS OUTLET-THREE LORDS (BROADWAY/LAUGHARN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 0.32191 | 1.7707 | 5500.7108 | 5
521 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 11.7898 | 5.0909 | 431.8057 | 3
522 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 7.0228 | 2.8775 | 409.7318 | 3
523 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CRAY__CLYDACH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 10.9566 | 3.0988 | 282.825 | 3
524 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CRAY__CLYDACH-CLYDACH AREA ALT-YNYSTAWE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 1.4882 | 2.2134 | 1487.367 | 5
525 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 39.7727 | 5.5336 | 139.1298 | 2
526 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-NEWTON P.O.-CAMBRIDGE WD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 3.0906 | 1.7707 | 572.9489 | 4
527 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKEWEN__LLANDARCY_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 5.3162 | 3.0988 | 582.8925 | 4
528 | DIAM_LT_320-AC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 18.7665 | 3.5415 | 188.7128 | 2
529 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | [6 empty] | 36.2423 | 1.5494 | 42.7511 | 1
530 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 2.7935 | 1.7707 | 633.8844 | 4
531 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-VALE_OF_GLAM__RHONDDA_VALLEYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 6.6235 | 2.8775 | 434.4307 | 3
532 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-EASTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 16.8962 | 1.5494 | 91.7009 | 1
533 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(0,70]-TALYBONT-ABERGAVENNY__CWMTILLERY-PONTYPOOL TDMA-AREA FED BY SUB SUPPLY SYSTEM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B13_1970 |  | <=320mm | (0,70] | 0.91095 | 4.2055 | 4616.6183 | 5
534 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 8.4464 | 2.4348 | 288.2611 | 3
535 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1961_1980 | B13_1970 |  | <=320mm | (0,70] | 4.0392 | 3.0988 | 767.1819 | 4
536 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(0,70]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B13_1970 |  | <=320mm | (0,70] | 7.6249 | 4.6482 | 609.607 | 4
537 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B13_1970 |  | <=320mm | (0,70] | 2.2789 | 1.5494 | 679.9037 | 4
538 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(0,70]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B13_1970 |  | <=320mm | (0,70] | 1.8393 | 2.6561 | 1444.1064 | 5
539 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(0,70]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B13_1970 |  | <=320mm | (0,70] | 0.89996 | 1.7707 | 1967.5818 | 5
540 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(0,70]-SOUTH_MEIRIONNYDD-DOLGELLAU_PEN_Y_CEFN-PENYCEFN TRUNK-GANLLWYN RES INLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B13_1970 |  | <=320mm | (0,70] | 0.32803 | 1.5494 | 4723.2955 | 5
541 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 6.8078 | 2.2134 | 325.1314 | 3
542 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160]-ALWEN_/_DEE-DENBIGH_ALWEN-DENBIGH TRUNK-1402 LLANGWYFAN(G40) | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 1.8709 | 2.8775 | 1537.9938 | 5
543 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160]-ALWEN_/_DEE-FLINT__CONNAHS_QUAY_BRETTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 19.1169 | 3.7628 | 196.8329 | 2
544 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 47.8008 | 7.747 | 162.0684 | 2
545 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON-BUCKLEY LIVERPOOL ROAD-EWLOE/HAWARDEN. | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 3.3099 | 2.2134 | 668.7333 | 4
546 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON-HOLYWELL ST PHILOMENIA-ST.PHILOMENIAHOLYWELL. | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 0.59805 | 1.5494 | 2590.7349 | 5
547 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON-PEN Y BALL TO GWESPYR & AXTON TRUNK-AREA FED BY S/SUPPLY 3SF8100 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 7.328 | 1.7707 | 241.642 | 2
548 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON-WHITFORD SR TO MOSTYN DOCKS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 3.1987 | 1.5494 | 484.3825 | 3
549 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | AC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 8.7767 | 4.2055 | 479.1697 | 3
550 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-FLINT__CONNAHS_QUAY_BRETTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 25.9864 | 6.1976 | 238.4942 | 2
551 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 93.3489 | 15.494 | 165.9795 | 2
552 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON-BUCKLEY BROOKE STREET-BROOKEST.BUCKLEY. | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 3.0739 | 1.7707 | 576.0625 | 4
553 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON-BUCKLEY PRECINCT WAY-PRECINCT WAYBUCKLEY. | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 4.9969 | 1.9921 | 398.6644 | 3
554 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON-RHOSESMOR BERTH DDU | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | AC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 3.726 | 1.5494 | 415.8398 | 3
555 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 4.4817 | 2.2134 | 493.8789 | 3
556 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 5.6022 | 4.6482 | 829.7036 | 4
557 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 7.1095 | 4.6482 | 653.8019 | 4
558 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-FFYNNON WEN-GROESLON VILLAGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 0.81518 | 1.5494 | 1900.6879 | 5
559 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 16.2434 | 1.9921 | 122.6398 | 1
560 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B13_1970 |  | <=320mm | (0,70] | 0.18787 | 1.5494 | 8247.0154 | 5
561 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 19.1257 | 3.0988 | 162.0225 | 2
562 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | AC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 19.4519 | 3.9842 | 204.8216 | 2
563 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CRAY__CLYDACH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 8.9634 | 3.3201 | 370.4124 | 3
564 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 11.4182 | 2.6561 | 232.6202 | 2
565 | DIAM_LT_320-AC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE-DRUIDS STONE-DRUID'S STONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 0.41905 | 1.7707 | 4225.5891 | 5
566 | DIAM_LT_320-AC-<=320mm-B14_1980 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN | [6 empty] | 14.3958 | 1.5494 | 107.6283 | 1
567 | DIAM_LT_320-AC-<=320mm-B14_1980-1961_1980-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-HAFOD FELINWYNT-HAFOD FELINWYNT 5 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | AC | 1961_1980 | B14_1980 |  | <=320mm | (70,120] | 0.15081 | 2.2134 | 14677.0597 | 5
568 | DIAM_LT_320-AC-<=320mm-B14_1980-1981_2000-EASTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 1.7123 | 1.7707 | 1034.1276 | 5
569 | DIAM_LT_320-AC-<=320mm-B14_1980-1981_2000-NORTHERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 8.2412 | 1.9921 | 241.7238 | 2
570 | DIAM_LT_320-AC-<=320mm-B14_1980-1981_2000-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | AC | 1981_2000 | B14_1980 |  | <=320mm | (70,120] | 2.247 | 1.9921 | 886.5399 | 4
571 | DIAM_LT_320-ALKATHENE-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | ALKATHENE | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 1.628 | 1.7707 | 1087.691 | 5
572 | DIAM_LT_320-ALKATHENE-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(0,70]-PONTSTICILL_LOW_LEVEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | ALKATHENE | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 1.8519 | 1.7707 | 956.1997 | 4
573 | DIAM_LT_320-ALKATHENE-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | ALKATHENE | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 10.0147 | 2.2134 | 221.0175 | 2
574 | DIAM_LT_320-ALKATHENE-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(0,70]-BRECON_/_PORTIS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | ALKATHENE | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 2.3933 | 1.7707 | 739.8712 | 4
575 | DIAM_LT_320-ALKATHENE-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | ALKATHENE | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 8.5448 | 1.5494 | 181.3276 | 2
576 | DIAM_LT_320-ALKATHENE-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | ALKATHENE | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 5.5747 | 1.9921 | 357.343 | 3
577 | DIAM_LT_320-ALKATHENE-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-PEMBROKESHIRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | ALKATHENE | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 22.8675 | 2.4348 | 106.4728 | 1
578 | DIAM_LT_320-ALKATHENE-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | ALKATHENE | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 21.4541 | 2.4348 | 113.4874 | 1
579 | DIAM_LT_320-ALKATHENE-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-BRYNGWYN-LLANNON WEST-PONT MORLAIS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | ALKATHENE | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 2.6164 | 4.4269 | 1691.9859 | 5
580 | DIAM_LT_320-ALKATHENE-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-LLANELLI_FELINDRE-POLIN TO RHYDARGAEAU-NANTGAREDIG BRIDGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | ALKATHENE | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 1.4401 | 3.0988 | 2151.8061 | 5
581 | DIAM_LT_320-ALKATHENE-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA-LLANELLI_FELINDRE-REHOBOTH RED DMA-REHOBOTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | ALKATHENE | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 1.0196 | 2.4348 | 2388.067 | 5
582 | DIAM_LT_320-ALKATHENE-<=320mm-B12_1960-1941_1960 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | [6 empty] | 8.3767 | 1.5494 | 184.9645 | 2
583 | DIAM_LT_320-ALKATHENE-<=320mm-B12_1960-1941_1960-EASTERN-NONE-(0,70]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_SW__RISCA__ABERCARN-MICHAELSTONE TO MARSHFIELD SOUTH-MICHAELSTONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | ALKATHENE | 1941_1960 | B12_1960 |  | <=320mm | (0,70] | 0.43602 | 1.5494 | 3553.5344 | 5
584 | DIAM_LT_320-ALKATHENE-<=320mm-B12_1960-1961_1980 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | [6 empty] | 6.489 | 1.5494 | 238.7748 | 2
585 | DIAM_LT_320-ALKATHENE-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(0,70]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | ALKATHENE | 1961_1980 | B12_1960 |  | <=320mm | (0,70] | 2.5052 | 2.2134 | 883.5162 | 4
586 | DIAM_LT_320-ALKATHENE-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(0,70]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_EAST-BRYN CELYN-BRYN CELYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | ALKATHENE | 1961_1980 | B12_1960 |  | <=320mm | (0,70] | 0.03781 | 1.5494 | 40978.149 | 5
587 | DIAM_LT_320-ALKATHENE-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | ALKATHENE | 1961_1980 | B12_1960 |  | <=320mm | (0,70] | 8.6837 | 1.9921 | 229.4051 | 2
588 | DIAM_LT_320-ALKATHENE-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | ALKATHENE | 1961_1980 | B12_1960 |  | <=320mm | (0,70] | 10.611 | 2.4348 | 229.4578 | 2
589 | DIAM_LT_320-ALKATHENE-<=320mm-B13_1970-1961_1980 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | [6 empty] | 7.7481 | 2.2134 | 285.6744 | 3
590 | DIAM_LT_320-ALKATHENE-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | ALKATHENE | 1961_1980 | B13_1970 |  | <=320mm | (0,70] | 7.2912 | 1.5494 | 212.5025 | 2
591 | DIAM_LT_320-ALKATHENE-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(0,70]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-PORTHMADOG WEST-TYDDYN LLWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | ALKATHENE | 1961_1980 | B13_1970 |  | <=320mm | (0,70] | 0.25081 | 1.9921 | 7942.6177 | 5
592 | DIAM_LT_320-ALKATHENE-<=320mm-B14_1980 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN | [6 empty] | 8.712 | 2.4348 | 279.4731 | 3
593 | DIAM_LT_320-COPPER-<=320mm | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY | [6 empty] | 12.851 | 1.5494 | 120.5665 | 1
594 | DIAM_LT_320-FERROUS_1-<=320mm | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY | [6 empty] | 108.5588 | 7.3043 | 67.2844 | 1
595 | DIAM_LT_320-FERROUS_1-<=320mm-B01_1850-PRE_1880-NORTHERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 6.3191 | 1.9921 | 315.2474 | 3
596 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 50.5648 | 2.2134 | 43.7741 | 1
597 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-CEMENT_MORTAR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 6.471 | 1.5494 | 239.4368 | 2
598 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-EPOXY_RESIN-(120,160]-PEMBROKESHIRE-BOLTON_HILL-MOUNTAIN TREFFGARNE AND RUDBAXTON-MOUNTAIN WATER | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | PRE_1880 | B02_1860 |  | <=320mm | (120,160] | 7.503 | 1.5494 | 206.5044 | 2
599 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-EPOXY_RESIN-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | PRE_1880 | B02_1860 |  | <=320mm | (70,120] | 5.445 | 1.9921 | 365.8533 | 3
600 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | PRE_1880 | B02_1860 |  | <=320mm | (70,120] | 21.0209 | 3.3201 | 157.9451 | 2
601 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY-SOUTHERNDOWN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | PRE_1880 | B02_1860 |  | <=320mm | (70,120] | 5.823 | 1.5494 | 266.0823 | 3
602 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA-BRYNGWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | PRE_1880 | B02_1860 |  | <=320mm | (70,120] | 19.6227 | 1.7707 | 90.2395 | 1
603 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | PRE_1880 | B02_1860 |  | <=320mm | (0,70] | 4.4448 | 1.5494 | 348.5873 | 3
604 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | PRE_1880 | B02_1860 |  | <=320mm | (120,160] | 50.1718 | 4.2055 | 83.8222 | 1
605 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | PRE_1880 | B02_1860 |  | <=320mm | (120,160] | 3.9657 | 1.5494 | 390.6999 | 3
606 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(160,320] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | PRE_1880 | B02_1860 |  | <=320mm | (160,320] | 37.4145 | 1.9921 | 53.2436 | 1
607 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(160,320]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | PRE_1880 | B02_1860 |  | <=320mm | (160,320] | 9.7443 | 2.4348 | 249.8672 | 2
608 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | PRE_1880 | B02_1860 |  | <=320mm | (70,120] | 10.7059 | 2.2134 | 206.748 | 2
609 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-PENCOED__BRIDGEND_VALLEYS-BRIDGEND ROAD-LLANHARRY ROAD 7IN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | PRE_1880 | B02_1860 |  | <=320mm | (70,120] | 1.4002 | 1.5494 | 1106.5241 | 5
610 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | PRE_1880 | B02_1860 |  | <=320mm | (70,120] | 28.2314 | 3.0988 | 109.7641 | 1
611 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | PRE_1880 | B02_1860 |  | <=320mm | (70,120] | 4.7119 | 1.7707 | 375.8052 | 3
612 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-BETTWS-BUTCHERS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | PRE_1880 | B02_1860 |  | <=320mm | (70,120] | 1.021 | 1.7707 | 1734.2968 | 5
613 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAERAU__YSTRADFELLTE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | PRE_1880 | B02_1860 |  | <=320mm | (70,120] | 10.0027 | 3.0988 | 309.7961 | 3
614 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CRAY__CLYDACH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | PRE_1880 | B02_1860 |  | <=320mm | (70,120] | 6.0554 | 1.7707 | 292.4254 | 3
615 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-DAFEN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | PRE_1880 | B02_1860 |  | <=320mm | (70,120] | 5.9861 | 1.5494 | 258.831 | 3
616 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-LLANELLI_FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | PRE_1880 | B02_1860 |  | <=320mm | (70,120] | 14.3069 | 1.7707 | 123.7684 | 1
617 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-LLANELLI_FELINDRE-FURNACE ROAD TO KIDWELLY RED DMA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | PRE_1880 | B02_1860 |  | <=320mm | (70,120] | 4.058 | 1.9921 | 490.9022 | 3
618 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PENCOED__BRIDGEND_VALLEYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | PRE_1880 | B02_1860 |  | <=320mm | (70,120] | 23.1132 | 4.4269 | 191.5294 | 2
619 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PENCOED__BRIDGEND_VALLEYS-RED COW TO NANT ST EAST ALT-REVLON OAKWOOD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | PRE_1880 | B02_1860 |  | <=320mm | (70,120] | 0.55881 | 1.5494 | 2772.667 | 5
620 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PORT_TALBOT_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | PRE_1880 | B02_1860 |  | <=320mm | (70,120] | 14.2791 | 3.5415 | 248.0193 | 2
621 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-POLYURETHANE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 12.7871 | 1.9921 | 155.789 | 2
622 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-POLYURETHANE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | PRE_1880 | B02_1860 |  | <=320mm | (70,120] | 11.6155 | 2.4348 | 209.6137 | 2
623 | DIAM_LT_320-FERROUS_1-<=320mm-B02_1860-PRE_1880-WESTERN-POLYURETHANE-(70,120]-TYWI_C.U._AREA-BRYNGWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | PRE_1880 | B02_1860 |  | <=320mm | (70,120] | 8.263 | 2.6561 | 321.4453 | 3
624 | DIAM_LT_320-FERROUS_1-<=320mm-B03_1870-PRE_1880 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | [6 empty] | 17.6455 | 1.7707 | 100.3512 | 1
625 | DIAM_LT_320-FERROUS_1-<=320mm-B03_1870-PRE_1880-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 15.0976 | 1.9921 | 131.9473 | 2
626 | DIAM_LT_320-FERROUS_1-<=320mm-B04_1880 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN | [6 empty] | 13.0934 | 1.5494 | 118.3347 | 1
627 | DIAM_LT_320-FERROUS_1-<=320mm-B04_1880-1881_1900-CENTRAL-EPOXY_RESIN-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1881_1900 | B04_1880 |  | <=320mm | (70,120] | 1.6079 | 1.5494 | 963.6213 | 4
628 | DIAM_LT_320-FERROUS_1-<=320mm-B04_1880-1881_1900-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 13.7605 | 1.9921 | 144.7679 | 2
629 | DIAM_LT_320-FERROUS_1-<=320mm-B04_1880-1881_1900-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__CANTON__CATHAYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1881_1900 | B04_1880 |  | <=320mm | (70,120] | 2.6068 | 1.7707 | 679.2841 | 4
630 | DIAM_LT_320-FERROUS_1-<=320mm-B04_1880-1881_1900-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__RUMNEY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1881_1900 | B04_1880 |  | <=320mm | (70,120] | 10.3938 | 2.2134 | 212.956 | 2
631 | DIAM_LT_320-FERROUS_1-<=320mm-B04_1880-1881_1900-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1881_1900 | B04_1880 |  | <=320mm | (120,160] | 3.2653 | 1.5494 | 474.5042 | 3
632 | DIAM_LT_320-FERROUS_1-<=320mm-B04_1880-PRE_1880-NORTHERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 5.2029 | 2.2134 | 425.4228 | 3
633 | DIAM_LT_320-FERROUS_1-<=320mm-B04_1880-PRE_1880-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 9.8239 | 1.5494 | 157.717 | 2
634 | DIAM_LT_320-FERROUS_1-<=320mm-B04_1880-PRE_1880-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE-HAFOD-HAFOD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | PRE_1880 | B04_1880 |  | <=320mm | (70,120] | 2.3989 | 1.7707 | 738.1424 | 4
635 | DIAM_LT_320-FERROUS_1-<=320mm-B05_1890-1881_1900 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | [6 empty] | 33.7739 | 1.7707 | 52.4294 | 1
636 | DIAM_LT_320-FERROUS_1-<=320mm-B05_1890-1881_1900-CENTRAL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 28.6525 | 1.9921 | 69.5257 | 1
637 | DIAM_LT_320-FERROUS_1-<=320mm-B05_1890-1881_1900-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1881_1900 | B05_1890 |  | <=320mm | (120,160] | 9.6966 | 2.6561 | 273.9233 | 3
638 | DIAM_LT_320-FERROUS_1-<=320mm-B05_1890-1881_1900-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1881_1900 | B05_1890 |  | <=320mm | (70,120] | 10.4827 | 1.7707 | 168.9206 | 2
639 | DIAM_LT_320-FERROUS_1-<=320mm-B05_1890-1881_1900-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__RUMNEY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1881_1900 | B05_1890 |  | <=320mm | (70,120] | 9.1146 | 3.7628 | 412.8353 | 3
640 | DIAM_LT_320-FERROUS_1-<=320mm-B05_1890-1881_1900-CENTRAL-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1881_1900 | B05_1890 |  | <=320mm | (70,120] | 8.3356 | 1.7707 | 212.4305 | 2
641 | DIAM_LT_320-FERROUS_1-<=320mm-B05_1890-1881_1900-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1881_1900 | B05_1890 |  | <=320mm | (120,160] | 5.6537 | 2.2134 | 391.5028 | 3
642 | DIAM_LT_320-FERROUS_1-<=320mm-B05_1890-1881_1900-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1881_1900 | B05_1890 |  | <=320mm | (70,120] | 10.597 | 1.7707 | 167.0987 | 2
643 | DIAM_LT_320-FERROUS_1-<=320mm-B05_1890-1881_1900-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_WEST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1881_1900 | B05_1890 |  | <=320mm | (70,120] | 6.4704 | 2.4348 | 376.2919 | 3
644 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | [6 empty] | 16.0002 | 1.7707 | 110.67 | 1
645 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 19.1624 | 1.9921 | 103.958 | 1
646 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-CENTRAL-NONE-(70,120]-RHONDDA-MAERDY__PORTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1881_1900 | B06_1900 |  | <=320mm | (70,120] | 16.5057 | 6.1976 | 375.4824 | 3
647 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-CENTRAL-NONE-(70,120]-RHONDDA-MAERDY__PORTH-FURNACE ROAD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1881_1900 | B06_1900 |  | <=320mm | (70,120] | 4.9533 | 1.9921 | 402.1748 | 3
648 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1881_1900 | B06_1900 |  | <=320mm | (70,120] | 4.6454 | 1.7707 | 381.1827 | 3
649 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__CANTON__CATHAYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1881_1900 | B06_1900 |  | <=320mm | (70,120] | 4.4141 | 2.6561 | 601.7406 | 4
650 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-CENTRAL-POLYURETHANE-(70,120]-RHONDDA-VALE_OF_GLAM__RHONDDA_VALLEYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1881_1900 | B06_1900 |  | <=320mm | (70,120] | 7.4013 | 3.7628 | 508.4033 | 4
651 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-NORTHERN-CEMENT_MORTAR-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1881_1900 | B06_1900 |  | <=320mm | (70,120] | 10.8136 | 2.2134 | 204.6893 | 2
652 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-NORTHERN-CEMENT_MORTAR-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1881_1900 | B06_1900 |  | <=320mm | (70,120] | 10.1305 | 2.6561 | 262.191 | 3
653 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-NORTHERN-CEMENT_MORTAR-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-CAERNARFON SEGONTIWM-PRINCE OF WALES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1881_1900 | B06_1900 |  | <=320mm | (70,120] | 2.5731 | 1.9921 | 774.1837 | 4
654 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-NORTHERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 25.4922 | 2.2134 | 86.8275 | 1
655 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1881_1900 | B06_1900 |  | <=320mm | (70,120] | 6.4626 | 1.7707 | 274.0003 | 3
656 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 42.7242 | 4.8695 | 113.9761 | 1
657 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-CEMENT_MORTAR-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1881_1900 | B06_1900 |  | <=320mm | (120,160] | 2.5752 | 1.7707 | 687.6184 | 4
658 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-EPOXY_RESIN-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1881_1900 | B06_1900 |  | <=320mm | (70,120] | 6.1027 | 2.2134 | 362.6962 | 3
659 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-EPOXY_RESIN-(70,120]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1881_1900 | B06_1900 |  | <=320mm | (70,120] | 9.5703 | 1.7707 | 185.025 | 2
660 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1881_1900 | B06_1900 |  | <=320mm | (70,120] | 15.0681 | 2.6561 | 176.2739 | 2
661 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1881_1900 | B06_1900 |  | <=320mm | (120,160] | 21.1324 | 3.0988 | 146.6377 | 2
662 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-NONE-(160,320]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1881_1900 | B06_1900 |  | <=320mm | (160,320] | 10.3559 | 1.7707 | 170.9893 | 2
663 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1881_1900 | B06_1900 |  | <=320mm | (70,120] | 11.1292 | 1.9921 | 178.9968 | 2
664 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-NONE-(70,120]-NORTH_CEREDIGION-ABERYSTWYTH_BONTGOCH__LOVESGROVE-CHALYBEATE STREET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1881_1900 | B06_1900 |  | <=320mm | (70,120] | 3.0035 | 1.7707 | 589.5531 | 4
665 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL-TENBY 7 DMA-TENBY 7 WD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1881_1900 | B06_1900 |  | <=320mm | (70,120] | 1.6621 | 1.5494 | 932.2044 | 4
666 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1881_1900 | B06_1900 |  | <=320mm | (70,120] | 22.1184 | 2.8775 | 130.0931 | 2
667 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PENCOED__BRIDGEND_VALLEYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1881_1900 | B06_1900 |  | <=320mm | (70,120] | 14.7469 | 2.4348 | 165.104 | 2
668 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PORT_TALBOT_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1881_1900 | B06_1900 |  | <=320mm | (70,120] | 13.5455 | 2.8775 | 212.429 | 2
669 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-POLYURETHANE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1881_1900 | B06_1900 |  | <=320mm | (120,160] | 10.605 | 1.5494 | 146.1012 | 2
670 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-POLYURETHANE-(70,120]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1881_1900 | B06_1900 |  | <=320mm | (70,120] | 12.5667 | 3.0988 | 246.5882 | 2
671 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1881_1900-WESTERN-POLYURETHANE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-TWYNLLANAN-MOUNTPLEASANT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1881_1900 | B06_1900 |  | <=320mm | (70,120] | 2.7287 | 1.7707 | 648.923 | 4
672 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-CENTRAL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 12.5895 | 1.5494 | 123.0713 | 1
673 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 21.7692 | 1.9921 | 91.5094 | 1
674 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__RUMNEY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B06_1900 |  | <=320mm | (70,120] | 6.6308 | 2.4348 | 367.1917 | 3
675 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_WEST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B06_1900 |  | <=320mm | (120,160] | 4.859 | 1.5494 | 318.8725 | 3
676 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B06_1900 |  | <=320mm | (70,120] | 16.497 | 3.7628 | 228.0918 | 2
677 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_WEST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B06_1900 |  | <=320mm | (70,120] | 10.0796 | 3.5415 | 351.3519 | 3
678 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-NORTHERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 29.3309 | 1.5494 | 52.8248 | 1
679 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-NORTHERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 12.9114 | 2.4348 | 188.5755 | 2
680 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 25.6412 | 2.4348 | 94.9554 | 1
681 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-CEMENT_MORTAR-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B06_1900 |  | <=320mm | (70,120] | 11.8543 | 1.7707 | 149.375 | 2
682 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-EPOXY_RESIN-(120,160]-TYWI_C.U._AREA-CAPEL_DEWI-CARMARTHEN TOWN-CWMOERNANT - CARMS TOWN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B06_1900 |  | <=320mm | (120,160] | 0.59725 | 1.5494 | 2594.2108 | 5
683 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B06_1900 |  | <=320mm | (70,120] | 20.563 | 3.3201 | 161.4617 | 2
684 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA-BRYNGWYN-CARMEL TO LLANNON SR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1901_1920 | B06_1900 |  | <=320mm | (70,120] | 7.6275 | 1.5494 | 203.1342 | 2
685 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 26.229 | 2.2134 | 84.3886 | 1
686 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B06_1900 |  | <=320mm | (120,160] | 30.9835 | 3.0988 | 100.0146 | 1
687 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B06_1900 |  | <=320mm | (70,120] | 39.4897 | 5.0909 | 128.9168 | 2
688 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CRAY__CLYDACH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B06_1900 |  | <=320mm | (70,120] | 6.8058 | 1.5494 | 227.6603 | 2
689 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-LLANELLI_FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B06_1900 |  | <=320mm | (70,120] | 16.3754 | 3.0988 | 189.2347 | 2
690 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PENCOED__BRIDGEND_VALLEYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B06_1900 |  | <=320mm | (70,120] | 13.5477 | 3.3201 | 245.0709 | 2
691 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PENCOED__BRIDGEND_VALLEYS-OGMORE VALE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1901_1920 | B06_1900 |  | <=320mm | (70,120] | 5.3355 | 3.5415 | 663.7611 | 4
692 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE-WYCHTREE MORFYDD PENTREMALWED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1901_1920 | B06_1900 |  | <=320mm | (70,120] | 4.8712 | 1.5494 | 318.0762 | 3
693 | DIAM_LT_320-FERROUS_1-<=320mm-B06_1900-1901_1920-WESTERN-POLYURETHANE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B06_1900 |  | <=320mm | (70,120] | 20.1094 | 2.4348 | 121.0764 | 1
694 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-EPOXY_RESIN-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (120,160] | 12.6407 | 1.7707 | 140.0826 | 2
695 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-EPOXY_RESIN-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 5.3414 | 1.5494 | 290.0717 | 3
696 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-EPOXY_RESIN-(70,120]-PONTSTICILL_LOW_LEVEL-RHYMNEY__BARGOED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 13.053 | 3.0988 | 237.4019 | 2
697 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-EPOXY_RESIN-(70,120]-RHONDDA-TYNYWAUN-BAGLAN STREET TO DR THOMAS-ROCK DRIVE GELLI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 0.60898 | 1.5494 | 2544.2469 | 5
698 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-EPOXY_RESIN-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 13.3802 | 1.9921 | 148.883 | 2
699 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 34.1532 | 1.9921 | 58.3279 | 1
700 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (0,70] | 7.6785 | 1.5494 | 201.785 | 2
701 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(120,160]-PONTSTICILL_LOW_LEVEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (120,160] | 17.4317 | 2.8775 | 165.0699 | 2
702 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(120,160]-RHONDDA-MAERDY__PORTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (120,160] | 1.872 | 1.5494 | 827.6612 | 4
703 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (120,160] | 21.7284 | 5.5336 | 254.6694 | 3
704 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-PENARTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (120,160] | 15.5337 | 3.0988 | 199.4891 | 2
705 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(160,320]-PONTSTICILL_LOW_LEVEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (160,320] | 14.5164 | 1.7707 | 121.9822 | 1
706 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(160,320]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (160,320] | 21.1465 | 1.5494 | 73.2697 | 1
707 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-CYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 9.3209 | 1.5494 | 166.2292 | 2
708 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-MERTHYR__ABERCYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 6.1398 | 1.9921 | 324.4545 | 3
709 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RHYMNEY__BARGOED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 11.7622 | 2.2134 | 188.1814 | 2
710 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-MAERDY__PORTH-CASTLE INN BRIDGE-MAESYCOED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 3.0378 | 1.5494 | 510.04 | 4
711 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-MERTHYR__ABERCYNON-PENTREBACH-PENTREBACH/TROEDYRHIW | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 2.661 | 1.5494 | 582.2618 | 4
712 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-RHYMNEY__BARGOED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 18.8361 | 4.6482 | 246.7704 | 2
713 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-RHYMNEY__BARGOED-MAESYCWMMER-FLEUR DE LYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 3.3755 | 2.2134 | 655.7401 | 4
714 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-VALE_OF_GLAM__RHONDDA_VALLEYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 26.1105 | 4.4269 | 169.5431 | 2
715 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-RHONDDA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 9.8463 | 2.6561 | 269.7572 | 3
716 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-RHONDDA-MAERDY__PORTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 20.6435 | 6.8616 | 332.3873 | 3
717 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-RHONDDA-TYNYWAUN-BAGLAN STREET TO DR THOMAS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 1.6698 | 1.5494 | 927.8889 | 4
718 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 9.2444 | 1.9921 | 215.4912 | 2
719 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__CANTON__CATHAYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 4.8271 | 1.7707 | 366.8361 | 3
720 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__RUMNEY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 12.9905 | 3.0988 | 238.5441 | 2
721 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__RUMNEY-PLASNEWYDD ROAD PRV-SUPPLY SUB-SYSTEM BOUNDARY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 1.575 | 1.5494 | 983.7762 | 4
722 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 14.5274 | 1.7707 | 121.8897 | 1
723 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_HEATH_&_LLANISHEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 6.3868 | 2.4348 | 381.2166 | 3
724 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 41.3978 | 10.4031 | 251.2963 | 3
725 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-POLYURETHANE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 35.6343 | 3.5415 | 99.384 | 1
726 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-POLYURETHANE-(70,120]-PONTSTICILL_LOW_LEVEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 12.8732 | 1.7707 | 137.553 | 2
727 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-POLYURETHANE-(70,120]-PONTSTICILL_LOW_LEVEL-CAERPHILLY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 6.9329 | 2.4348 | 351.192 | 3
728 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-POLYURETHANE-(70,120]-PONTSTICILL_LOW_LEVEL-MERTHYR__ABERCYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 5.672 | 1.7707 | 312.1914 | 3
729 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-POLYURETHANE-(70,120]-RHONDDA-VALE_OF_GLAM__RHONDDA_VALLEYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 4.5566 | 1.7707 | 388.6098 | 3
730 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 6.7052 | 1.7707 | 264.0854 | 3
731 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CAERPHILLY-TY CANOL-NANTGARW OFF TYCANOL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 1.3045 | 1.7707 | 1357.4065 | 5
732 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-CENTRAL-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 4.3659 | 1.5494 | 354.8857 | 3
733 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 15.6579 | 1.7707 | 113.0897 | 1
734 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-EPOXY_RESIN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 29.3132 | 1.9921 | 67.9586 | 1
735 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-EPOXY_RESIN-(120,160]-PONTSTICILL_HIGH_LEVEL/HEADS_O | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (120,160] | 5.9638 | 1.5494 | 259.8008 | 3
736 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-EPOXY_RESIN-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RASSAU__SIRHOWY_VALLEY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 9.6167 | 3.0988 | 322.2313 | 3
737 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-EPOXY_RESIN-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_SW__RISCA__ABERCARN-SALISBURY STREET-WEST END NEWBRIDGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 1.3219 | 1.5494 | 1172.1241 | 5
738 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-EPOXY_RESIN-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 8.7155 | 2.6561 | 304.7579 | 3
739 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-EPOXY_RESIN-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-TREVETHIN HILL-TREVETHIN L/LEVEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 2.7927 | 1.5494 | 554.794 | 4
740 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-EPOXY_RESIN-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-VARTEG-VARTEG VILLAGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 6.1821 | 2.4348 | 393.8452 | 3
741 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (0,70] | 15.3668 | 2.2134 | 144.0397 | 2
742 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (120,160] | 11.8098 | 2.8775 | 243.6492 | 2
743 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (120,160] | 11.3971 | 2.2134 | 194.2104 | 2
744 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_WEST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (120,160] | 4.7656 | 1.5494 | 325.1197 | 3
745 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(120,160]-TALYBONT-ABERGAVENNY__CWMTILLERY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (120,160] | 14.4877 | 1.7707 | 122.2243 | 1
746 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(160,320] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (160,320] | 31.5964 | 1.5494 | 49.0373 | 1
747 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(160,320]-TALYBONT-ABERGAVENNY__CWMTILLERY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (160,320] | 8.2861 | 2.6561 | 320.551 | 3
748 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(70,120]-MONMOUTH-MONMOUTH_MAYHILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 3.9595 | 1.5494 | 391.3145 | 3
749 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 16.4186 | 2.4348 | 148.2933 | 2
750 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-EBBW_VALE__BRYNMAWR-CRAIG DDU | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 3.4101 | 1.7707 | 519.2604 | 4
751 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-EBBW_VALE__BRYNMAWR-NANTYGLO AND FFOESMAEN-BLAINA VILLAGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 2.3668 | 1.5494 | 654.6416 | 4
752 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 7.1243 | 1.5494 | 217.4814 | 2
753 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 5.4353 | 1.5494 | 285.0642 | 3
754 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_WEST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 9.7743 | 1.7707 | 181.164 | 2
755 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 29.5629 | 5.7549 | 194.6667 | 2
756 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-GRWYNE FAWR-GELLI/FELIN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 3.7344 | 4.8695 | 1303.966 | 5
757 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-LLANHILLETH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 5.8133 | 2.2134 | 380.7548 | 3
758 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-POLYURETHANE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 22.0264 | 2.2134 | 100.4899 | 1
759 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-POLYURETHANE-(120,160]-TALYBONT-ABERGAVENNY__CWMTILLERY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (120,160] | 7.3253 | 2.6561 | 362.593 | 3
760 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-POLYURETHANE-(160,320] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (160,320] | 11.891 | 1.9921 | 167.529 | 2
761 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-POLYURETHANE-(160,320]-PONTSTICILL_HIGH_LEVEL/HEADS_O-EBBW_VALE__BRYNMAWR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (160,320] | 7.118 | 1.7707 | 248.768 | 2
762 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-POLYURETHANE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 5.7727 | 1.5494 | 268.401 | 3
763 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-POLYURETHANE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-EBBW_VALE__BRYNMAWR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 8.1362 | 3.5415 | 435.2736 | 3
764 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_SW__RISCA__ABERCARN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 17.5194 | 4.8695 | 277.9508 | 3
765 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-POLYURETHANE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 19.6888 | 5.0909 | 258.5678 | 3
766 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-POLYURETHANE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-PONTYPOOL WEST-CWMYNYSCOY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 2.9886 | 1.5494 | 518.4388 | 4
767 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-EASTERN-POLYURETHANE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-TREVETHIN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 3.1098 | 1.5494 | 498.2294 | 3
768 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-NORTHERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 10.8721 | 1.9921 | 183.2298 | 2
769 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-NORTHERN-CEMENT_MORTAR-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 8.8591 | 1.5494 | 174.8929 | 2
770 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-WESTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 55.1419 | 2.4348 | 44.1546 | 1
771 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-WESTERN-CEMENT_MORTAR-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 15.4169 | 2.2134 | 143.5711 | 2
772 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-WESTERN-EPOXY_RESIN-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (120,160] | 11.0755 | 1.7707 | 159.8793 | 2
773 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA-CAPEL_DEWI-EBENEZER SR OUTLETS-EBENEZER-LLANGAIN 4 INCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 1.5768 | 1.5494 | 982.6153 | 4
774 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-WESTERN-NONE-(120,160]-PEMBROKESHIRE-PENDINE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (120,160] | 7.917 | 1.7707 | 223.664 | 2
775 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (120,160] | 19.7873 | 2.2134 | 111.861 | 1
776 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-WESTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 8.9554 | 1.9921 | 222.4454 | 2
777 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PENDINE-THREE LORDS OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 9.4901 | 1.7707 | 186.5876 | 2
778 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 35.1753 | 4.6482 | 132.1439 | 2
779 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PORT_TALBOT_FELINDRE__CRAY-RODERICKS AND DYFFRYN YD-RODERICKS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B07_1910 |  | <=320mm | (70,120] | 2.9238 | 2.2134 | 757.0293 | 4
780 | DIAM_LT_320-FERROUS_1-<=320mm-B07_1910-1901_1920-WESTERN-POLYURETHANE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 8.0111 | 1.9921 | 248.6649 | 2
781 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | [6 empty] | 14.4806 | 1.5494 | 106.9985 | 1
782 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 32.4763 | 2.6561 | 81.7863 | 1
783 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-EPOXY_RESIN-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 7.9106 | 1.7707 | 223.8448 | 2
784 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-EPOXY_RESIN-(70,120]-CYNON-MERTHYR__ABERCYNON-PENLOCKS 19INCH-HAWTHORN TERRACE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 0.99484 | 1.5494 | 1557.4428 | 5
785 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-EPOXY_RESIN-(70,120]-CYNON-PENDERYN__PONTSTICILL-MOUNTAIN ASH WEST-MOUNTAIN ASH WEST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 1.7987 | 1.7707 | 984.4779 | 4
786 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-EPOXY_RESIN-(70,120]-PONTSTICILL_LOW_LEVEL-CAERPHILLY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 4.7771 | 1.7707 | 370.677 | 3
787 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-EPOXY_RESIN-(70,120]-PONTSTICILL_LOW_LEVEL-CAERPHILLY-BEDWAS OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 2.5776 | 1.7707 | 686.981 | 4
788 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (120,160] | 13.3278 | 2.4348 | 182.6838 | 2
789 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(120,160]-PONTSTICILL_HIGH_LEVEL/HEADS_O-MERTHYR__ABERCYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (120,160] | 8.4187 | 1.9921 | 236.6269 | 2
790 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(120,160]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RHYMNEY__BARGOED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (120,160] | 15.5846 | 2.8775 | 184.6345 | 2
791 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(120,160]-PONTSTICILL_LOW_LEVEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (120,160] | 19.6385 | 3.0988 | 157.7917 | 2
792 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-PENARTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (120,160] | 4.8862 | 1.5494 | 317.0962 | 3
793 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(160,320] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (160,320] | 44.4028 | 1.5494 | 34.8942 | 1
794 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(160,320]-PONTSTICILL_HIGH_LEVEL/HEADS_O | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (160,320] | 34.6583 | 1.7707 | 51.0914 | 1
795 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-CYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 10.4834 | 2.2134 | 211.1366 | 2
796 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-CYNON-MERTHYR__ABERCYNON-TAFF 8INCH HIGH LEVEL-HIRWAUN 8 INCH SUPPLY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 2.0744 | 2.2134 | 1067.0183 | 5
797 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-CYNON-MERTHYR__ABERCYNON-TAFF 8INCH HIGH LEVEL-SUB SUPPLY SYSTEM BOUNDARY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 1.2905 | 1.5494 | 1200.6097 | 5
798 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-MERTHYR__ABERCYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 16.2995 | 4.2055 | 258.0142 | 3
799 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RHYMNEY__BARGOED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 28.0022 | 5.9763 | 213.4208 | 2
800 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RHYMNEY__BARGOED-BRITHDIR AND DERI-DERI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 4.6101 | 4.4269 | 960.2464 | 4
801 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RHYMNEY__BARGOED-RHYMNEY CENTRAL AND NORTH-RHYMNEY CENTRAL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 2.9727 | 2.6561 | 893.4911 | 4
802 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RHYMNEY__BARGOED-RHYMNEY SOUTH-PONTLOTTYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 3.2696 | 3.3201 | 1015.4569 | 5
803 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 17.9941 | 2.2134 | 123.0086 | 1
804 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-MAERDY__PORTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 5.047 | 1.5494 | 306.9958 | 3
805 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-MERTHYR__ABERCYNON-BLACK LION | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 2.5713 | 1.5494 | 602.5812 | 4
806 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-MERTHYR__ABERCYNON-QUAKERS YARD 24INCH-SUB SUPPLY SYSTEM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 1.2103 | 2.4348 | 2011.7358 | 5
807 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-MERTHYR__ABERCYNON-QUAKERS YARD 24INCH-TRELEWIS - STORMTOWN (PT 4) | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 2.9251 | 1.7707 | 605.3693 | 4
808 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-PONTYPRIDD_PONTSTICILL_HIGH-CILFYNDD SR AND TY GWYN 9IN OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 7.7379 | 2.6561 | 343.2589 | 3
809 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-PONTYPRIDD_PONTSTICILL_HIGH-CILFYNYDD HIGH-CILFYNYDD HIGH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 3.1292 | 1.9921 | 636.6073 | 4
810 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-RHYMNEY__BARGOED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 10.9232 | 2.8775 | 263.4274 | 3
811 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-RHYMNEY__BARGOED-CEFN FOREST NORTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 1.1954 | 1.5494 | 1296.1468 | 5
812 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-RHYMNEY__BARGOED-QUAKERS YARD 31INCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 4.764 | 1.7707 | 371.6925 | 3
813 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-RHONDDA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 9.9037 | 2.6561 | 268.1954 | 3
814 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-RHONDDA-MAERDY__PORTH-GRAIGWEN AND LANWOOD-GRAIGWEN & LANWOOD OFF R.L | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 2.4722 | 1.7707 | 716.2507 | 4
815 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 21.4405 | 5.3122 | 247.7657 | 2
816 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-POLYURETHANE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 15.403 | 3.0988 | 201.1811 | 2
817 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-POLYURETHANE-(70,120]-CYNON-MERTHYR__ABERCYNON-ABERCYNON WEST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 3.0853 | 1.9921 | 645.6654 | 4
818 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-POLYURETHANE-(70,120]-PONTSTICILL_LOW_LEVEL-CAERPHILLY-MAESYCWMMER-MAESYCWMMER | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 3.2232 | 1.5494 | 480.7058 | 3
819 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-POLYURETHANE-(70,120]-PONTSTICILL_LOW_LEVEL-MERTHYR__ABERCYNON-TREHARRIS TANK-TREHARRIS TANK | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 2.965 | 1.7707 | 597.2091 | 4
820 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-POLYURETHANE-(70,120]-PONTSTICILL_LOW_LEVEL-VALE_OF_GLAM__RHONDDA_VALLEYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 4.6097 | 1.7707 | 384.1362 | 3
821 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-CENTRAL-POLYURETHANE-(70,120]-RHONDDA-VALE_OF_GLAM__RHONDDA_VALLEYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 1.8106 | 1.5494 | 855.7589 | 4
822 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-NORTHERN-CEMENT_MORTAR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 13.5213 | 2.2134 | 163.6997 | 2
823 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-NORTHERN-CEMENT_MORTAR-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-DEINIOLEN CEFN COCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 2.3533 | 1.9921 | 846.5074 | 4
824 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-NORTHERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 33.5288 | 2.2134 | 66.0157 | 1
825 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 9.9685 | 2.4348 | 244.2466 | 2
826 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 7.0287 | 1.5494 | 220.4399 | 2
827 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-WESTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 30.5232 | 2.6561 | 87.0195 | 1
828 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-WESTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 8.6606 | 1.5494 | 178.9011 | 2
829 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 3.9435 | 1.5494 | 392.9021 | 3
830 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1901_1920-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PORT_TALBOT_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1901_1920 | B08_1920 |  | <=320mm | (70,120] | 8.8126 | 1.9921 | 226.0504 | 2
831 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-CENTRAL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 15.2383 | 1.5494 | 101.6782 | 1
832 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 35.8787 | 2.4348 | 67.8613 | 1
833 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B08_1920 |  | <=320mm | (70,120] | 30.0272 | 3.5415 | 117.9428 | 1
834 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-CENTRAL-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B08_1920 |  | <=320mm | (70,120] | 14.1355 | 1.5494 | 109.6106 | 1
835 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-EASTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 22.6193 | 2.2134 | 97.8557 | 1
836 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B08_1920 |  | <=320mm | (70,120] | 10.1225 | 1.7707 | 174.9319 | 2
837 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_WEST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B08_1920 |  | <=320mm | (70,120] | 9.5551 | 1.9921 | 208.4837 | 2
838 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-EASTERN-POLYURETHANE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 7.2869 | 1.9921 | 273.3782 | 3
839 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-NORTHERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 23.5656 | 2.4348 | 103.3187 | 1
840 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-NORTHERN-CEMENT_MORTAR-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1921_1940 | B08_1920 |  | <=320mm | (70,120] | 8.8655 | 1.5494 | 174.7677 | 2
841 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-NORTHERN-EPOXY_RESIN-(120,160]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-LLANDUDNO MAESDU ROAD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1921_1940 | B08_1920 |  | <=320mm | (120,160] | 0.75157 | 1.5494 | 2061.5446 | 5
842 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1921_1940 | B08_1920 |  | <=320mm | (70,120] | 7.3036 | 1.5494 | 212.1417 | 2
843 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-WESTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 18.7127 | 2.2134 | 118.2849 | 1
844 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-WESTERN-CEMENT_MORTAR-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B08_1920 |  | <=320mm | (120,160] | 7.4964 | 1.7707 | 236.2117 | 2
845 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-WESTERN-CEMENT_MORTAR-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B08_1920 |  | <=320mm | (70,120] | 7.7075 | 1.9921 | 258.4616 | 3
846 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-WESTERN-EPOXY_RESIN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 10.4474 | 1.7707 | 169.491 | 2
847 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-PENCOED__BRIDGEND_VALLEYS-CEFN HIRGOED TO LLANGEINOR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1921_1940 | B08_1920 |  | <=320mm | (120,160] | 1.3802 | 1.7707 | 1283.0012 | 5
848 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-WESTERN-NONE-(160,320]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B08_1920 |  | <=320mm | (160,320] | 36.0808 | 1.7707 | 49.0771 | 1
849 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B08_1920 |  | <=320mm | (70,120] | 15.725 | 1.9921 | 126.683 | 2
850 | DIAM_LT_320-FERROUS_1-<=320mm-B08_1920-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-LLANELLI_FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B08_1920 |  | <=320mm | (70,120] | 3.5616 | 1.5494 | 435.0311 | 3
851 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 11.4931 | 1.7707 | 154.0699 | 2
852 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-EPOXY_RESIN-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 11.7195 | 2.4348 | 207.7543 | 2
853 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (120,160] | 10.2489 | 1.9921 | 194.3699 | 2
854 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (120,160] | 16.0524 | 2.2134 | 137.888 | 2
855 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(160,320] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (160,320] | 34.6605 | 1.7707 | 51.0882 | 1
856 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 7.1822 | 1.5494 | 215.7287 | 2
857 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-CYNON-ABERDARE_HIRWAUN__PONSTICILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 12.3965 | 3.3201 | 267.8297 | 3
858 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-CYNON-MERTHYR__ABERCYNON-CWMDARE AND BRYNNAU FARM-CWMDARE LESS BRYNAU FARM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 2.4358 | 1.7707 | 726.9641 | 4
859 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 4.6067 | 1.7707 | 384.3839 | 3
860 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 4.0552 | 1.5494 | 382.0807 | 3
861 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 20.2435 | 2.8775 | 142.1426 | 2
862 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__RUMNEY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 4.5912 | 1.5494 | 337.4709 | 3
863 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__RUMNEY-LLANRUMNEY AVENUE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 3.5991 | 2.2134 | 615.0002 | 4
864 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 21.9722 | 3.0988 | 141.0329 | 2
865 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 19.6493 | 4.2055 | 214.0285 | 2
866 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-POLYURETHANE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (120,160] | 10.1604 | 2.2134 | 217.8479 | 2
867 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-POLYURETHANE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 13.9102 | 3.0988 | 222.772 | 2
868 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-POLYURETHANE-(70,120]-PONTSTICILL_LOW_LEVEL-MERTHYR__ABERCYNON-TWYNRODYN BULK-SUMMERHILL PLACE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 3.1333 | 1.9921 | 635.7872 | 4
869 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-POLYURETHANE-(70,120]-RHONDDA-MAERDY__PORTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 2.5719 | 1.5494 | 602.4387 | 4
870 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-CENTRAL-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_HEATH_&_LLANISHEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 10.7329 | 1.5494 | 144.3601 | 2
871 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-EASTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 34.5136 | 4.4269 | 128.264 | 2
872 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-EASTERN-EPOXY_RESIN-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 17.0597 | 3.3201 | 194.619 | 2
873 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-EASTERN-EPOXY_RESIN-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-TALYWAIN-TALYWAIN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 3.2536 | 2.2134 | 680.3079 | 4
874 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (120,160] | 9.0342 | 1.7707 | 196.0034 | 2
875 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 14.1309 | 1.5494 | 109.6463 | 1
876 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 7.3204 | 2.2134 | 302.3638 | 3
877 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN-LLANDERFEL-HENLLYS 4 INCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 2.8259 | 1.7707 | 626.6032 | 4
878 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 11.9058 | 1.5494 | 130.1379 | 2
879 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_WEST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 14.1971 | 2.2134 | 155.9075 | 2
880 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-EASTERN-NONE-(70,120]-TALYBONT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 2.5717 | 1.9921 | 774.6089 | 4
881 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-NORTHERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 33.5636 | 3.3201 | 98.921 | 1
882 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-NORTHERN-CEMENT_MORTAR-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 38.2678 | 4.4269 | 115.681 | 1
883 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-NORTHERN-EPOXY_RESIN-(70,120]-CLWYD_COASTAL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 5.942 | 1.7707 | 298.0067 | 3
884 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (120,160] | 20.594 | 1.7707 | 85.9834 | 1
885 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 15.389 | 2.2134 | 143.8321 | 2
886 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-FLINT__CONNAHS_QUAY_BRETTON-ASTON 9 INCH-ASTON FROM PLOUGHINN. | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 2.9052 | 1.7707 | 609.5087 | 4
887 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 28.6512 | 5.9763 | 208.5868 | 2
888 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 6.2294 | 2.2134 | 355.3204 | 3
889 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 16.9348 | 2.8775 | 169.9137 | 2
890 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON-BANGOR MAESGEIRCHEN-MAESGERCHEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 3.2159 | 1.5494 | 481.7934 | 3
891 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-WESTERN-CEMENT_MORTAR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 17.3298 | 2.2134 | 127.7241 | 2
892 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-WESTERN-EPOXY_RESIN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 11.3094 | 1.5494 | 137.001 | 2
893 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-WESTERN-EPOXY_RESIN-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (120,160] | 11.5507 | 1.9921 | 172.4639 | 2
894 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-WESTERN-EPOXY_RESIN-(70,120]-MID_-_SOUTH_CEREDIGION | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 7.0944 | 1.5494 | 218.3983 | 2
895 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY-SIGGINGSTONE 12INCH OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 2.0893 | 1.9921 | 953.4862 | 4
896 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 28.0427 | 1.9921 | 71.0377 | 1
897 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-WESTERN-NONE-(120,160]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (120,160] | 10.8108 | 1.7707 | 163.7938 | 2
898 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 11.6135 | 1.9921 | 171.5319 | 2
899 | DIAM_LT_320-FERROUS_1-<=320mm-B09_1930-1921_1940-WESTERN-POLYURETHANE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B09_1930 |  | <=320mm | (70,120] | 6.163 | 2.2134 | 359.1453 | 3
900 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | [6 empty] | 30.3184 | 2.2134 | 73.0062 | 1
901 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-CENTRAL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 7.6535 | 2.4348 | 318.1244 | 3
902 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 9.1564 | 1.5494 | 169.2155 | 2
903 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-CENTRAL-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 9.1402 | 3.3201 | 363.2464 | 3
904 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RHYMNEY__BARGOED-RHYMNEY SOUTH-ABERTYSSWG | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 0.59805 | 2.4348 | 4071.1603 | 5
905 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-PONTYPRIDD_PONTSTICILL_HIGH-RHYDYFELIN LOW LEVEL BULK-RHYDYFELIN L.L. BULK | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 3.9627 | 1.5494 | 390.9972 | 3
906 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-RHYMNEY__BARGOED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 2.9924 | 1.5494 | 517.7761 | 4
907 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-CENTRAL-NONE-(70,120]-RHONDDA-PONTYPRIDD_PONTSTICILL_HIGH-GLYNCOCH HIGH-GLYNCOCH HIGH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 5.1739 | 3.3201 | 641.7113 | 4
908 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH__BARRY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 2.4748 | 1.5494 | 626.075 | 4
909 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-CENTRAL-POLYURETHANE-(70,120]-PONTSTICILL_LOW_LEVEL-CAERPHILLY-GWERNAU 12INCH CAERPHILLY FLOW-CAERPHILLY NORTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 5.9064 | 3.5415 | 599.6 | 4
910 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-NORTHERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 21.7808 | 1.5494 | 71.136 | 1
911 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-NORTHERN-CEMENT_MORTAR-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 12.0852 | 3.3201 | 274.7286 | 3
912 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 17.1167 | 3.5415 | 206.9023 | 2
913 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-GOSEN TYN Y FRITH-T1 TO RHYD Y FOEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 5.3959 | 1.7707 | 328.1653 | 3
914 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-CEMENT_MORTAR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 13.5937 | 1.9921 | 146.5446 | 2
915 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-EPOXY_RESIN-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1921_1940 | B10_1940 |  | <=320mm | (120,160] | 10.8045 | 2.8775 | 266.3205 | 3
916 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-EPOXY_RESIN-(70,120]-MID_-_SOUTH_CEREDIGION | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 7.1098 | 1.7707 | 249.058 | 2
917 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-EPOXY_RESIN-(70,120]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 7.528 | 4.6482 | 617.4586 | 4
918 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 6.6628 | 1.9921 | 298.9865 | 3
919 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 17.6408 | 4.8695 | 276.0379 | 3
920 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(120,160]-PEMBROKESHIRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B10_1940 |  | <=320mm | (120,160] | 4.9396 | 1.7707 | 358.4775 | 3
921 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B10_1940 |  | <=320mm | (120,160] | 10.4759 | 1.7707 | 169.0309 | 2
922 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B10_1940 |  | <=320mm | (120,160] | 5.9475 | 1.9921 | 334.9442 | 3
923 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-PEMBROKESHIRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 4.8993 | 1.7707 | 361.4294 | 3
924 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 7.1227 | 2.2134 | 310.7573 | 3
925 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 5.72 | 1.5494 | 270.8729 | 3
926 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY-LLANGEWYDD-LLANGEWYDD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 3.911 | 1.7707 | 452.7594 | 3
927 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY-NEWTON NOTTAGE-NEWTON NOTTAGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 3.1216 | 2.2134 | 709.0786 | 4
928 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY-NOTTAGE MAIN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 4.4018 | 1.9921 | 452.5646 | 3
929 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PENCOED__BRIDGEND_VALLEYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 14.6348 | 4.4269 | 302.4892 | 3
930 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PORT_TALBOT_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 11.5872 | 2.8775 | 248.3314 | 2
931 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PORT_TALBOT_FELINDRE__CRAY-TOLLGATE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 3.6629 | 1.9921 | 543.856 | 4
932 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKEWEN__LLANDARCY_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 19.8573 | 4.2055 | 211.7868 | 2
933 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKEWEN__LLANDARCY_FELINDRE__CRAY-MAES RHEDYN AND LODGE DRIVE-LODGE DRIVE BAGLAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 1.4943 | 1.5494 | 1036.9023 | 5
934 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-POLYURETHANE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 4.1851 | 1.5494 | 370.2173 | 3
935 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-POLYURETHANE-(70,120]-PEMBROKESHIRE-BOLTON_HILL-ROSEPOOL-FOXHILL RES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 1.1812 | 1.7707 | 1499.0989 | 5
936 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1921_1940-WESTERN-POLYURETHANE-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 8.2965 | 3.3201 | 400.1877 | 3
937 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | [6 empty] | 27.9577 | 1.9921 | 71.2535 | 1
938 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-CENTRAL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 9.4197 | 2.2134 | 234.9792 | 2
939 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-CENTRAL-EPOXY_RESIN-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 2.8892 | 1.9921 | 689.4988 | 4
940 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 11.1844 | 3.9842 | 356.2246 | 3
941 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 4.4759 | 2.8775 | 642.8833 | 4
942 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-EASTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 16.3283 | 1.7707 | 108.4461 | 1
943 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 8.2637 | 1.9921 | 241.0653 | 2
944 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 7.1194 | 3.0988 | 435.2638 | 3
945 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_WEST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 7.5705 | 3.0988 | 409.3253 | 3
946 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-NORTHERN-CEMENT_MORTAR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 17.8376 | 1.9921 | 111.6788 | 1
947 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-NORTHERN-EPOXY_RESIN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 7.6509 | 1.5494 | 202.5115 | 2
948 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 3.1538 | 1.7707 | 561.4701 | 4
949 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 8.7561 | 1.5494 | 176.951 | 2
950 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 3.0362 | 1.7707 | 583.2126 | 4
951 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 8.5117 | 2.4348 | 286.0493 | 3
952 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 34.7339 | 1.9921 | 57.3527 | 1
953 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-CEMENT_MORTAR-(70,120]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 5.5719 | 1.7707 | 317.7963 | 3
954 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-EPOXY_RESIN-(70,120]-PEMBROKESHIRE-PRESELI_SUPPLY-PRESELI DOLWEN-EITHBED OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 7.2533 | 2.4348 | 335.6785 | 3
955 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 19.6663 | 4.4269 | 225.0984 | 2
956 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY-NEWTON NOTTAGE-NEWTON NOTTAGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 5.7028 | 2.4348 | 426.9429 | 3
957 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 34.0653 | 3.5415 | 103.9617 | 1
958 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 |  | <=320mm | (120,160] | 22.8833 | 2.4348 | 106.3995 | 1
959 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL-NORCHARD BEACON SR OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 2.4506 | 1.5494 | 632.2577 | 4
960 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL-STEPHENS GREEN SR OUTLET-JAMESTON YOUTH CLUB | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 2.9955 | 1.7707 | 591.1366 | 4
961 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PENDINE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 5.5558 | 1.5494 | 278.8816 | 3
962 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PENDINE-BRANDY HILL TO ST. CLEARS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 6.1404 | 2.4348 | 396.5165 | 3
963 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PENDINE-THREE LORDS OUTLET-THREE LORDS (BROADWAY/LAUGHARN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 1.8145 | 1.5494 | 853.8795 | 4
964 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 28.8422 | 3.7628 | 130.4625 | 2
965 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 5.2172 | 1.5494 | 296.9786 | 3
966 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-LLANELLI_FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 4.6882 | 2.4348 | 519.3395 | 4
967 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PENCOED__BRIDGEND_VALLEYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 6.8788 | 2.4348 | 353.9552 | 3
968 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKEWEN__LLANDARCY_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 5.7288 | 1.5494 | 270.4566 | 3
969 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-POLYURETHANE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 5.3936 | 1.9921 | 369.3432 | 3
970 | DIAM_LT_320-FERROUS_1-<=320mm-B10_1940-1941_1960-WESTERN-POLYURETHANE-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 3.1503 | 1.9921 | 632.3498 | 4
971 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 5.7265 | 2.2134 | 386.5214 | 3
972 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-EPOXY_RESIN-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_HEATH_&_LLANISHEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 5.4099 | 2.2134 | 409.1416 | 3
973 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 20.9275 | 1.7707 | 84.6133 | 1
974 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 10.7075 | 1.5494 | 144.7028 | 2
975 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 11.5317 | 2.2134 | 191.9437 | 2
976 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 15.4108 | 2.4348 | 157.9917 | 2
977 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-CYNON-MERTHYR__ABERCYNON-PENYWAUN / CEMETERY ROAD-PENYWAUN/CEMETERY RD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 6.7936 | 3.7628 | 553.8764 | 4
978 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-MERTHYR__ABERCYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 2.2216 | 1.7707 | 797.0489 | 4
979 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-MERTHYR__ABERCYNON-GALON UCHAF ESTATE-GALON UCHAF ESTATE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 7.3947 | 2.4348 | 329.2602 | 3
980 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-MERTHYR__ABERCYNON-GUERNOS EAST-GURNOS EAST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 6.0302 | 1.5494 | 256.9406 | 3
981 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 6.4172 | 1.5494 | 241.4457 | 2
982 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-MERTHYR__ABERCYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 4.977 | 1.5494 | 311.3139 | 3
983 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-PONTYPRIDD_PONTSTICILL_HIGH-RHYDYFELIN LOW LEVEL BULK-RHYDYFELIN L.L. BULK | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 5.1106 | 1.7707 | 346.4838 | 3
984 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-VALE_OF_GLAM__RHONDDA_VALLEYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 2.9162 | 1.5494 | 531.3002 | 4
985 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-RHONDDA-MAERDY__PORTH-CYMMER | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 2.7997 | 1.5494 | 553.4171 | 4
986 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-RHONDDA-MAERDY__PORTH-MAERDY HP OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 3.8701 | 1.7707 | 457.5389 | 3
987 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 15.5193 | 4.6482 | 299.5106 | 3
988 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_EAST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 7.5165 | 2.4348 | 323.9237 | 3
989 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_EAST-LLANRUMNEY PUMPS-LLANRUMNEY PUMP | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 4.9025 | 2.4348 | 496.6386 | 3
990 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 8.3612 | 2.4348 | 291.1994 | 3
991 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF-PENTREBANE NORTH-PENTREBANE NORTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 3.6876 | 1.5494 | 420.1642 | 3
992 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH__BARRY-LOWER PENARTH PRV-AREA FED BY SSS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 1.263 | 1.7707 | 1401.985 | 5
993 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH__BARRY-REDLANDS ROAD SOUTH-REDLANDS ROAD SOUTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 2.6388 | 1.7707 | 671.0506 | 4
994 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-POLYURETHANE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 5.3276 | 1.7707 | 332.3718 | 3
995 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-POLYURETHANE-(70,120]-PONTSTICILL_LOW_LEVEL-MERTHYR__ABERCYNON-TWYNRODYN BULK-SUMMERHILL PLACE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 2.0923 | 2.6561 | 1269.4624 | 5
996 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-POLYURETHANE-(70,120]-PONTSTICILL_LOW_LEVEL-PONTYPRIDD_PONTSTICILL_HIGH-RHYDYFELIN LOW LEVEL BULK-RHYDYFELIN SOUTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 1.7996 | 1.5494 | 860.9671 | 4
997 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 3.7195 | 1.5494 | 416.556 | 3
998 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_HEATH_&_LLANISHEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 7.2435 | 2.8775 | 397.2458 | 3
999 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-CENTRAL-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_HEATH_&_LLANISHEN-LLANDENNIS ROAD-LLANDENNIS ROAD 10 INCH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 5.2671 | 2.8775 | 546.309 | 4
1000 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 42.6733 | 3.7628 | 88.1776 | 1
1001 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-EPOXY_RESIN-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 6.9141 | 1.7707 | 256.1055 | 3
1002 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-EPOXY_RESIN-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 18.1363 | 4.6482 | 256.293 | 3
1003 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-EPOXY_RESIN-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL-WEOBLEY NORTH-WEOBLEY RES NORTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 2.7953 | 2.4348 | 871.0256 | 4
1004 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-EPOXY_RESIN-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 12.3668 | 3.9842 | 322.1656 | 3
1005 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-EPOXY_RESIN-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 9.3 | 3.0988 | 333.2029 | 3
1006 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-EPOXY_RESIN-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-CEFN PENDEGAR REDUCED DMA-BRYN DERI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 4.1982 | 1.5494 | 369.0614 | 3
1007 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-EPOXY_RESIN-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-CEFN PENDEGAR REDUCED DMA-LLANTILLIO | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 7.4396 | 3.5415 | 476.0326 | 3
1008 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 9.5787 | 2.6561 | 277.2941 | 3
1009 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(0,70]-TALYBONT-ABERGAVENNY__CWMTILLERY-LITTLE MILL TO USK | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 0.7691 | 1.5494 | 2014.5747 | 5
1010 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 30.5587 | 2.2134 | 72.4319 | 1
1011 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(120,160]-MONMOUTH-TRELLECH__MAYHILL__FYNNON_GAER-TRELLECK-FARR HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 8.1374 | 1.5494 | 190.405 | 2
1012 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(160,320] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (160,320] | 33.8449 | 2.6561 | 78.4791 | 1
1013 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 18.8512 | 4.4269 | 234.8313 | 2
1014 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 8.8845 | 2.2134 | 249.1335 | 2
1015 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-DUNFIELD_CROSSWAYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 6.2137 | 1.9921 | 320.5969 | 3
1016 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-MONMOUTH-TRELLECH__MAYHILL__FYNNON_GAER-TRELLECK | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 15.2062 | 4.6482 | 305.6783 | 3
1017 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-MONMOUTH-TRELLECH__MAYHILL__FYNNON_GAER-TRELLECK-CATBROOK | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 4.2826 | 1.5494 | 361.7854 | 3
1018 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-MONMOUTH-TRELLECH__MAYHILL__FYNNON_GAER-TRELLECK-FARR HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 4.1417 | 2.4348 | 587.8737 | 4
1019 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-MONMOUTH-TRELLECH__MAYHILL__FYNNON_GAER-TRELLECK-NEW MILLS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 3.5315 | 2.4348 | 689.4403 | 4
1020 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-MONMOUTH-TRELLECH__MAYHILL__FYNNON_GAER-TRELLECK-PENALLT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 6.9887 | 2.4348 | 348.386 | 3
1021 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 7.2701 | 1.5494 | 213.1198 | 2
1022 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 4.7583 | 1.9921 | 418.6519 | 3
1023 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 10.3692 | 2.2134 | 213.461 | 2
1024 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN-SLUVAD A-LLANGIBBY VILLAGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 3.0538 | 1.5494 | 507.3637 | 4
1025 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 6.1442 | 1.5494 | 252.1729 | 3
1026 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT-ST JULIANS ROAD-FIRBANK AVENUE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 3.6224 | 2.4348 | 672.1498 | 4
1027 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 29.0351 | 6.8616 | 236.3218 | 2
1028 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-LITTLE MILL TO USK-GWEHELOG SUPPLY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 4.387 | 3.3201 | 756.8188 | 4
1029 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-LITTLE MILL TO USK-USK-LLANGIBBY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 4.2554 | 1.5494 | 364.0997 | 3
1030 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-POLYURETHANE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 13.9907 | 3.3201 | 237.3113 | 2
1031 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-POLYURETHANE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 7.6613 | 2.4348 | 317.8007 | 3
1032 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-EASTERN-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN-LLANYRAVON-LLANYRAVON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 6.3288 | 3.0988 | 489.6378 | 3
1033 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 62.7377 | 4.4269 | 70.5614 | 1
1034 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-CEMENT_MORTAR-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 20.3503 | 3.5415 | 174.0259 | 2
1035 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-CEMENT_MORTAR-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 22.2482 | 4.8695 | 218.8731 | 2
1036 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-CEMENT_MORTAR-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-GWALCHMAI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 8.6569 | 1.9921 | 230.1157 | 2
1037 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-CEMENT_MORTAR-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-MONA TO HOLLAND ARMS-PENTRE BERW TO LLANGAFFO | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 3.8419 | 1.5494 | 403.2922 | 3
1038 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-CEMENT_MORTAR-(70,120]-NORTH_ERYRI_/_YNYS_MON-SOUTH_ANGLESEY_CWELLYN__MYNYDD-PENMYNYDD CADNANT GAERWEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 2.8501 | 1.7707 | 621.2956 | 4
1039 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-EPOXY_RESIN-(160,320] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (160,320] | 23.5932 | 1.9921 | 84.4347 | 1
1040 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-EPOXY_RESIN-(160,320]-NORTH_ERYRI_/_YNYS_MON-EAST_ANGLESEY_CEFNI-LLANDYFRYDOG TO PENSARN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (160,320] | 7.7861 | 1.9921 | 255.8503 | 3
1041 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-EPOXY_RESIN-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 9.0651 | 2.4348 | 268.5886 | 3
1042 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-EPOXY_RESIN-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-BYLCHAU HIGH-CEFN LLWYDHENLLAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 2.8247 | 2.2134 | 783.5976 | 4
1043 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-EPOXY_RESIN-(70,120]-CLWYD_COASTAL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 10.2682 | 1.7707 | 172.4494 | 2
1044 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-EPOXY_RESIN-(70,120]-NORTH_ERYRI_/_YNYS_MON-EAST_ANGLESEY_CEFNI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 1.7424 | 1.5494 | 889.2294 | 4
1045 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 8.2456 | 2.2134 | 268.4374 | 3
1046 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 20.0769 | 1.7707 | 88.1979 | 1
1047 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(120,160]-NORTH_ERYRI_/_YNYS_MON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 6.9966 | 1.5494 | 221.4519 | 2
1048 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 9.8795 | 2.8775 | 291.2552 | 3
1049 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-FLINT__CONNAHS_QUAY_BRETTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 3.1668 | 1.7707 | 559.151 | 4
1050 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON-RHOSESMOR BERTH DDU | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 2.6603 | 1.5494 | 582.4091 | 4
1051 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 22.0481 | 5.7549 | 261.0161 | 3
1052 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT VALLEY GAP | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 9.9379 | 2.6561 | 267.2704 | 3
1053 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-PENRHYNDEUDRAETH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 1.2302 | 1.9921 | 1619.3256 | 5
1054 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 16.5905 | 2.6561 | 160.0989 | 2
1055 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-BANGOR__CAERNARFON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 6.4331 | 2.2134 | 344.0711 | 3
1056 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-EAST_ANGLESEY_CEFNI-RHOSYBOL TO COEDEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 1.9364 | 1.9921 | 1028.7612 | 5
1057 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 25.2714 | 2.4348 | 96.345 | 1
1058 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-CAERGEILIOG SCHOOL 150-REFAIL CROSSROADS TO RHOSCOLY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 3.5678 | 1.5494 | 434.275 | 3
1059 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-COEDEN TO LLANFAETHLU-LLANRHUDDLAD TO RHYDWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 2.7922 | 2.2134 | 792.728 | 4
1060 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-COEDEN TO LLANFAETHLU-RHYDWYN VILLAGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 1.405 | 2.6561 | 1890.5286 | 5
1061 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-MONA TO HOLLAND ARMS-CEFN CWMWD TO BETHEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 9.5703 | 4.4269 | 462.5615 | 3
1062 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-SOUTH_ANGLESEY_CWELLYN__MYNYDD-FELIN ENGAN LLANFAIR PG-FELIN ENGAN TO LLANFAIRPWLL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 2.1678 | 1.7707 | 816.8294 | 4
1063 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-NORTHERN-POLYURETHANE-(70,120]-CLWYD_COASTAL-ABERGELE__RHYL_GLASCOED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 11.0803 | 3.0988 | 279.6672 | 3
1064 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-CEMENT_MORTAR-(120,160]-PEMBROKESHIRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 10.6716 | 1.9921 | 186.6712 | 2
1065 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-CEMENT_MORTAR-(120,160]-PEMBROKESHIRE-PRESELI_SUPPLY-MOUNTAIN TREFFGARNE AND RUDBAXTON-PLUMSTONE TO TREFFGARNE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 5.2817 | 1.7707 | 335.2575 | 3
1066 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-CEMENT_MORTAR-(70,120]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 6.7603 | 2.6561 | 392.9015 | 3
1067 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-EPOXY_RESIN-(120,160]-TYWI_C.U._AREA-CAPEL_DEWI-EBENEZER SR OUTLETS-LLANSTEPHAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 2.5094 | 1.9921 | 793.8504 | 4
1068 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-EPOXY_RESIN-(70,120]-PEMBROKESHIRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 4.3699 | 1.5494 | 354.5627 | 3
1069 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 15.9237 | 3.0988 | 194.6027 | 2
1070 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 36.3621 | 1.9921 | 54.7846 | 1
1071 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 8.3169 | 1.7707 | 212.9102 | 2
1072 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 4.0593 | 1.7707 | 436.223 | 3
1073 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 2.3832 | 2.2134 | 928.7708 | 4
1074 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PENDINE-BRANDY HILL TO CROSSHANDS-PONT Y FENNI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 0.88876 | 1.5494 | 1743.3198 | 5
1075 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 14.7209 | 4.2055 | 285.6825 | 3
1076 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKEWEN__LLANDARCY_FELINDRE__CRAY-MAES RHEDYN AND LODGE DRIVE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 1.0648 | 1.5494 | 1455.1702 | 5
1077 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SWANSEA__MORRISTON_BRYNGWYN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 2.2951 | 1.5494 | 675.0939 | 4
1078 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-POLYURETHANE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 12.5632 | 1.5494 | 123.3284 | 1
1079 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-POLYURETHANE-(70,120]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 2.5296 | 1.9921 | 787.5177 | 4
1080 | DIAM_LT_320-FERROUS_1-<=320mm-B11_1950-1941_1960-WESTERN-POLYURETHANE-(70,120]-TYWI_C.U._AREA-BRYNGWYN-TROEDYRHIW TO MAESTWYNOG-POST GWYN FFARMERS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 2.4545 | 2.6561 | 1082.1217 | 5
1081 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN | [6 empty] | 24.2962 | 2.2134 | 91.1017 | 1
1082 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-EPOXY_RESIN-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 4.0244 | 1.5494 | 385.0038 | 3
1083 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-EPOXY_RESIN-(70,120]-CYNON-MERTHYR__ABERCYNON-PENLOCKS 19INCH-HAWTHORN TERRACE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 0.80307 | 1.7707 | 2204.9654 | 5
1084 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-EPOXY_RESIN-(70,120]-CYNON-PENDERYN__PONTSTICILL-PERTHCELYN-PERTHCELYN PUMPS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 0.91825 | 1.5494 | 1687.3411 | 5
1085 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-EPOXY_RESIN-(70,120]-PONTSTICILL_LOW_LEVEL-RHYMNEY__BARGOED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 5.9443 | 1.7707 | 297.8912 | 3
1086 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B12_1960 |  | <=320mm | (120,160] | 11.4959 | 2.4348 | 211.7945 | 2
1087 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(70,120]-CYNON-ABERDARE_HIRWAUN__PONSTICILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 3.7308 | 1.5494 | 415.2959 | 3
1088 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-MERTHYR__ABERCYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 7.5385 | 2.2134 | 293.6169 | 3
1089 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RHYMNEY__BARGOED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 3.2173 | 1.5494 | 481.5903 | 3
1090 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 12.5409 | 3.0988 | 247.096 | 2
1091 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-RHYMNEY__BARGOED-CEFN FOREST NORTH-BRITTANIA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 1.7853 | 1.5494 | 867.8861 | 4
1092 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(70,120]-RHONDDA-MAERDY__PORTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 4.7418 | 2.4348 | 513.4721 | 4
1093 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 8.5221 | 3.3201 | 389.5909 | 3
1094 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-POLYURETHANE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 3.0866 | 1.5494 | 501.9795 | 4
1095 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-CENTRAL-POLYURETHANE-(70,120]-PONTSTICILL_LOW_LEVEL-MERTHYR__ABERCYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 3.1788 | 1.5494 | 487.4173 | 3
1096 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-EASTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 18.0678 | 1.7707 | 98.0055 | 1
1097 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-EASTERN-EPOXY_RESIN-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 11.9118 | 2.6561 | 222.9824 | 2
1098 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-EASTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 16.6467 | 1.9921 | 119.6686 | 1
1099 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 14.7763 | 4.6482 | 314.5703 | 3
1100 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-DUNFIELD_CROSSWAYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 6.6057 | 1.5494 | 234.5533 | 2
1101 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 4.7219 | 1.5494 | 328.1311 | 3
1102 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 2.0495 | 1.7707 | 863.9963 | 4
1103 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN-MALPAS ROAD HIGH PRESSURE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 0.94237 | 1.7707 | 1879.0306 | 5
1104 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-EASTERN-POLYURETHANE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RASSAU__SIRHOWY_VALLEY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 5.1876 | 1.9921 | 384.0088 | 3
1105 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-EASTERN-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_SW__RISCA__ABERCARN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 8.2743 | 3.3201 | 401.2586 | 3
1106 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-NORTHERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 15.7391 | 1.9921 | 126.5689 | 2
1107 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 7.6398 | 1.5494 | 202.8065 | 2
1108 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-WESTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 7.5095 | 1.5494 | 206.3258 | 2
1109 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-WESTERN-EPOXY_RESIN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 9.0552 | 1.7707 | 195.55 | 2
1110 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 5.3327 | 1.7707 | 332.0521 | 3
1111 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 8.4678 | 2.6561 | 313.6722 | 3
1112 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-CENTRAL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 28.3183 | 1.7707 | 62.53 | 1
1113 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-CENTRAL-EPOXY_RESIN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 4.5294 | 1.5494 | 342.074 | 3
1114 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 3.151 | 1.5494 | 491.7206 | 3
1115 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 13.9286 | 1.9921 | 143.021 | 2
1116 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-VALE_OF_GLAM__RHONDDA_VALLEYS-ALFRED STREET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 2.0028 | 1.9921 | 994.6424 | 4
1117 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL-VALE_OF_GLAM__RHONDDA_VALLEYS-LLANTRISANT TANK 12INCH PONTYCLUN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 2.9221 | 1.5494 | 530.2286 | 4
1118 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 2.4122 | 1.9921 | 825.8236 | 4
1119 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 2.4568 | 1.5494 | 630.6589 | 4
1120 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH__BARRY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 3.5533 | 1.5494 | 436.0433 | 3
1121 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 52.2135 | 3.9842 | 76.3053 | 1
1122 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-BITUMEN-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 8.4408 | 1.9921 | 236.0074 | 2
1123 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-BITUMEN-(70,120]-HEREFORD_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 7.9394 | 2.4348 | 306.6705 | 3
1124 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-BITUMEN-(70,120]-VOWCHURCH-VOWCHURCH-BRAMPTON SR-WALTERSTONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 5.9769 | 1.5494 | 259.2307 | 3
1125 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-BITUMEN-(70,120]-WHITBOURNE-WHITBOURNE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 1.5242 | 1.7707 | 1161.7673 | 5
1126 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-EPOXY_RESIN-(120,160]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 7.0986 | 1.5494 | 218.2686 | 2
1127 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-EPOXY_RESIN-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 11.6705 | 3.0988 | 265.5239 | 3
1128 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-EPOXY_RESIN-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 22.0706 | 5.5336 | 250.7219 | 3
1129 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-EPOXY_RESIN-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL-MALVERN RD-LEDBURY RES MALVERN RD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 0.51598 | 1.5494 | 3002.8483 | 5
1130 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-EPOXY_RESIN-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL-WEOBLEY SOUTH-NORTON PRV | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 11.0923 | 1.7707 | 159.6373 | 2
1131 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-EPOXY_RESIN-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL-WEOBLEY SOUTH-NORTON WOOD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 8.8654 | 2.8775 | 324.5724 | 3
1132 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-EPOXY_RESIN-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL-WEOBLEY SOUTH-REDLION PUB BREDWARDINE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 17.302 | 4.6482 | 268.6509 | 3
1133 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-EPOXY_RESIN-(70,120]-ROSS-ON-WYE-ROSS-ON-WYE_MITCHELDEAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 4.0275 | 1.5494 | 384.7051 | 3
1134 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-EPOXY_RESIN-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 1.8161 | 1.9921 | 1096.8979 | 5
1135 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (0,70] | 12.8034 | 3.0988 | 242.0293 | 2
1136 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 40.1943 | 7.083 | 176.2183 | 2
1137 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(120,160]-HEREFORD_C.U._AREA-DUNFIELD_CROSSWAYS-CROSSWAYS SOUTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 14.4313 | 1.9921 | 138.0392 | 2
1138 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 6.0447 | 1.9921 | 329.5599 | 3
1139 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 5.9755 | 1.7707 | 296.3343 | 3
1140 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 8.0493 | 1.9921 | 247.4866 | 2
1141 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(160,320]-HEREFORD_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (160,320] | 13.4106 | 1.7707 | 132.0401 | 2
1142 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 29.3279 | 5.7549 | 196.2264 | 2
1143 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-DUNFIELD_CROSSWAYS-CROSSWAYS NORTH AND HIGH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 20.3696 | 4.4269 | 217.3264 | 2
1144 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-DUNFIELD_CROSSWAYS-CROSSWAYS NORTH AND HIGH-BRILLEY SCHOOL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 10.802 | 3.5415 | 327.8531 | 3
1145 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-DUNFIELD_CROSSWAYS-CROSSWAYS NORTH AND HIGH-KINGSWOOD(CROSSWAYS HIGH) | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 2.1412 | 2.2134 | 1033.7532 | 5
1146 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-DUNFIELD_CROSSWAYS-CROSSWAYS NORTH AND HIGH-PHONEBOX BRILLEY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 5.664 | 1.9921 | 351.7079 | 3
1147 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-DUNFIELD_CROSSWAYS-CROSSWAYS NORTH AND HIGH-THE SHAWL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 5.8569 | 3.3201 | 566.8725 | 4
1148 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-DUNFIELD_CROSSWAYS-CROSSWAYS SOUTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 35.888 | 4.6482 | 129.5194 | 2
1149 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-DUNFIELD_CROSSWAYS-CROSSWAYS SOUTH-SARNESFIELD JUNCTION | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 2.9518 | 1.7707 | 599.8922 | 4
1150 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 8.2346 | 1.9921 | 241.9169 | 2
1151 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL-BEWDLEY RES TO WOEBLEY RES TDMA-AREA FEED BY 1T810310 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 1.4414 | 1.5494 | 1074.9464 | 5
1152 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL-WEOBLEY SOUTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 3.8274 | 1.7707 | 462.6466 | 3
1153 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__SOUTH_BROOMY_HILL_ | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 4.609 | 1.5494 | 336.1682 | 3
1154 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 8.2054 | 1.7707 | 215.8027 | 2
1155 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 8.051 | 2.8775 | 357.4016 | 3
1156 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 17.5735 | 5.0909 | 289.6906 | 3
1157 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN-LLANDERFEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 4.9217 | 2.2134 | 449.7266 | 3
1158 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN-MALPAS ROAD HIGH PRESSURE-WHITTLE DRIVE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 1.389 | 2.2134 | 1593.4903 | 5
1159 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 13.3063 | 3.9842 | 299.4202 | 3
1160 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT-RINGWOOD 1 AND 2 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 3.2273 | 1.5494 | 480.0898 | 3
1161 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 6.5387 | 3.0988 | 473.9174 | 3
1162 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-CHAIN ROAD DAN Y DERRY-CHAIN ROAD(UNDERHILL) | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 3.5189 | 1.7707 | 503.2121 | 4
1163 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-VOWCHURCH-VOWCHURCH-BRAMPTON SR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 24.9547 | 3.5415 | 141.9165 | 2
1164 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-VOWCHURCH-VOWCHURCH-BRAMPTON SR-MYNYDD FERDDYN (LONGTOWN) | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 1.3443 | 1.5494 | 1152.554 | 5
1165 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-VOWCHURCH-VOWCHURCH-BRAMPTON SR-SARAS CROSS (LONGTOWN) | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 5.4155 | 1.7707 | 326.9776 | 3
1166 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-WHITBOURNE-WHITBOURNE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 8.3185 | 2.6561 | 319.3007 | 3
1167 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-WHITBOURNE-WHITBOURNE-RIDGEWAY STIFFORDS BRIDGE-STIFFORDS BRIDGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 3.105 | 1.7707 | 570.2895 | 4
1168 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-WHITBOURNE-WHITBOURNE-WARRENWOOD-UPPER SAPEY METER | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 0.6001 | 1.7707 | 2950.7468 | 5
1169 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-POLYURETHANE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 12.6937 | 1.5494 | 122.0607 | 1
1170 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-POLYURETHANE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 9.7679 | 1.9921 | 203.9417 | 2
1171 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 6.8497 | 2.6561 | 387.7732 | 3
1172 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN-BETTWS EAST-BETTWS EAST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 4.0791 | 2.4348 | 596.8951 | 4
1173 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-EASTERN-POLYURETHANE-(70,120]-TALYBONT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 2.5553 | 2.2134 | 866.2155 | 4
1174 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-NORTHERN-EPOXY_RESIN-(70,120]-CLWYD_COASTAL-PRESTATYN_GLASCOED__TRECASTELL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 7.3783 | 1.5494 | 209.994 | 2
1175 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-NORTHERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 17.5338 | 1.9921 | 113.6141 | 1
1176 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 10.1374 | 2.6561 | 262.0117 | 3
1177 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 13.1095 | 3.7628 | 287.0296 | 3
1178 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-WESTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 35.2546 | 2.4348 | 69.0625 | 1
1179 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 8.9721 | 2.6561 | 296.0425 | 3
1180 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 6.6147 | 1.5494 | 234.2353 | 2
1181 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-SKEWEN__LLANDARCY_FELINDRE__CRAY-EAST SWANSEA DOCKS-BURROWS ENTRANCE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 0.32472 | 2.2134 | 6816.3214 | 5
1182 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 19.4945 | 6.8616 | 351.9776 | 3
1183 | DIAM_LT_320-FERROUS_1-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PORT_TALBOT_FELINDRE__CRAY-TY CANOL PUMPED OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 3.4355 | 1.5494 | 450.9984 | 3
1184 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-CENTRAL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 18.5816 | 2.8775 | 154.8551 | 2
1185 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 11.7806 | 1.5494 | 131.5209 | 2
1186 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(70,120]-CYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 4.8768 | 1.5494 | 317.708 | 3
1187 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-MERTHYR__ABERCYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 16.334 | 3.0988 | 189.7144 | 2
1188 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(70,120]-PONTSTICILL_HIGH_LEVEL/HEADS_O-MERTHYR__ABERCYNON-PONSTICILL AND VAYNOR-TREFECHAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 3.6236 | 2.6561 | 732.9952 | 4
1189 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 18.2924 | 3.3201 | 181.5043 | 2
1190 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(70,120]-RHONDDA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 8.1734 | 2.8775 | 352.0531 | 3
1191 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 14.9489 | 2.8775 | 192.4867 | 2
1192 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-CENTRAL-POLYURETHANE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 2.8853 | 1.5494 | 537.0065 | 4
1193 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-CENTRAL-POLYURETHANE-(70,120]-CYNON-ABERDARE_HIRWAUN__PONSTICILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 4.3368 | 1.5494 | 357.2661 | 3
1194 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-CENTRAL-POLYURETHANE-(70,120]-PONTSTICILL_LOW_LEVEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 5.1028 | 1.5494 | 303.6348 | 3
1195 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-EASTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 41.8074 | 1.5494 | 37.0604 | 1
1196 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-EASTERN-EPOXY_RESIN-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 11.7602 | 4.8695 | 414.0692 | 3
1197 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-EASTERN-EPOXY_RESIN-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 7.6797 | 1.5494 | 201.7528 | 2
1198 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 12.8048 | 1.9921 | 155.5729 | 2
1199 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 14.8581 | 4.2055 | 283.0449 | 3
1200 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-BRECON_/_PORTIS-BRECON_BOREHOLES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 3.1321 | 1.5494 | 494.6909 | 3
1201 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 14.0843 | 2.8775 | 204.3031 | 2
1202 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 2.358 | 1.5494 | 657.0887 | 4
1203 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 5.6146 | 3.0988 | 551.9162 | 4
1204 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-WHITBOURNE-WHITBOURNE-WARRENWOOD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | FERROUS_1 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 4.4189 | 2.8775 | 651.1641 | 4
1205 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-EASTERN-POLYURETHANE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 7.3755 | 2.4348 | 330.114 | 3
1206 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-EASTERN-POLYURETHANE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 5.2726 | 1.7707 | 335.8389 | 3
1207 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-NORTHERN-EPOXY_RESIN-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_1 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 1.5862 | 1.7707 | 1116.3261 | 5
1208 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-NORTHERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 6.8324 | 1.9921 | 291.565 | 3
1209 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-ALWEN_/_DEE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 3.9297 | 1.7707 | 450.6038 | 3
1210 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 2.614 | 1.7707 | 677.4146 | 4
1211 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 6.0327 | 1.5494 | 256.833 | 3
1212 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-BRYN GWENALLT-CARMEL BOOSTER | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 0.86996 | 2.2134 | 2544.2914 | 5
1213 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-WESTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 27.9845 | 2.8775 | 102.8232 | 1
1214 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-WESTERN-EPOXY_RESIN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 6.7799 | 1.5494 | 228.5296 | 2
1215 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-WESTERN-EPOXY_RESIN-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 5.3977 | 1.9921 | 369.0619 | 3
1216 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 10.171 | 2.2134 | 217.6214 | 2
1217 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 16.2487 | 4.4269 | 272.4431 | 3
1218 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_1 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 6.1843 | 2.4348 | 393.7004 | 3
1219 | DIAM_LT_320-FERROUS_1-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRIDGEND__PORTHCAWL_FELINDRE__CRAY-NOTTAGE MAIN-FULMAR ROAD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_1 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 3.9957 | 2.2134 | 553.9466 | 4
1220 | DIAM_LT_320-FERROUS_2-<=320mm | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY | [6 empty] | 60.9489 | 1.5494 | 25.4213 | 1
1221 | DIAM_LT_320-FERROUS_2-<=320mm-B11_1950-1941_1960-WESTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 78.6264 | 2.2134 | 28.1512 | 1
1222 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | [6 empty] | 43.4313 | 1.7707 | 40.7711 | 1
1223 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-CENTRAL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 36.5938 | 1.7707 | 48.3891 | 1
1224 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-CENTRAL-CEMENT_MORTAR-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 14.034 | 1.5494 | 110.4033 | 1
1225 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(160,320]-PONTSTICILL_LOW_LEVEL-VALE_OF_GLAM__RHONDDA_VALLEYS-12 LLANILID OUTLET TDMA-AREA FED BY SUB SUPPLY SYSTEM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_2 | 1961_1980 | B13_1970 |  | <=320mm | (160,320] | 1.3837 | 2.2134 | 1599.6723 | 5
1226 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 34.3908 | 3.3201 | 96.5415 | 1
1227 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-CEMENT_MORTAR-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 5.7834 | 2.4348 | 420.9912 | 3
1228 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-CEMENT_MORTAR-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 3.8437 | 1.5494 | 403.0983 | 3
1229 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-CEMENT_MORTAR-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_2 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 6.6567 | 1.9921 | 299.2586 | 3
1230 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-EPOXY_RESIN-(120,160]-TALYBONT-ABERGAVENNY__CWMTILLERY-8116-CONFIRMED OUTSIDE OF SDMAS-PANT FARM OUTLET TO CROSS ASH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_2 | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 1.9173 | 1.7707 | 923.5602 | 4
1231 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-EPOXY_RESIN-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 13.9187 | 2.2134 | 159.0252 | 2
1232 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 17.5421 | 3.3201 | 189.2672 | 2
1233 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_2 | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 14.1993 | 2.2134 | 155.8824 | 2
1234 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(160,320] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1961_1980 | B13_1970 |  | <=320mm | (160,320] | 26.0128 | 1.7707 | 68.072 | 1
1235 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(160,320]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_2 | 1961_1980 | B13_1970 |  | <=320mm | (160,320] | 9.624 | 1.7707 | 183.9915 | 2
1236 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(160,320]-WHITBOURNE-WHITBOURNE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_2 | 1961_1980 | B13_1970 |  | <=320mm | (160,320] | 2.2664 | 2.4348 | 1074.2983 | 5
1237 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 41.4749 | 5.0909 | 122.7462 | 1
1238 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_2 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 8.4515 | 2.6561 | 314.277 | 3
1239 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_2 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 4.8547 | 1.9921 | 410.3388 | 3
1240 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN-THORNHILL-THORNHILL ROAD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_2 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 4.2817 | 3.0988 | 723.7335 | 4
1241 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_2 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 8.024 | 1.7707 | 220.6806 | 2
1242 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-WHITBOURNE-WHITBOURNE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_2 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 5.0619 | 1.5494 | 306.0919 | 3
1243 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-EASTERN-POLYURETHANE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 20.7452 | 1.5494 | 74.687 | 1
1244 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-NORTHERN-CEMENT_MORTAR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 45.4796 | 1.9921 | 43.8018 | 1
1245 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-NORTHERN-CEMENT_MORTAR-(160,320]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT VALLEY TRUNK-AREA FED BY S/SUPPLY 3SC20M18 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_2 | 1961_1980 | B13_1970 |  | <=320mm | (160,320] | 2.8543 | 1.9921 | 697.9238 | 4
1246 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-NORTHERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 20.0475 | 1.7707 | 88.3272 | 1
1247 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_2 | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 25.1317 | 2.2134 | 88.073 | 1
1248 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_2 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 31.2392 | 1.9921 | 63.7687 | 1
1249 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-WESTERN-CEMENT_MORTAR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 56.6301 | 2.6561 | 46.9028 | 1
1250 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-WESTERN-CEMENT_MORTAR-(160,320]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_2 | 1961_1980 | B13_1970 |  | <=320mm | (160,320] | 57.3505 | 1.5494 | 27.0163 | 1
1251 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 15.4688 | 2.4348 | 157.3986 | 2
1252 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(120,160]-PEMBROKESHIRE-PENDINE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_2 | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 7.0866 | 1.5494 | 218.6375 | 2
1253 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(160,320] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1961_1980 | B13_1970 |  | <=320mm | (160,320] | 43.5157 | 2.2134 | 50.8651 | 1
1254 | DIAM_LT_320-FERROUS_2-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 13.4444 | 2.2134 | 164.6359 | 2
1255 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1961_1980-CENTRAL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 37.2625 | 1.9921 | 53.4608 | 1
1256 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1961_1980-CENTRAL-CEMENT_MORTAR-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1961_1980 | B14_1980 |  | <=320mm | (70,120] | 66.866 | 2.6561 | 39.7229 | 1
1257 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1961_1980-EASTERN-CEMENT_MORTAR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 17.4504 | 1.5494 | 88.789 | 1
1258 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1961_1980-EASTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 11.2086 | 1.5494 | 138.2337 | 2
1259 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | [6 empty] | 58.3389 | 1.5494 | 26.5586 | 1
1260 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-CENTRAL-CEMENT_MORTAR-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1981_2000 | B14_1980 |  | <=320mm | (120,160] | 47.2749 | 1.9921 | 42.1383 | 1
1261 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-CENTRAL-CEMENT_MORTAR-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1981_2000 | B14_1980 |  | <=320mm | (70,120] | 46.2273 | 2.8775 | 62.2459 | 1
1262 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-CENTRAL-CEMENT_MORTAR-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_2 | 1981_2000 | B14_1980 |  | <=320mm | (70,120] | 95.509 | 3.9842 | 41.7151 | 1
1263 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-EASTERN-CEMENT_MORTAR-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1981_2000 | B14_1980 |  | <=320mm | (120,160] | 40.1473 | 3.3201 | 82.699 | 1
1264 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-EASTERN-CEMENT_MORTAR-(160,320] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1981_2000 | B14_1980 |  | <=320mm | (160,320] | 82.9268 | 2.6561 | 32.0296 | 1
1265 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-EASTERN-CEMENT_MORTAR-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1981_2000 | B14_1980 |  | <=320mm | (70,120] | 34.0614 | 2.4348 | 71.4818 | 1
1266 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-EASTERN-CEMENT_MORTAR-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_2 | 1981_2000 | B14_1980 |  | <=320mm | (70,120] | 27.2936 | 3.0988 | 113.5357 | 1
1267 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-EASTERN-CEMENT_MORTAR-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | FERROUS_2 | 1981_2000 | B14_1980 |  | <=320mm | (70,120] | 21.4018 | 2.2134 | 103.4226 | 1
1268 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-EASTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 77.0763 | 2.4348 | 31.5891 | 1
1269 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-NORTHERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 105.38 | 1.5494 | 14.703 | 1
1270 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-WESTERN-CEMENT_MORTAR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 61.5452 | 1.7707 | 28.7714 | 1
1271 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-WESTERN-CEMENT_MORTAR-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_2 | 1981_2000 | B14_1980 |  | <=320mm | (120,160] | 29.4948 | 3.3201 | 112.5669 | 1
1272 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-WESTERN-CEMENT_MORTAR-(120,160]-TYWI_C.U._AREA-DAFEN__FELINDRE-FRAMPTON OUTLET RED DMA-PRINCESS STREET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_2 | 1981_2000 | B14_1980 |  | <=320mm | (120,160] | 0.2621 | 1.9921 | 7600.3595 | 5
1273 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-WESTERN-CEMENT_MORTAR-(160,320]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_2 | 1981_2000 | B14_1980 |  | <=320mm | (160,320] | 55.0406 | 4.8695 | 88.4719 | 1
1274 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-WESTERN-CEMENT_MORTAR-(160,320]-TYWI_C.U._AREA-PENCOED__BRIDGEND_VALLEYS-CEFN HIRGOED TO LLANGEINOR-TYN-Y-WAUN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_2 | 1981_2000 | B14_1980 |  | <=320mm | (160,320] | 0.67383 | 1.5494 | 2299.4088 | 5
1275 | DIAM_LT_320-FERROUS_2-<=320mm-B14_1980-1981_2000-WESTERN-CEMENT_MORTAR-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | FERROUS_2 | 1981_2000 | B14_1980 |  | <=320mm | (70,120] | 26.332 | 2.4348 | 92.4644 | 1
1276 | DIAM_LT_320-FERROUS_2-<=320mm-B15_1990-1981_2000 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | [6 empty] | 222.9507 | 2.2134 | 9.9279 | 1
1277 | DIAM_LT_320-FERROUS_2-<=320mm-B15_1990-1981_2000-CENTRAL-CEMENT_MORTAR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 105.7431 | 1.9921 | 18.8389 | 1
1278 | DIAM_LT_320-FERROUS_2-<=320mm-B15_1990-1981_2000-CENTRAL-CEMENT_MORTAR-(160,320]-CYNON-PENDERYN__PONTSTICILL-RHIGOS VILLAGE 8IN & 10IN OUTLETS-HIRWAUN INDUSTRIAL ESTATE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | FERROUS_2 | 1981_2000 | B15_1990 |  | <=320mm | (160,320] | 2.06 | 3.7628 | 1826.6325 | 5
1279 | DIAM_LT_320-FERROUS_2-<=320mm-B15_1990-1981_2000-EASTERN-CEMENT_MORTAR-(160,320] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1981_2000 | B15_1990 |  | <=320mm | (160,320] | 56.4909 | 1.5494 | 27.4274 | 1
1280 | DIAM_LT_320-FERROUS_2-<=320mm-B15_1990-1981_2000-EASTERN-CEMENT_MORTAR-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1981_2000 | B15_1990 |  | <=320mm | (70,120] | 25.632 | 1.5494 | 60.4479 | 1
1281 | DIAM_LT_320-FERROUS_2-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1981_2000 | B15_1990 |  | <=320mm | (70,120] | 7.4889 | 1.9921 | 266.004 | 3
1282 | DIAM_LT_320-FERROUS_2-<=320mm-B15_1990-1981_2000-NORTHERN-CEMENT_MORTAR-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 1981_2000 | B15_1990 |  | <=320mm | (70,120] | 40.982 | 1.5494 | 37.8069 | 1
1283 | DIAM_LT_320-FERROUS_2-<=320mm-B15_1990-1981_2000-WESTERN-CEMENT_MORTAR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 183.5565 | 1.9921 | 10.8527 | 1
1284 | DIAM_LT_320-FERROUS_2-<=320mm-B16_2000-2001_2020 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | [6 empty] | 94.9469 | 2.6561 | 27.9747 | 1
1285 | DIAM_LT_320-FERROUS_2-<=320mm-B16_2000-2001_2020-CENTRAL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 47.5942 | 2.2134 | 46.5063 | 1
1286 | DIAM_LT_320-FERROUS_2-<=320mm-B16_2000-2001_2020-WESTERN-EPOXY_RESIN-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 2001_2020 | B16_2000 |  | <=320mm | (120,160] | 15.9136 | 1.9921 | 125.1809 | 2
1287 | DIAM_LT_320-FERROUS_2-<=320mm-B16_2000-2001_2020-WESTERN-EPOXY_RESIN-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | FERROUS_2 | 2001_2020 | B16_2000 |  | <=320mm | (70,120] | 14.6353 | 1.7707 | 120.991 | 1
1288 | DIAM_LT_320-FERROUS_2-<=320mm-B17_2010-2001_2020 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | [6 empty] | 46.5613 | 1.5494 | 33.2766 | 1
1289 | DIAM_LT_320-OTHER-<=320mm-B12_1960 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN | [6 empty] | 0.2377 | 1.5494 | 6518.2684 | 5
1290 | DIAM_LT_320-PLASTIC_PE-<=320mm | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY | [6 empty] | 39.1036 | 1.7707 | 45.2834 | 1
1291 | DIAM_LT_320-PLASTIC_PE-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 1961_1980 | B13_1970 |  | <=320mm | (0,70] | 17.6289 | 1.5494 | 87.8898 | 1
1292 | DIAM_LT_320-PLASTIC_PE-<=320mm-B14_1980-1981_2000 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | [6 empty] | 123.6303 | 3.0988 | 25.065 | 1
1293 | DIAM_LT_320-PLASTIC_PE-<=320mm-B14_1980-1981_2000-EASTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 1981_2000 | B14_1980 |  | <=320mm | (120,160] | 91.7673 | 2.4348 | 26.532 | 1
1294 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 63.2957 | 1.5494 | 24.4788 | 1
1295 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-CENTRAL-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 1981_2000 | B15_1990 |  | <=320mm | (120,160] | 71.502 | 1.7707 | 24.765 | 1
1296 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 1981_2000 | B15_1990 |  | <=320mm | (120,160] | 183.4648 | 2.4348 | 13.2711 | 1
1297 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-PENARTH__BARRY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PE | 1981_2000 | B15_1990 |  | <=320mm | (120,160] | 12.6912 | 1.5494 | 122.0845 | 1
1298 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-CENTRAL-NONE-(160,320] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 1981_2000 | B15_1990 |  | <=320mm | (160,320] | 55.4374 | 1.9921 | 35.934 | 1
1299 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 1981_2000 | B15_1990 |  | <=320mm | (70,120] | 30.8484 | 2.6561 | 86.1022 | 1
1300 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 1981_2000 | B15_1990 |  | <=320mm | (0,70] | 80.8626 | 2.2134 | 27.3727 | 1
1301 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 1981_2000 | B15_1990 |  | <=320mm | (120,160] | 219.959 | 3.0988 | 14.0881 | 1
1302 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 1981_2000 | B15_1990 |  | <=320mm | (120,160] | 73.9578 | 2.2134 | 29.9283 | 1
1303 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PE | 1981_2000 | B15_1990 |  | <=320mm | (120,160] | 38.5794 | 2.2134 | 57.3734 | 1
1304 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(120,160]-TALYBONT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 1981_2000 | B15_1990 |  | <=320mm | (120,160] | 16.9566 | 1.5494 | 91.3744 | 1
1305 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(120,160]-TALYBONT-ABERGAVENNY__CWMTILLERY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PE | 1981_2000 | B15_1990 |  | <=320mm | (120,160] | 107.8409 | 3.3201 | 30.7874 | 1
1306 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(160,320] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 1981_2000 | B15_1990 |  | <=320mm | (160,320] | 78.4374 | 2.2134 | 28.219 | 1
1307 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(160,320]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 1981_2000 | B15_1990 |  | <=320mm | (160,320] | 42.876 | 1.7707 | 41.2992 | 1
1308 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(160,320]-TALYBONT-ABERGAVENNY__CWMTILLERY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PE | 1981_2000 | B15_1990 |  | <=320mm | (160,320] | 24.8863 | 1.7707 | 71.1533 | 1
1309 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 1981_2000 | B15_1990 |  | <=320mm | (70,120] | 108.6284 | 3.7628 | 34.6394 | 1
1310 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 1981_2000 | B15_1990 |  | <=320mm | (70,120] | 93.8772 | 2.4348 | 25.9357 | 1
1311 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 1981_2000 | B15_1990 |  | <=320mm | (70,120] | 61.1432 | 3.0988 | 50.6811 | 1
1312 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-NORTHERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 272.8248 | 2.6561 | 9.7356 | 1
1313 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-NORTHERN-NONE-(160,320] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 1981_2000 | B15_1990 |  | <=320mm | (160,320] | 120.8574 | 1.7707 | 14.6515 | 1
1314 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 1981_2000 | B15_1990 |  | <=320mm | (70,120] | 103.6776 | 1.7707 | 17.0793 | 1
1315 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-NORTHERN-NONE-(70,120]-ALWEN_/_DEE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 1981_2000 | B15_1990 |  | <=320mm | (70,120] | 103.112 | 1.5494 | 15.0264 | 1
1316 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 139.651 | 1.5494 | 11.0948 | 1
1317 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-WESTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 1981_2000 | B15_1990 |  | <=320mm | (0,70] | 57.7485 | 1.5494 | 26.8301 | 1
1318 | DIAM_LT_320-PLASTIC_PE-<=320mm-B15_1990-1981_2000-WESTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 1981_2000 | B15_1990 |  | <=320mm | (120,160] | 97.016 | 1.7707 | 18.2521 | 1
1319 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN | [6 empty] | 63.6539 | 1.5494 | 24.341 | 1
1320 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 96.4789 | 2.6561 | 27.5305 | 1
1321 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 2001_2020 | B16_2000 |  | <=320mm | (120,160] | 31.9318 | 2.2134 | 69.3174 | 1
1322 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-CENTRAL-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 2001_2020 | B16_2000 |  | <=320mm | (70,120] | 57.8231 | 2.6561 | 45.9352 | 1
1323 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 2001_2020 | B16_2000 |  | <=320mm | (70,120] | 82.3161 | 3.3201 | 40.334 | 1
1324 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 2001_2020 | B16_2000 |  | <=320mm | (70,120] | 107.1434 | 2.6561 | 24.7903 | 1
1325 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-EASTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 2001_2020 | B16_2000 |  | <=320mm | (0,70] | 127.7897 | 2.6561 | 20.785 | 1
1326 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-EASTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 2001_2020 | B16_2000 |  | <=320mm | (120,160] | 200.9577 | 3.0988 | 15.4202 | 1
1327 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 2001_2020 | B16_2000 |  | <=320mm | (120,160] | 27.3571 | 1.7707 | 64.7269 | 1
1328 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-EASTERN-NONE-(160,320]-HEREFORD_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 2001_2020 | B16_2000 |  | <=320mm | (160,320] | 49.9136 | 1.5494 | 31.0416 | 1
1329 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 2001_2020 | B16_2000 |  | <=320mm | (70,120] | 318.6634 | 4.8695 | 15.2811 | 1
1330 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 2001_2020 | B16_2000 |  | <=320mm | (70,120] | 110.2674 | 1.7707 | 16.0586 | 1
1331 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PE | 2001_2020 | B16_2000 |  | <=320mm | (70,120] | 139.885 | 1.7707 | 12.6586 | 1
1332 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 2001_2020 | B16_2000 |  | <=320mm | (70,120] | 88.6929 | 2.6561 | 29.9473 | 1
1333 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PE | 2001_2020 | B16_2000 |  | <=320mm | (70,120] | 115.4523 | 3.5415 | 30.6749 | 1
1334 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-CROSS ASH-CROSS ASH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PE | 2001_2020 | B16_2000 |  | <=320mm | (70,120] | 9.2551 | 1.7707 | 191.3261 | 2
1335 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-NORTHERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 209.9392 | 1.9921 | 9.4889 | 1
1336 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 2001_2020 | B16_2000 |  | <=320mm | (70,120] | 280.7902 | 2.8775 | 10.2477 | 1
1337 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 141.262 | 2.4348 | 17.2359 | 1
1338 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 2001_2020 | B16_2000 |  | <=320mm | (0,70] | 32.1731 | 1.5494 | 48.1582 | 1
1339 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-WESTERN-NONE-(0,70]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 2001_2020 | B16_2000 |  | <=320mm | (0,70] | 51.0261 | 2.4348 | 47.7162 | 1
1340 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-WESTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 2001_2020 | B16_2000 |  | <=320mm | (120,160] | 174.1763 | 2.8775 | 16.5204 | 1
1341 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-WESTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 2001_2020 | B16_2000 |  | <=320mm | (70,120] | 113.3497 | 1.5494 | 13.6692 | 1
1342 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PE | 2001_2020 | B16_2000 |  | <=320mm | (70,120] | 91.4897 | 1.5494 | 16.9352 | 1
1343 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PE | 2001_2020 | B16_2000 |  | <=320mm | (70,120] | 249.1136 | 2.8775 | 11.5508 | 1
1344 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PRESELI_SUPPLY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PE | 2001_2020 | B16_2000 |  | <=320mm | (70,120] | 88.3699 | 1.9921 | 22.5426 | 1
1345 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 2001_2020 | B16_2000 |  | <=320mm | (70,120] | 346.2703 | 5.5336 | 15.9805 | 1
1346 | DIAM_LT_320-PLASTIC_PE-<=320mm-B16_2000-2001_2020-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PE | 2001_2020 | B16_2000 |  | <=320mm | (70,120] | 144.8952 | 2.4348 | 16.8037 | 1
1347 | DIAM_LT_320-PLASTIC_PE-<=320mm-B17_2010-2001_2020 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | [6 empty] | 194.9268 | 1.9921 | 10.2197 | 1
1348 | DIAM_LT_320-PLASTIC_PE-<=320mm-B17_2010-2001_2020-CENTRAL-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 2001_2020 | B17_2010 |  | <=320mm | (70,120] | 75.5908 | 1.5494 | 20.4972 | 1
1349 | DIAM_LT_320-PLASTIC_PE-<=320mm-B17_2010-2001_2020-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 2001_2020 | B17_2010 |  | <=320mm | (70,120] | 188.6442 | 3.3201 | 17.6 | 1
1350 | DIAM_LT_320-PLASTIC_PE-<=320mm-B17_2010-2001_2020-NORTHERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 85.9106 | 1.5494 | 18.035 | 1
1351 | DIAM_LT_320-PLASTIC_PE-<=320mm-B17_2010-2001_2020-NORTHERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 2001_2020 | B17_2010 |  | <=320mm | (0,70] | 85.348 | 2.6561 | 31.121 | 1
1352 | DIAM_LT_320-PLASTIC_PE-<=320mm-B17_2010-2001_2020-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 2001_2020 | B17_2010 |  | <=320mm | (70,120] | 184.693 | 1.5494 | 8.3891 | 1
1353 | DIAM_LT_320-PLASTIC_PE-<=320mm-B17_2010-2001_2020-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 156.5133 | 1.9921 | 12.7279 | 1
1354 | DIAM_LT_320-PLASTIC_PE-<=320mm-B17_2010-2001_2020-WESTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PE | 2001_2020 | B17_2010 |  | <=320mm | (70,120] | 119.965 | 1.7707 | 14.7605 | 1
1355 | DIAM_LT_320-PLASTIC_PE-<=320mm-B17_2010-2001_2020-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PE | 2001_2020 | B17_2010 |  | <=320mm | (70,120] | 119.6338 | 1.9921 | 16.6515 | 1
1356 | DIAM_LT_320-PLASTIC_PVC-<=320mm | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY | [6 empty] | 30.0647 | 1.9921 | 66.26 | 1
1357 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1921_1940 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | [6 empty] | 8.8888 | 1.5494 | 174.3091 | 2
1358 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1921_1940-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 6.9357 | 1.5494 | 223.3936 | 2
1359 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 18.8064 | 1.9921 | 105.9259 | 1
1360 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1921_1940-WESTERN-NONE-(70,120]-PEMBROKESHIRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1921_1940 | B10_1940 |  | <=320mm | (70,120] | 15.7861 | 1.5494 | 98.1497 | 1
1361 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | [6 empty] | 12.5951 | 2.6561 | 210.8844 | 2
1362 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 5.7288 | 2.2134 | 386.3703 | 3
1363 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 45.9958 | 3.7628 | 81.8082 | 1
1364 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1941_1960 | B10_1940 |  | <=320mm | (0,70] | 6.3373 | 1.5494 | 244.4877 | 2
1365 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-BETTWS LLANGYBI AND LLANDDEWI BREFI-BETTWS BLEDRWS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1941_1960 | B10_1940 |  | <=320mm | (0,70] | 0.56634 | 3.0988 | 5471.6476 | 5
1366 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(0,70]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1941_1960 | B10_1940 |  | <=320mm | (0,70] | 5.9911 | 1.5494 | 258.6158 | 3
1367 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(120,160]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1941_1960 | B10_1940 |  | <=320mm | (120,160] | 15.5997 | 3.0988 | 198.6448 | 2
1368 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(120,160]-PEMBROKESHIRE-BOLTON_HILL-PLUMSTONE TO BRAWDY-CUFFERN/SIMPSON CROSS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1941_1960 | B10_1940 |  | <=320mm | (120,160] | 5.4483 | 1.7707 | 325.0063 | 3
1369 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(120,160]-PEMBROKESHIRE-BOLTON_HILL-ROSEPOOL-ROSEPOOL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1941_1960 | B10_1940 |  | <=320mm | (120,160] | 1.3797 | 2.2134 | 1604.2315 | 5
1370 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(120,160]-PEMBROKESHIRE-PRESELI_SUPPLY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1941_1960 | B10_1940 |  | <=320mm | (120,160] | 4.7199 | 2.2134 | 468.9613 | 3
1371 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1941_1960 | B10_1940 |  | <=320mm | (120,160] | 22.3889 | 2.8775 | 128.5219 | 2
1372 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 23.4716 | 1.7707 | 75.4421 | 1
1373 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 14.4671 | 1.5494 | 107.0984 | 1
1374 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 52.5275 | 2.2134 | 42.1385 | 1
1375 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PENDINE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 10.5321 | 1.7707 | 168.1275 | 2
1376 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PRESELI_SUPPLY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 19.841 | 1.5494 | 78.0907 | 1
1377 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B10_1940-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1941_1960 | B10_1940 |  | <=320mm | (70,120] | 70.404 | 6.6403 | 94.3169 | 1
1378 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | [6 empty] | 21.1322 | 1.7707 | 83.7935 | 1
1379 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 5.1008 | 1.7707 | 347.1524 | 3
1380 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-CENTRAL-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 8.0783 | 1.5494 | 191.7979 | 2
1381 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 13.2676 | 1.5494 | 116.7806 | 1
1382 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-ELAN_/_BUILTH-ELAN-NEUADD NORTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | PLASTIC_PVC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 8.2851 | 2.8775 | 347.3032 | 3
1383 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-PILLETH-PILLETH_KNIGHTON__BLEDDFA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 2.5068 | 1.7707 | 706.3668 | 4
1384 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-MALPAS__CAERLEON__CWMBRAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 5.1041 | 1.7707 | 346.9227 | 3
1385 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-EASTERN-NONE-(70,120]-TALYBONT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 6.8251 | 1.5494 | 227.0147 | 2
1386 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(120,160]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-GOSEN TYN Y FRITH-GOSEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1941_1960 | B11_1950 |  | <=320mm | (120,160] | 3.1016 | 1.5494 | 499.5492 | 3
1387 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 13.5675 | 1.5494 | 114.1997 | 1
1388 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-GOSEN TYN Y FRITH-GOSEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 5.8745 | 1.5494 | 263.7509 | 3
1389 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 14.7815 | 2.8775 | 194.666 | 2
1390 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-PENWCH SERVICE RES OUTLET-BETHANIA TREFENTER | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1941_1960 | B11_1950 |  | <=320mm | (0,70] | 4.3223 | 1.7707 | 409.6738 | 3
1391 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 32.8094 | 3.7628 | 114.6875 | 1
1392 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-BETTWS LLANGYBI AND LLANDDEWI BREFI-LANGYBI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 6.2494 | 1.7707 | 283.3476 | 3
1393 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-PENWCH SERVICE RES OUTLET-BETHANIA TREFENTER | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 13.1197 | 3.0988 | 236.1947 | 2
1394 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAPEL_DEWI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 6.9042 | 1.9921 | 288.5319 | 3
1395 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1941_1960 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | [6 empty] | 15.8616 | 2.6561 | 167.4561 | 2
1396 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 8.0391 | 1.7707 | 220.266 | 2
1397 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 3.9506 | 1.7707 | 448.2204 | 3
1398 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1941_1960-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH-STUMPY EAST NO. 2 OUTLET-HOLTON ROAD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 1.3918 | 1.7707 | 1272.2309 | 5
1399 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1941_1960-EASTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 21.2245 | 1.5494 | 73.0006 | 1
1400 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1941_1960-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 11.9868 | 1.7707 | 147.7249 | 2
1401 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1941_1960-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 16.3005 | 2.2134 | 135.7889 | 2
1402 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(120,160]-PEMBROKESHIRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1941_1960 | B12_1960 |  | <=320mm | (120,160] | 24.0017 | 1.7707 | 73.7758 | 1
1403 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 62.8585 | 3.0988 | 49.298 | 1
1404 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(70,120]-PEMBROKESHIRE-PENDINE-CROSSHANDS RES OUTLETS-X HANDS RES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 26.252 | 3.5415 | 134.9034 | 2
1405 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1941_1960-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAPEL_DEWI-MAENIEUAN OUTLETS-MADOX TO TRELECH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1941_1960 | B12_1960 |  | <=320mm | (70,120] | 12.0307 | 1.5494 | 128.7871 | 2
1406 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 9.5619 | 1.7707 | 185.1873 | 2
1407 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 2.9316 | 1.5494 | 528.5137 | 4
1408 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 6.4101 | 1.7707 | 276.2442 | 3
1409 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__RUMNEY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 4.423 | 1.9921 | 450.396 | 3
1410 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_BAY__RUMNEY-LLANRUMNEY AVENUE-NEWPORT ROAD RUMNEY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 0.42346 | 1.5494 | 3658.9123 | 5
1411 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_EAST-COED Y GORAS-COED Y GORES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 1.8704 | 2.4348 | 1301.7321 | 5
1412 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_EAST-TY DRAW ROAD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 4.4997 | 1.7707 | 393.5234 | 3
1413 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_HEATH_&_LLANISHEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 8.0149 | 3.3201 | 414.2483 | 3
1414 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 16.5119 | 3.3201 | 201.0756 | 2
1415 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_EAST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 14.3902 | 1.7707 | 123.0522 | 1
1416 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_EAST-COED Y GORAS-COED Y GORES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 3.0327 | 1.9921 | 656.8689 | 4
1417 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_EAST-NORTH PENTWYN SOUTH-NORTH PENTWYN SOUTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 4.116 | 1.5494 | 376.436 | 3
1418 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 4.1785 | 1.9921 | 476.7499 | 3
1419 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_HEATH_&_LLANISHEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 9.5279 | 2.8775 | 302.0037 | 3
1420 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_HEATH_&_LLANISHEN-WERN GOCH ROAD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 8.6009 | 2.2134 | 257.3472 | 3
1421 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 11.6198 | 2.6561 | 228.5857 | 2
1422 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 31.7224 | 1.7707 | 55.82 | 1
1423 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(0,70]-TALYBONT-ABERGAVENNY__CWMTILLERY-PONTYPOOL TDMA-AREA FED BY SUB SUPPLY SYSTEM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (0,70] | 2.7064 | 3.7628 | 1390.3393 | 5
1424 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(120,160]-TALYBONT-ABERGAVENNY__CWMTILLERY-BUNKERS-HILLSIDE NO.1 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 1.2101 | 1.5494 | 1280.4375 | 5
1425 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(120,160]-WHITBOURNE-WHITBOURNE-LEYSTERS 8INCH-POLE FARM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 0.88762 | 1.7707 | 1994.9435 | 5
1426 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 54.8185 | 5.9763 | 109.0189 | 1
1427 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-ELAN_/_BUILTH-BUILTH-BUILTH WELLS-BUILTH TO ABERDW | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 7.6629 | 3.0988 | 404.3878 | 3
1428 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-ELAN_/_BUILTH-ELAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 13.0607 | 1.5494 | 118.6311 | 1
1429 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 8.6012 | 1.9921 | 231.6057 | 2
1430 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL-WEOBLEY NORTH-DILWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 1.2778 | 1.9921 | 1559.0283 | 5
1431 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__SOUTH_BROOMY_HILL_ | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 11.5111 | 1.5494 | 134.6009 | 2
1432 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CHEPSTOW__CALDICOT_COURT_FARM | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 11.3218 | 1.7707 | 156.4009 | 2
1433 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_SW__RISCA__ABERCARN-RHIWDERIN TO DUFFRYN SR OUT TDMA-RHIWDERIN TO DUFFRYN S.R. | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 1.6884 | 2.4348 | 1442.0822 | 5
1434 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-CEFN PENDEGAR REDUCED DMA-CEFN PENDEGAR | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 2.7659 | 2.6561 | 960.3169 | 4
1435 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-CROSS ASH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 6.9629 | 1.5494 | 222.5226 | 2
1436 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-USK MARKET ST AND DAVINGTON HOUSE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 2.9089 | 1.9921 | 684.8327 | 4
1437 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-USK MARKET ST AND DAVINGTON HOUSE-GWERNESNEY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 5.1911 | 3.3201 | 639.5896 | 4
1438 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (0,70] | 20.0599 | 1.9921 | 99.3066 | 1
1439 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 16.0013 | 1.7707 | 110.6623 | 1
1440 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(120,160]-NORTH_ERYRI_/_YNYS_MON-EAST_ANGLESEY_CEFNI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 16.5842 | 1.9921 | 120.1196 | 1
1441 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(160,320]-NORTH_ERYRI_/_YNYS_MON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (160,320] | 3.9993 | 1.5494 | 387.4169 | 3
1442 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 33.5952 | 2.8775 | 85.6508 | 1
1443 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-CLWYD_COASTAL-ABERGELE__RHYL_GLASCOED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 23.6503 | 1.9921 | 84.2309 | 1
1444 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-CLWYD_COASTAL-PRESTATYN_GLASCOED__TRECASTELL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 13.7104 | 1.7707 | 129.1537 | 2
1445 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-EAST_ANGLESEY_CEFNI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 41.7554 | 2.6561 | 63.6113 | 1
1446 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 39.1894 | 1.5494 | 39.5361 | 1
1447 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW-COEDEN TO LLANFAETHLU-RHYDWYN BOOSTER | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 3.5318 | 2.4348 | 689.3812 | 4
1448 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 15.9112 | 1.9921 | 125.1998 | 2
1449 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (0,70] | 8.8769 | 1.5494 | 174.5434 | 2
1450 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(120,160]-PEMBROKESHIRE-BOLTON_HILL-BRAWDY ST DAVIDS-ST DAVIDS LOW PRES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (120,160] | 2.0577 | 1.9921 | 968.1347 | 4
1451 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-HAFOD LLECHRYD-LECHRYD VILLIAGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 3.115 | 2.4348 | 781.64 | 4
1452 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 16.8454 | 2.2134 | 131.3968 | 2
1453 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 51.9944 | 3.7628 | 72.3698 | 1
1454 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B12_1960-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAPEL_DEWI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B12_1960 |  | <=320mm | (70,120] | 17.595 | 2.6561 | 150.9586 | 2
1455 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 8.477 | 1.7707 | 208.8887 | 2
1456 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 8.8347 | 2.4348 | 275.5921 | 3
1457 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON-PENARTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 2.3452 | 2.2134 | 943.8199 | 4
1458 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 8.096 | 2.2134 | 273.3966 | 3
1459 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_ELY__RADYR__LLANDAFF | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 12.885 | 2.4348 | 188.9613 | 2
1460 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-PENARTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 10.42 | 1.7707 | 169.9366 | 2
1461 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(0,70]-PONTSTICILL_HIGH_LEVEL/HEADS_O-RASSAU__SIRHOWY_VALLEY-TY FRY SR-TY FRY OUTLET TO BLACKWOOD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (0,70] | 0.17062 | 1.7707 | 10378.2153 | 5
1462 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 17.4756 | 3.3201 | 189.9874 | 2
1463 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(120,160]-HEREFORD_C.U._AREA-HEREFORD__SOUTH_BROOMY_HILL_ | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 6.7581 | 2.4348 | 360.2722 | 3
1464 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(120,160]-VOWCHURCH-VOWCHURCH-KINGSTONE SR-CLEHONGER | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 2.6616 | 1.5494 | 582.1293 | 4
1465 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(160,320]-BRECON_/_PORTIS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (160,320] | 1.375 | 1.7707 | 1287.8129 | 5
1466 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(160,320]-ELAN_/_BUILTH-ELAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (160,320] | 3.5806 | 1.5494 | 432.7235 | 3
1467 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 39.8578 | 3.3201 | 83.2996 | 1
1468 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-ELAN_/_BUILTH-ELAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 27.6563 | 1.5494 | 56.0234 | 1
1469 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-ELAN_/_BUILTH-ELAN-ELAN-BWLCH-Y-SARNAU S.R. | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 1.82 | 1.5494 | 851.3004 | 4
1470 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-ELAN_/_BUILTH-ELAN-NEUADD SOUTH-HOWEY-BUILTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 3.5676 | 1.7707 | 496.3448 | 3
1471 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 24.0168 | 1.5494 | 64.5132 | 1
1472 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 13.2373 | 1.7707 | 133.7696 | 2
1473 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-LLYSWEN-LLYSWEN-HAY ON WYE-DORSTONE OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 1.3618 | 1.5494 | 1137.7857 | 5
1474 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-LLYSWEN-LLYSWEN-LLYSWEN TO LLANSTEPHAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 17.7308 | 2.2134 | 124.835 | 1
1475 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-PILLETH-PILLETH_KNIGHTON__BLEDDFA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 10.258 | 2.2134 | 215.7759 | 2
1476 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-PILLETH-PILLETH_KNIGHTON__BLEDDFA-BEGGARS BUSH TO KNOWLE HILL TDMA-KINNERTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 5.4534 | 3.9842 | 730.5888 | 4
1477 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-PILLETH-PILLETH_KNIGHTON__BLEDDFA-WHITTON BEGGARS BUSH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 13.9832 | 2.4348 | 174.1207 | 2
1478 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-PILLETH-PILLETH_KNIGHTON__BLEDDFA-WOODHOUSE-KNIGHTON-KNUCKLAS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 1.5122 | 1.7707 | 1170.9565 | 5
1479 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-TALYBONT-ABERGAVENNY__CWMTILLERY-USK MARKET ST AND DAVINGTON HOUSE-LLANDENNY MAIN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 2.7708 | 2.2134 | 798.8361 | 4
1480 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-WHITBOURNE-WHITBOURNE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 14.4172 | 1.9921 | 138.1739 | 2
1481 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-EASTERN-NONE-(70,120]-WHITBOURNE-WHITBOURNE-WARRENWOOD-STOKE LACY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 11.9691 | 1.7707 | 147.943 | 2
1482 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(0,70] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (0,70] | 35.262 | 2.4348 | 69.0479 | 1
1483 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(0,70]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (0,70] | 27.9716 | 1.9921 | 71.2181 | 1
1484 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(0,70]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-CERRIG-BRYN GLAS SRV O/LET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (0,70] | 3.0293 | 1.5494 | 511.4788 | 4
1485 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(0,70]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-COWLYD CWT & GORSWEN MINOR-EGLWYSBACH 85 LLYN CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (0,70] | 1.8691 | 3.0988 | 1657.9436 | 5
1486 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 29.4033 | 3.5415 | 120.4453 | 1
1487 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 13.5904 | 2.2134 | 162.8665 | 2
1488 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160]-LLEYNHARLECH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 7.6377 | 1.5494 | 202.8633 | 2
1489 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(120,160]-NORTH_ERYRI_/_YNYS_MON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 30.3214 | 1.9921 | 65.6991 | 1
1490 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(160,320] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (160,320] | 8.9367 | 2.4348 | 272.447 | 3
1491 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(160,320]-ALWEN_/_DEE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (160,320] | 7.3981 | 2.4348 | 329.1063 | 3
1492 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(160,320]-ALWEN_/_DEE-DENBIGH_ALWEN-MEIFOD-1104 FOELAS (G10) | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (160,320] | 3.1007 | 1.7707 | 571.0806 | 4
1493 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(160,320]-ALWEN_/_DEE-FLINT__CONNAHS_QUAY_BRETTON-ASTON 9 INCH-ASTON FROM PLOUGHINN. | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (160,320] | 0.807 | 1.9921 | 2468.5083 | 5
1494 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(160,320]-ALWEN_/_DEE-FLINT__CONNAHS_QUAY_BRETTON-HAWARDEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (160,320] | 3.2616 | 2.2134 | 678.628 | 4
1495 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(160,320]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (160,320] | 15.9202 | 1.9921 | 125.129 | 2
1496 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(160,320]-NORTH_ERYRI_/_YNYS_MON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (160,320] | 4.0195 | 1.9921 | 495.6052 | 3
1497 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(160,320]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (160,320] | 10.8497 | 1.9921 | 183.6072 | 2
1498 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 29.5693 | 2.4348 | 82.3411 | 1
1499 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 39.6473 | 1.5494 | 39.0796 | 1
1500 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN-ALWEN TO BWLCH TRUNK | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 5.4803 | 1.5494 | 282.7223 | 3
1501 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 22.8349 | 2.4348 | 106.6251 | 1
1502 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-BLAENAU_FFESTINIOG-BLAENAU_GARREGLWYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 16.1228 | 1.5494 | 96.0999 | 1
1503 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-CLWYD_COASTAL-ABERGELE__RHYL_GLASCOED | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 46.7691 | 1.9921 | 42.594 | 1
1504 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-CLWYD_COASTAL-PRESTATYN_GLASCOED__TRECASTELL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 11.4741 | 1.7707 | 154.3258 | 2
1505 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-CLWYD_COASTAL-PRESTATYN_GLASCOED__TRECASTELL-DYSERTH-0805 DYSERTHGRAVITY (R80) | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 0.75678 | 1.5494 | 2047.3531 | 5
1506 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 20.164 | 1.9921 | 98.7942 | 1
1507 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-CERRIG | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 4.0995 | 1.5494 | 377.9448 | 3
1508 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-LLYSFAEN-0059 BRYN Y PIN(R00) | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 10.1042 | 1.9921 | 197.1547 | 2
1509 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 17.4503 | 1.9921 | 114.1575 | 1
1510 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-LLEYNHARLECH-LLEYN_CWMYSTRADLLYN-PENRHYNDEUDRAETH-PENRHYD LLANFROTHEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 0.82214 | 1.7707 | 2153.8166 | 5
1511 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 30.3623 | 1.9921 | 65.6105 | 1
1512 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-EAST_ANGLESEY_CEFNI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 37.6667 | 1.5494 | 41.1345 | 1
1513 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON-NORTH_ANGLESEY_ALAW | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 52.6369 | 2.4348 | 46.2559 | 1
1514 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-NORTHERN-NONE-(70,120]-SOUTH_MEIRIONNYDD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 11.9533 | 1.9921 | 166.6556 | 2
1515 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 36.6301 | 2.2134 | 60.4265 | 1
1516 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(0,70]-MID_-_SOUTH_CEREDIGION-LLECHRYD-SYNOD INN LLANARTH-LLANARTH TO ABERAERON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (0,70] | 1.1288 | 2.2134 | 1960.9357 | 5
1517 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(0,70]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (0,70] | 9.5909 | 1.5494 | 161.5486 | 2
1518 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 12.3438 | 1.9921 | 161.3829 | 2
1519 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(120,160]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 21.5387 | 3.0988 | 143.871 | 2
1520 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(120,160]-PEMBROKESHIRE-BOLTON_HILL-BRAWDY ST DAVIDS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 1.7547 | 1.9921 | 1135.2948 | 5
1521 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(120,160]-PEMBROKESHIRE-BOLTON_HILL-TEMPLETON TO MARTLETWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 4.8237 | 1.5494 | 321.2042 | 3
1522 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 25.5916 | 4.2055 | 164.3317 | 2
1523 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-CAPEL_DEWI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 4.1435 | 1.5494 | 373.9372 | 3
1524 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-CAPEL_DEWI-EBENEZER SR OUTLETS-FOEL RES TO EBENEEZER RES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 1.2998 | 1.5494 | 1192.0272 | 5
1525 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(120,160]-TYWI_C.U._AREA-CAPEL_DEWI-FOEL TO MAENIEUAN-FOEL RES TALOG-ABERNANT | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (120,160] | 3.0796 | 2.6561 | 862.4927 | 4
1526 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(160,320]-TYWI_C.U._AREA-CAPEL_DEWI-PENLLAIN TO NIMPWLL-PENLLAIN RES TO NIMPWLL RES | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (160,320] | 4.7147 | 3.0988 | 657.27 | 4
1527 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 40.5141 | 4.8695 | 120.1938 | 1
1528 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD-CROSSROADS TO CRUGIAU AND TREGAMMON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 23.8648 | 2.4348 | 102.0236 | 1
1529 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 38.0996 | 2.2134 | 58.0958 | 1
1530 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-STRATA_FLORIDA-MAESTIR TO BRYNGARREG-BRYNCARREG RES OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 13.9386 | 2.8775 | 206.438 | 2
1531 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-NORTH_CEREDIGION-BONTGOCH_SUPPLY_NOT_ABERYSTWYTH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 26.7185 | 2.6561 | 99.411 | 1
1532 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 27.5234 | 2.2134 | 80.42 | 1
1533 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-PEMBROKESHIRE-BOLTON_HILL-TEMPLETON TO MARTLETWY | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 9.8366 | 1.7707 | 180.0159 | 2
1534 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 37.6847 | 3.0988 | 82.2296 | 1
1535 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 16.2038 | 1.7707 | 109.2794 | 1
1536 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAERAU__YSTRADFELLTE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 15.3355 | 1.5494 | 101.0335 | 1
1537 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAPEL_DEWI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 33.3032 | 2.6561 | 79.7555 | 1
1538 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAPEL_DEWI-FOEL TO MAENIEUAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 9.0296 | 1.5494 | 171.5908 | 2
1539 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAPEL_DEWI-STONECUTTER TALOG ABERNANT-ABERNANT BPT OUTLET | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 7.1855 | 2.8775 | 400.4529 | 3
1540 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CRAY__CLYDACH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 16.9479 | 3.0988 | 182.8421 | 2
1541 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-DAFEN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 14.6098 | 1.7707 | 121.202 | 1
1542 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-LLANELLI_FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 11.7282 | 1.7707 | 150.9819 | 2
1543 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B13_1970-1961_1980-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-SKETTY__GOWER_BRYNGWYN__FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B13_1970 |  | <=320mm | (70,120] | 29.5487 | 1.9921 | 67.417 | 1
1544 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN | [6 empty] | 35.3402 | 1.9921 | 56.3688 | 1
1545 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_EAST | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1961_1980 | B14_1980 |  | <=320mm | (70,120] | 5.1021 | 1.7707 | 347.0627 | 3
1546 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1961_1980-CENTRAL-NONE-(70,120]-SLUVAD__COURT_FARM__LLWYNON-CARDIFF_HEATH_&_LLANISHEN-UPPER AND LOWER GRAIG | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | PLASTIC_PVC | 1961_1980 | B14_1980 |  | <=320mm | (70,120] | 5.9732 | 1.5494 | 259.3928 | 3
1547 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1961_1980-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1961_1980 | B14_1980 |  | <=320mm | (70,120] | 7.3203 | 1.9921 | 272.1329 | 3
1548 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1961_1980-NORTHERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 25.6375 | 2.4348 | 94.969 | 1
1549 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1961_1980-NORTHERN-NONE-(0,70]-DYFFRYN_CONWY-COWLYD__LLYN_CONWY-LLYN CONWY MINOR-NEBO RES 0/LET CAPEL GARMON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | PLASTIC_PVC | 1961_1980 | B14_1980 |  | <=320mm | (0,70] | 0.62926 | 1.9921 | 3165.758 | 5
1550 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1961_1980-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1961_1980 | B14_1980 |  | <=320mm | (70,120] | 41.7981 | 1.5494 | 37.0686 | 1
1551 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1961_1980-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 20.7475 | 1.5494 | 74.6789 | 1
1552 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1981_2000-CENTRAL-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 7.3987 | 1.9921 | 269.2498 | 3
1553 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1981_2000-EASTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1981_2000 | B14_1980 |  | <=320mm | (120,160] | 7.3019 | 1.9921 | 272.8176 | 3
1554 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1981_2000-NORTHERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 59.0725 | 1.9921 | 33.7227 | 1
1555 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1981_2000-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1981_2000 | B14_1980 |  | <=320mm | (70,120] | 68.6514 | 5.5336 | 80.6039 | 1
1556 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1981_2000-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-DENBIGH_ALWEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1981_2000 | B14_1980 |  | <=320mm | (70,120] | 35.3496 | 1.5494 | 43.8308 | 1
1557 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1981_2000-NORTHERN-NONE-(70,120]-ALWEN_/_DEE-HOLYWELL__MOLD_ALWEN__BRETTON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1981_2000 | B14_1980 |  | <=320mm | (70,120] | 21.2098 | 1.7707 | 83.4869 | 1
1558 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1981_2000-NORTHERN-NONE-(70,120]-NORTH_ERYRI_/_YNYS_MON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1981_2000 | B14_1980 |  | <=320mm | (70,120] | 53.5777 | 3.0988 | 57.8375 | 1
1559 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1981_2000-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 52.3607 | 1.5494 | 29.5909 | 1
1560 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1981_2000-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1981_2000 | B14_1980 |  | <=320mm | (120,160] | 59.1171 | 2.4348 | 41.1856 | 1
1561 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1981_2000-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1981_2000 | B14_1980 |  | <=320mm | (70,120] | 163.0006 | 6.4189 | 39.3799 | 1
1562 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B14_1980-1981_2000-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1981_2000 | B14_1980 |  | <=320mm | (70,120] | 49.0382 | 2.4348 | 49.6505 | 1
1563 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | [6 empty] | 45.0118 | 1.7707 | 39.3395 | 1
1564 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-CENTRAL-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1981_2000 | B15_1990 |  | <=320mm | (120,160] | 47.0148 | 1.5494 | 32.9556 | 1
1565 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-CENTRAL-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1981_2000 | B15_1990 |  | <=320mm | (70,120] | 69.9955 | 2.2134 | 31.6225 | 1
1566 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-CENTRAL-NONE-(70,120]-CYNON-ABERDARE_HIRWAUN__PONSTICILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1981_2000 | B15_1990 |  | <=320mm | (70,120] | 14.5531 | 1.5494 | 106.4653 | 1
1567 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-CENTRAL-NONE-(70,120]-PONTSTICILL_LOW_LEVEL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1981_2000 | B15_1990 |  | <=320mm | (70,120] | 25.992 | 1.9921 | 76.6422 | 1
1568 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1981_2000 | B15_1990 |  | <=320mm | (120,160] | 75.2 | 1.7707 | 23.5471 | 1
1569 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1981_2000 | B15_1990 |  | <=320mm | (70,120] | 116.0447 | 4.6482 | 40.0553 | 1
1570 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-EASTERN-NONE-(70,120]-HEREFORD_C.U._AREA-HEREFORD__NORTH__BROOMY_HILL | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1981_2000 | B15_1990 |  | <=320mm | (70,120] | 21.2558 | 1.5494 | 72.8932 | 1
1571 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-NORTHERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 41.9468 | 1.7707 | 42.214 | 1
1572 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-NORTHERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1981_2000 | B15_1990 |  | <=320mm | (70,120] | 145.3049 | 3.7628 | 25.8961 | 1
1573 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 91.3193 | 1.5494 | 16.9668 | 1
1574 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-WESTERN-NONE-(120,160]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1981_2000 | B15_1990 |  | <=320mm | (120,160] | 96.6922 | 2.4348 | 25.1806 | 1
1575 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-WESTERN-NONE-(70,120] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | PLASTIC_PVC | 1981_2000 | B15_1990 |  | <=320mm | (70,120] | 176.8226 | 3.7628 | 21.2802 | 1
1576 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-WESTERN-NONE-(70,120]-MID_-_SOUTH_CEREDIGION-LLECHRYD | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1981_2000 | B15_1990 |  | <=320mm | (70,120] | 65.5636 | 1.7707 | 27.008 | 1
1577 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-WESTERN-NONE-(70,120]-TYWI_C.U._AREA | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | PLASTIC_PVC | 1981_2000 | B15_1990 |  | <=320mm | (70,120] | 146.601 | 3.3201 | 22.6475 | 1
1578 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-BRYNGWYN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1981_2000 | B15_1990 |  | <=320mm | (70,120] | 58.8033 | 1.5494 | 26.3488 | 1
1579 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CAPEL_DEWI | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1981_2000 | B15_1990 |  | <=320mm | (70,120] | 76.9935 | 2.4348 | 31.6231 | 1
1580 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CRAY__CLYDACH | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1981_2000 | B15_1990 |  | <=320mm | (70,120] | 40.5199 | 3.3201 | 81.9386 | 1
1581 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-CRAY__CLYDACH-CAEHOPKIN AND PENYCAE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | PLASTIC_PVC | 1981_2000 | B15_1990 |  | <=320mm | (70,120] | 4.6082 | 1.5494 | 336.2233 | 3
1582 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-LLANELLI_FELINDRE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1981_2000 | B15_1990 |  | <=320mm | (70,120] | 71.6533 | 2.8775 | 40.1581 | 1
1583 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B15_1990-1981_2000-WESTERN-NONE-(70,120]-TYWI_C.U._AREA-PENCOED__BRIDGEND_VALLEYS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | PLASTIC_PVC | 1981_2000 | B15_1990 |  | <=320mm | (70,120] | 27.7444 | 1.7707 | 63.8235 | 1
1584 | DIAM_LT_320-PLASTIC_PVC-<=320mm-B16_2000-2001_2020 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | [6 empty] | 68.5366 | 1.7707 | 25.8364 | 1
1585 | DIAM_LT_320-STEEL-<=320mm | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY | [6 empty] | 40.0293 | 3.9842 | 99.5313 | 1
1586 | DIAM_LT_320-STEEL-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(120,160]-SLUVAD__COURT_FARM__LLWYNON | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME | STEEL | 1901_1920 | B07_1910 |  | <=320mm | (120,160] | 3.3018 | 2.2134 | 670.373 | 4
1587 | DIAM_LT_320-STEEL-<=320mm-B07_1910-1901_1920-EASTERN-NONE-(160,320]-SLUVAD__COURT_FARM__LLWYNON-NEWPORT_SW__RISCA__ABERCARN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME | STEEL | 1901_1920 | B07_1910 |  | <=320mm | (160,320] | 4.8201 | 1.7707 | 367.3627 | 3
1588 | DIAM_LT_320-STEEL-<=320mm-B07_1910-1901_1920-WESTERN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME | [6 empty] | 8.4544 | 2.2134 | 261.8074 | 3
1589 | DIAM_LT_320-STEEL-<=320mm-B07_1910-1901_1920-WESTERN-NONE-(120,160] | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND | STEEL | 1901_1920 | B07_1910 |  | <=320mm | (120,160] | 5.6235 | 1.5494 | 275.5216 | 3
1590 | DIAM_LT_320-STEEL-<=320mm-B09_1930-1921_1940 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | [6 empty] | 8.6194 | 1.5494 | 179.7577 | 2
1591 | DIAM_LT_320-STEEL-<=320mm-B09_1930-1921_1940-WESTERN-BITUMEN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 17.8157 | 1.5494 | 86.9683 | 1
1592 | DIAM_LT_320-STEEL-<=320mm-B11_1950-1941_1960 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | [6 empty] | 18.8485 | 1.7707 | 93.9459 | 1
1593 | DIAM_LT_320-STEEL-<=320mm-B11_1950-1941_1960-WESTERN-BITUMEN-(70,120]-TYWI_C.U._AREA-BRYNGWYN-TWYNLLANAN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | STEEL | 1941_1960 | B11_1950 |  | <=320mm | (70,120] | 6.1723 | 1.5494 | 251.0239 | 3
1594 | DIAM_LT_320-STEEL-<=320mm-B11_1950-1941_1960-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 11.9505 | 1.7707 | 148.1737 | 2
1595 | DIAM_LT_320-STEEL-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(160,320]-PEMBROKESHIRE-BOLTON_HILL-TEMPLETON TO MARTLETWY-CROSSHANDS VILLAGE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME,DMA_NAME | STEEL | 1941_1960 | B11_1950 |  | <=320mm | (160,320] | 4.0694 | 1.7707 | 435.1336 | 3
1596 | DIAM_LT_320-STEEL-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(160,320]-PEMBROKESHIRE-BOLTON_HILL-TTM OFF PENT PUMPS | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | STEEL | 1941_1960 | B11_1950 |  | <=320mm | (160,320] | 8.0372 | 2.2134 | 275.3978 | 3
1597 | DIAM_LT_320-STEEL-<=320mm-B11_1950-1941_1960-WESTERN-NONE-(160,320]-PEMBROKESHIRE-PRESELI_SUPPLY-TENBY MAIN | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN,DIAM_BIN_SECOND,WRZ_NAME,WQZ_NAME,SUPER_DMA_NAME | STEEL | 1941_1960 | B11_1950 |  | <=320mm | (160,320] | 9.2119 | 3.3201 | 360.4175 | 3
1598 | DIAM_LT_320-STEEL-<=320mm-B12_1960-1961_1980 | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS | [6 empty] | 27.26 | 1.7707 | 64.9575 | 1
1599 | DIAM_LT_320-STEEL-<=320mm-B13_1970-1961_1980-WESTERN-NONE | DIAM_LT_320,ASSET_MATERIAL_BIN,DIAM_BIN_PRIMARY,DATE_INSTALL_BIN,DATE_INSTALL_BIN_20YRS,AREA_NAME,LINING_BIN | [6 empty] | 1.7796 | 1.5494 | 870.624 | 4

## Pivot_MainsAge>5
Column Labels
| 1 | 2 | 3 | 4 | 5 | Grand Total
Sum of Average of bursts_year | 734.6368 | 816.3123 | 1023.7106 | 647.4278 | 760.5339 | 3982.6214

## Pivot_MainsAge>5 Pasted Outputs
<320mm, Age>5
| 1 | 2 | 3 | 4 | 5 | Grand Total
Sum of Sum of LENGTH_KM | 16750.3004 | 4497.4552 | 3026.1043 | 932.8899 | 388.011 | 25594.761 | Line CW20.3
<320mm, Age>5
| 1 | 2 | 3 | 4 | 5 | Grand Total
Sum of Average of bursts_year | 734.6368 | 816.3123 | 1023.7106 | 647.4278 | 760.5339 | 3982.6214 | Line CW20.4
Age<=5
Length km | [5 empty] | 380.239 | Line CW20.6 | all mains minus those age>5
Age<=5
Bursts/yr | [5 empty] | 16.0277 | Line CW20.7 | all mains minus those age>5

## CW20
CW20 | [10 empty] | Ofwat Bon Numbers
#REF!
Water mains - asset condition | [10 empty] | Water mains - asset condition
Line description | Units | DPs | [6 empty] | PR24 BP reference | RAG 4 reference | Line description | Units | DPs | [6 empty] | PR24 BP reference
|  |  | Grade 1 | Grade 2 | Grade 3 | Grade 4 | Grade 5 | Total | [5 empty] | Grade 1 | Grade 2 | Grade 3 | Grade 4 | Grade 5 | Total
|  |  | 2025-26 | [10 empty] | 2025-26
Length of potable mains by Condition Grade | [10 empty] | Length of potable mains by Condition Grade
Potable mains (up to 320mm) | km | 1 | 17128.0531 | 4497.4552 | 3026.1043 | 935.3763 | 388.011 | 25975 | CW20.1 |  | Potable mains (up to 320mm) | km | 1 | CW20_001_1_PR24 | CW20_001_2_PR24 | CW20_001_3_PR24 | CW20_001_4_PR24 | CW20_001_5_PR24 | CW20_001_TOT_PR24 | CW20.1
Potable mains (greater than 320mm) | km | 1 | 1866.1175 | 23.1549 | 2.3707 | 6.1369 | 2.42 | 1900.2 | CW20.2 |  | Potable mains (greater than 320mm) | km | 1 | CW20_002_1_PR24 | CW20_002_2_PR24 | CW20_002_3_PR24 | CW20_002_4_PR24 | CW20_002_5_PR24 | CW20_002_TOT_PR24 | CW20.2
Analysed burst rate comparison | [10 empty] | Analysed burst rate comparison
Analysed cohort potable mains (up to 320mm) | km | 2 | 16750.3004 | 4497.4552 | 3026.1043 | 932.8899 | 388.011 | 25594.761 | CW20.3 |  | Analysed cohort potable mains (up to 320mm) | km | 2 | CW20_003_1_PR24 | CW20_003_2_PR24 | CW20_003_3_PR24 | CW20_003_4_PR24 | CW20_003_5_PR24 | CW20_003_TOT_PR24 | CW20.3
Annual average bursts from cohort analysis (5 year average) potable mains (up to 320mm) | nr | 1 | 734.6368 | 816.3123 | 1023.7106 | 647.4278 | 760.5339 | 3982.6214 | CW20.4 |  | Annual average bursts from cohort analysis (5 year average) potable mains (up to 320mm) | nr | 1 | CW20_004_1_PR24 | CW20_004_2_PR24 | CW20_004_3_PR24 | CW20_004_4_PR24 | CW20_004_5_PR24 | CW20_004_TOT_PR24 | CW20.4
Annual average bursts on analysed cohorts potable mains (up to 320mm) | nr/000km | 2 | 43.8581 | 181.5054 | 338.2932 | 694.0023 | 1960.0833 | 155.603 | CW20.5 |  | Annual average bursts on analysed cohorts potable mains (up to 320mm) | nr/000km | 2 | CW20_005_1_PR24 | CW20_005_2_PR24 | CW20_005_3_PR24 | CW20_005_4_PR24 | CW20_005_5_PR24 | CW20_005_TOT_PR24 | CW20.5
Replaced and/or relined mains length | km | 2 | [5 empty] | 380.239 | CW20.6 |  | Replaced and/or relined mains length | km | 2 | [5 empty] | CW20_006_TOT_PR24 | CW20.6
Annual average bursts on replaced potable mains (5 year average) up to 320mm | nr | 1 | [5 empty] | 16.0277 | CW20.7 |  | Annual average bursts on replaced potable mains (5 year average) up to 320mm | nr | 1 | [5 empty] | CW20_007_TOT_PR24 | CW20.7
Annual average bursts (5 year average) on potable mains up to 320mm | nr | 1 | [5 empty] | 3998.6492 | CW20.8 |  | Annual average bursts (5 year average) on potable mains up to 320mm | nr | 1 | [5 empty] | CW20_008_TOT_PR24 | CW20.8
Current annual bursts on potable mains (up to 320mm) | nr | 2 | 748.3677 | 816.3123 | 1023.7106 | 649.7246 | 760.5339 | 3998.6492 | CW20.9 |  | Current annual bursts on potable mains (up to 320mm) | nr | 2 | CW20_009_1_PR24 | CW20_009_2_PR24 | CW20_009_3_PR24 | CW20_009_4_PR24 | CW20_009_5_PR24 | CW20_009_TOT_PR24 | CW20.9
Current annual bursts on potable mains (up to 320mm) | nr/000km | 1 | 43.6925 | 181.5054 | 338.2932 | 694.6131 | 1960.0833 | 153.9422 | CW20.10 |  | Current annual bursts on potable mains (up to 320mm) | nr/000km | 1 | CW20_010_1_PR24 | CW20_010_2_PR24 | CW20_010_3_PR24 | CW20_010_4_PR24 | CW20_010_5_PR24 | CW20_010_TOT_PR24 | CW20.10
Annual bursts on mains (5 year average) greater than 320mm and other mains | nr | 1 | [5 empty] | 34.7508 | CW20.11 |  | Annual bursts on mains (5 year average) greater than 320mm and other mains | nr | 1 | [5 empty] | CW20_011_TOT_PR24 | CW20.11
Annual bursts on mains (5 year average) on potable and other mains reported in APR 2019-2023 | nr | 1 | [5 empty] | 4033.4 | CW20.12 |  | Annual bursts on mains (5 year average) on potable and other mains reported in APR 2019-2023 | nr | 1 | [5 empty] | CW20_012_TOT_PR24 | CW20.12