## Cover
CWW21 – Sewer condition - cohort analysis guidance
Version 1.0
Objective To set out additional guidance for how companies should constrct the .xls file in support of Business Plan Table CWW21 - Wastewater network+ - Asset Condition Grade. This includes the variables to be used. Companies were asked to provide information on what metrics they use in cohort/deterioarion analysis. This data has been analysed to determine the variables that should be available across the majority of water companies, these are considered primary variables that all companise must standardise upon. Further metrics were identifed that are available across a number of companies, these are considered secondary variables, which companies should standardise on where feasible, but are not mandatory. Companies can add any further variables as required, provided the primary variables are adhered to. This guidance should be read in conjunction with the Business Plan Table Guidance and Table template. Data sources -Ofwat data request

## Example
Example table providing an indicative layout for the supporting .xls file of the cohort analysis.
| Primary | Primary | Secondary | Primary | Primary | Primary | Secondary | Secondary | Secondary | Other | Other | Other
Cohort Ref (user specified) | Material | Age | Age | Type | Formerly private sewers and lateral drains (s105A sewers) (Yes/No) | Pipe size | Pipe size | Corrosivity | Fracture potential | Other_1 (e.g. Catchment ID) | Other_2 (e.g. depth) | Other_3 | Sum of length (km) | Sum of collapses (over 5 year period) | Average annual collapses | Nominal expected collapses | Annual collapse rate tolerance (+/-50% as far as practicable) | Tolerance | Within tolerance | Average annual collapses per 1000km | Grade | Rank
1 | VC | 1941 to 1960 | 1941 to 1950 | Combined | No | ≤165mm | 150mm | Not used | Not used | STW1.1 |  |  | 40 | 10 | 2 | 2.5 | 0.2 | +/-50% | Yes | 50 | 4 | 6
2 | VC | 1941 to 1960 | 1941 to 1950 | Combined | No | ≤165mm | 150mm | Not used | Not used | STW1.2 |  |  | 80 | 14 | 2.8 | 2.5 | -0.12 | +/-50% | Yes | 35 | 3 | 10
3 | VC | 1941 to 1960 | 1951 to 1960 | Combined | No | >165mm and ≤320mm; | 225mm | Low | Not used |  |  |  | 100 | 16 | 3.2 | 2.5 | -0.28 | +/-50% | Yes | 32 | 3 | 12
4 | VC | 1941 to 1960 | 1951 to 1960 | Combined | No | >165mm and ≤320mm; | 225mm | Medium | Not used |  |  |  | 80 | 7 | 1.4 | 2.5 | 0.44 | +/-50% | Yes | 17.5 | 2 | 19
5 | VC | 1941 to 1960 | 1951 to 1960 | Combined | No | >165mm and ≤320mm; | 225mm | High | Not used |  |  |  | 61 | 15 | 3 | 2.5 | -0.2 | +/-50% | Yes | 49.1803 | 3 | 7
6 | VC | 1941 to 1960 | 1951 to 1960 | Combined | No | >165mm and ≤320mm; | 300mm | Not used | Not used |  |  |  | 82 | 20 | 4 | 2.5 | -0.6 | +/-50% | No | 48.7805 | 3 | 8
7 | VC | 1961 to 1980 | 1961 to 1970 | Combined | No | >320mm and ≤625mm; | 375mm | Not used | Not used |  |  |  | 76 | 12 | 2.4 | 2.5 | 0.04 | +/-50% | Yes | 31.5789 | 3 | 13
8 | PE | 1961 to 1980 | Not used | Combined | No | >320mm and ≤625mm; | Not used | Not used | Not used |  |  |  | 120 | 13 | 2.6 | 2.5 | -0.04 | +/-50% | Yes | 21.6667 | 2 | 16
9 | PE | 1981 to 2000 | Not used | Combined | No | >320mm and ≤625mm; | Not used | Not used | Not used |  |  |  | 130 | 13 | 2.6 | 2.5 | -0.04 | +/-50% | Yes | 20 | 2 | 17
10 | PE | 2001 to 2020 | Not used | Combined | No | >320mm and ≤625mm; | Not used | Not used | Not used |  |  |  | 140 | 13 | 2.6 | 2.5 | -0.04 | +/-50% | Yes | 18.5714 | 2 | 18
11 | PVC | 1961 to 1980 | Not used | Combined | No | >320mm and ≤625mm; | Not used | Not used | Not used |  |  |  | 20 | 14 | 2.8 | 2.5 | -0.12 | +/-50% | Yes | 140 | 5 | 2
12 | PVC | 1981 to 2000 | Not used | Combined | No | >320mm and ≤625mm; | Not used | Not used | Not used |  |  |  | 30 | 14 | 2.8 | 2.5 | -0.12 | +/-50% | Yes | 93.3333 | 4 | 3
13 | BR | 1901 to 1920 | Not used | Combined | No | >320mm and ≤625mm; | Not used | Not used | Not used |  |  |  | 45 | 13 | 2.6 | 2.5 | -0.04 | +/-50% | Yes | 57.7778 | 4 | 4
14 | BR | 1921 to 1940 | 1921 to 1930 | Combined | No | >320mm and ≤625mm; | Not used | Not used | High | STW2.1 |  |  | 50 | 13 | 2.6 | 2.5 | -0.04 | +/-50% | Yes | 52 | 4 | 5
15 | BR | 1921 to 1940 | 1921 to 1930 | Combined | No | >320mm and ≤625mm; | Not used | Not used | High | STW2.2 |  |  | 80 | 5 | 1 | 2.5 | 0.6 | +/-50% | No | 12.5 | 2 | 20
16 | BR | 1921 to 1940 | 1921 to 1930 | Combined | No | >320mm and ≤625mm; | Not used | Not used | High | STW1.2 |  |  | 8 | 13 | 2.6 | 2.5 | -0.04 | +/-50% | Yes | 325 | 5 | 1
17 | BR | 1901 to 1920 | Not used | Combined | No | >625mm and ≤1500mm; | >70mm and ≤120mm | Not used | Not used |  | 2-4m |  | 70 | 13 | 2.6 | 2.5 | -0.04 | +/-50% | Yes | 37.1429 | 3 | 9
18 | BR | 1921 to 1940 | Not used | Combined | No | >625mm and ≤1500mm; | >120mm and ≤160mm | Not used | Not used |  | 2-4m |  | 72 | 12 | 2.4 | 2.5 | 0.04 | +/-50% | Yes | 33.3333 | 3 | 11
19 | BR | 1941 to 1960 | Not used | Combined | No | >625mm and ≤1500mm; | >120mm and ≤160mm | Not used | Not used |  | 4-8m |  | 80 | 12 | 2.4 | 2.5 | 0.04 | +/-50% | Yes | 30 | 3 | 14
20 | BR | 1961 to 1980 | Not used | Combined | No | >625mm and ≤1500mm; | >70mm and ≤120mm | Not used | Not used |  | 4-8m |  | 85 | 12 | 2.4 | 2.5 | 0.04 | +/-50% | Yes | 28.2353 | 3 | 15
[14 empty] | Total | 50.8 | 50 | -0.016 | +/-10% | Yes
[16 empty] | Average of averages | -0.016 | +/-10% | Yes
Example table and graph of cumulative annual average bursts (y-axis) versus cumulative mains length (x-axis)
Cohort Ref | Rank | Average annual collapses | Cumulative average annual collapses | Length | Cumulative length (km)
16 | 1 | 2.6 | 2.6 | 8 | 8
11 | 2 | 2.8 | 5.4 | 20 | 28
12 | 3 | 2.8 | 8.2 | 30 | 58
13 | 4 | 2.6 | 10.8 | 45 | 103
14 | 5 | 2.6 | 13.4 | 50 | 153
1 | 6 | 2 | 15.4 | 40 | 193
5 | 7 | 3 | 18.4 | 61 | 254
6 | 8 | 4 | 22.4 | 82 | 336
17 | 9 | 2.6 | 25 | 70 | 406
2 | 10 | 2.8 | 27.8 | 80 | 486
18 | 11 | 2.4 | 30.2 | 72 | 558
3 | 12 | 3.2 | 33.4 | 100 | 658
7 | 13 | 2.4 | 35.8 | 76 | 734
19 | 14 | 2.4 | 38.2 | 80 | 814
20 | 15 | 2.4 | 40.6 | 85 | 899
8 | 16 | 2.6 | 43.2 | 120 | 1019
9 | 17 | 2.6 | 45.8 | 130 | 1149
10 | 18 | 2.6 | 48.4 | 140 | 1289
4 | 19 | 1.4 | 49.8 | 80 | 1369
15 | 20 | 1 | 50.8 | 80 | 1449

## Variables
Primary | Primary | Primary | Primary | Secondary | Primary | Secondary | Secondary | Secondary | Secondary | Calcualtion | Calcualtion
Material | Age | Type | Formerly private sewers and lateral drains (s105A sewers) | S_Age | Pipe size | S_Pipe size | CWW21 | Fracture potential | Other (user defined heading e.g. STW catchment, depth, gradient, CCTV grade) | Grade | Collapse average per 1000km
Not used | pre-1880 | Foul | Yes | Not used | ≤165mm | Not used | 21.1 Foul sewers | Not used | User defined variable list. | 1 | ≤12
AC | 1881 to 1900 | Combined | No | pre-1880 | >165mm and ≤320mm; | 100mm | 21.2 Combined sewers | Low |  | 2 | >12 and ≤25
VC | 1901 to 1920 | Surface Water |  | 1881 to 1890 | >320mm and ≤625mm; | 150mm | 21.3 Surface water sewers | Medium |  | 3 | >25 and ≤50
VI | 1921 to 1940 | Other |  | 1891 to 1900 | >625mm and ≤1500mm; | 225mm | 21.4 Other wastewater network pipes | High |  | 4 | >50 and ≤100
Ferrous_1 | 1941 to 1960 |  |  | 1901 to 1910 | >1500mm | 300mm | 21.6 Formerly private sewers and lateral drains (s105A sewers) |  |  | 5 | >50
Ferrous_2 | 1961 to 1980 |  |  | 1911 to 1920 |  | 375mm | 21.7 Sewage pumping mains
CO | 1981 to 2000 |  |  | 1921 to 1930 |  | 450mm
GRP | 2001 to 2020 |  |  | 1931 to 1940 |  | 525mm
PVC | 2021 onwards |  |  | 1941 to 1950 |  | 600mm
PE |  |  |  | 1951 to 1960 |  | 675mm
PF |  |  |  | 1961 to 1970 |  | 750mm
BR |  |  |  | 1971 to 1980 |  | 825mm
Other |  |  |  | 1981 to 1990 |  | 900mm
|  |  |  | 1991 to 2000 |  | 1050mm
|  |  |  | 2001 to 2010 |  | 1200mm
|  |  |  | 2011 to 2020 |  | ≤1500mm
2020 onwards

## Cohort analysis
Example table providing an indicative layout for the supporting .xls file of the cohort analysis.
| Primary | Primary | Secondary | Primary | Primary | Primary | Secondary | Table Line | Secondary | Other | Other | Other
Cohort Ref (user specified) | Material | Age | Age | Type | Formerly private sewers and lateral drains (s105A sewers) (Yes/No) | Pipe size | Pipe size | CWW21 | Fracture potential | Era | Region | Catchment | Sum of length (km) | Sum of collapses (over 5 year period) | Average annual collapses | Nominal expected collapses | Annual collapse rate tolerance (+/-50% as far as practicable) | Tolerance | Within tolerance | Average annual collapses per 1000km | Grade | Rank
Mapped PST - COMBINED | Not used |  |  | Combined | Yes |  |  | 21.6 Formerly private sewers and lateral drains (s105A sewers) |  |  |  |  | 179.909 | 10.9767 | 2.1953 | 2.5 | 0.12186 | +/-50% | Yes | 12.2025 | 2 | 55
Mapped PST - COMBINED-CONNECTING SEWER-VC-<=165mm-(10,100] | VC |  |  | Combined | Yes | ≤165mm |  | 21.6 Formerly private sewers and lateral drains (s105A sewers) |  |  |  |  | 349.2982 | 21.6358 | 4.3272 | 2.5 | -0.73086 | +/-50% | No | 12.3881 | 2 | 54
Mapped PST - COMBINED-CONNECTING SEWER-VC-<=165mm-(100,150] | VC |  |  | Combined | Yes | ≤165mm |  | 21.6 Formerly private sewers and lateral drains (s105A sewers) |  |  |  |  | 282.5603 | 14.5088 | 2.9018 | 2.5 | -0.16071 | +/-50% | Yes | 10.2695 | 1 | 61
Mapped PST - COMBINED-GRAVITY-VC | VC |  |  | Combined | Yes |  |  | 21.6 Formerly private sewers and lateral drains (s105A sewers) |  |  |  |  | 145.1436 | 8.3005 | 1.6601 | 2.5 | 0.33596 | +/-50% | Yes | 11.4376 | 1 | 58
Mapped PST - FOUL | Not used |  |  | Foul | Yes |  |  | 21.6 Formerly private sewers and lateral drains (s105A sewers) |  |  |  |  | 2.6975 | 0.028296 | 0.0056592 | 2.5 | 0.99774 | +/-50% | No | 2.098 | 1 | 103
Mapped PST - FOUL-CONNECTING SEWER | Not used |  |  | Foul | Yes |  |  | 21.6 Formerly private sewers and lateral drains (s105A sewers) |  |  |  |  | 214.2602 | 7.9243 | 1.5849 | 2.5 | 0.36605 | +/-50% | Yes | 7.3969 | 1 | 70
Mapped PST - FOUL-CONNECTING SEWER-VC-<=165mm-(10,100] | VC |  |  | Foul | Yes | ≤165mm |  | 21.6 Formerly private sewers and lateral drains (s105A sewers) |  |  |  |  | 619.9458 | 15.6903 | 3.1381 | 2.5 | -0.25522 | +/-50% | Yes | 5.0618 | 1 | 84
Mapped PST - FOUL-CONNECTING SEWER-VC-<=165mm-(10,100]-GWENT | VC |  |  | Foul | Yes | ≤165mm |  | 21.6 Formerly private sewers and lateral drains (s105A sewers) |  |  | Gwent |  | 207.8676 | 8.5996 | 1.7199 | 2.5 | 0.31203 | +/-50% | Yes | 8.2741 | 1 | 65
Mapped PST - FOUL-CONNECTING SEWER-VC-<=165mm-(10,100]-SWANSEA | VC |  |  | Foul | Yes | ≤165mm |  | 21.6 Formerly private sewers and lateral drains (s105A sewers) |  |  | Swansea |  | 115.9491 | 9.7378 | 1.9476 | 2.5 | 0.22097 | +/-50% | Yes | 16.7967 | 2 | 43
Mapped PST - FOUL-CONNECTING SEWER-VC-<=165mm-(100,150] | VC |  |  | Foul | Yes | ≤165mm |  | 21.6 Formerly private sewers and lateral drains (s105A sewers) |  |  |  |  | 459.7311 | 15.1405 | 3.0281 | 2.5 | -0.21124 | +/-50% | Yes | 6.5867 | 1 | 72
Mapped PST - FOUL-GRAVITY | Not used |  |  | Foul | Yes |  |  | 21.6 Formerly private sewers and lateral drains (s105A sewers) |  |  |  |  | 285.0869 | 8.6307 | 1.7261 | 2.5 | 0.30955 | +/-50% | Yes | 6.0548 | 1 | 77
Mapped PST - FOUL-GRAVITY-VC-<=165mm-(100,150] | VC |  |  | Foul | Yes | ≤165mm |  | 21.6 Formerly private sewers and lateral drains (s105A sewers) |  |  |  |  | 399.6797 | 10.3995 | 2.0799 | 2.5 | 0.16804 | +/-50% | Yes | 5.2039 | 1 | 81
Mapped PST - FOUL-LATERAL DRAIN | Not used |  |  | Foul | Yes |  |  | 21.6 Formerly private sewers and lateral drains (s105A sewers) |  |  |  |  | 194.7987 | 7.8336 | 1.5667 | 2.5 | 0.37331 | +/-50% | Yes | 8.0428 | 1 | 67
Mapped PST - OTHER | Not used |  |  | Other | Yes |  |  | 21.6 Formerly private sewers and lateral drains (s105A sewers) |  |  |  |  | 7.0107 | 0.11145 | 0.022291 | 2.5 | 0.99108 | +/-50% | No | 3.1796 | 1 | 93
Mapped PST - SURFACE WATER | Not used |  |  | Surface Water | Yes |  |  | 21.6 Formerly private sewers and lateral drains (s105A sewers) |  |  |  |  | 844.9697 | 8.0094 | 1.6019 | 2.5 | 0.35924 | +/-50% | Yes | 1.8958 | 1 | 108
Public_sewer - COMBINED | Not used |  |  | Combined | No |  |  | 21.2 Combined sewers |  |  |  |  | 23.4242 | 2.4241 | 0.48482 | 2.5 | 0.80607 | +/-50% | No | 20.6975 | 2 | 38
Public_sewer - COMBINED-CONNECTING SEWER | Not used |  |  | Combined | No |  |  | 21.2 Combined sewers |  |  |  |  | 88.6948 | 9.6964 | 1.9393 | 2.5 | 0.22428 | +/-50% | Yes | 21.8647 | 2 | 36
Public_sewer - COMBINED-CONNECTING SEWER-VC-<=165mm-(10,100] | VC |  |  | Combined | No | ≤165mm |  | 21.2 Combined sewers |  |  |  |  | 40.715 | 16.5935 | 3.3187 | 2.5 | -0.32748 | +/-50% | Yes | 81.5103 | 4 | 24
Public_sewer - COMBINED-CONNECTING SEWER-VC-<=165mm-(100,150]-VALLEYS | VC |  |  | Combined | No | ≤165mm |  | 21.2 Combined sewers |  |  | Valleys |  | 38.217 | 8.4844 | 1.6969 | 2.5 | 0.32125 | +/-50% | Yes | 44.4011 | 3 | 32
Public_sewer - COMBINED-GRAVITY | Not used |  |  | Combined | No |  |  | 21.2 Combined sewers |  |  |  |  | 400.3641 | 8.4844 | 1.6969 | 2.5 | 0.32125 | +/-50% | Yes | 4.2383 | 1 | 87
Public_sewer - COMBINED-GRAVITY-BRICK->625mm and <=1500mm-(900,1050] | BR |  |  | Combined | No | >625mm and ≤1500mm; |  | 21.2 Combined sewers |  |  |  |  | 156.8611 | 8.4844 | 1.6969 | 2.5 | 0.32125 | +/-50% | Yes | 10.8177 | 1 | 59
Public_sewer - COMBINED-GRAVITY-CONC | CO |  |  | Combined | No |  |  | 21.2 Combined sewers |  |  |  |  | 1072.0413 | 15.7567 | 3.1513 | 2.5 | -0.26054 | +/-50% | Yes | 2.9396 | 1 | 94
Public_sewer - COMBINED-GRAVITY-FERROUS_1 | Ferrous_1 |  |  | Combined | No |  |  | 21.2 Combined sewers |  |  |  |  | 170.5831 | 13.3326 | 2.6665 | 2.5 | -0.066609 | +/-50% | Yes | 15.6318 | 2 | 45
Public_sewer - COMBINED-GRAVITY-VC | VC |  |  | Combined | No |  |  | 21.2 Combined sewers |  |  |  |  | 947.234 | 16.9688 | 3.3938 | 2.5 | -0.3575 | +/-50% | Yes | 3.5828 | 1 | 89
Public_sewer - COMBINED-GRAVITY-VC-<=165mm-(10,100] | VC |  |  | Combined | No | ≤165mm |  | 21.2 Combined sewers |  |  |  |  | 97.3858 | 9.6964 | 1.9393 | 2.5 | 0.22428 | +/-50% | Yes | 19.9135 | 2 | 39
Public_sewer - COMBINED-GRAVITY-VC-<=165mm-(100,150] | VC |  |  | Combined | No | ≤165mm |  | 21.2 Combined sewers |  |  |  |  | 607.5084 | 15.7567 | 3.1513 | 2.5 | -0.26054 | +/-50% | Yes | 5.1873 | 1 | 82
Public_sewer - COMBINED-GRAVITY-VC-<=165mm-(100,150]-GWENT | VC |  |  | Combined | No | ≤165mm |  | 21.2 Combined sewers |  |  | Gwent |  | 372.4253 | 18.1808 | 3.6362 | 2.5 | -0.45447 | +/-50% | Yes | 9.7635 | 1 | 62
Public_sewer - COMBINED-GRAVITY-VC-<=165mm-(100,150]-NORTHEAST-PRE_PRIVATISATION | VC |  |  | Combined | No | ≤165mm |  | 21.2 Combined sewers |  | Pre-Privatisation | North-East |  | 278.2664 | 8.4844 | 1.6969 | 2.5 | 0.32125 | +/-50% | Yes | 6.098 | 1 | 76
Public_sewer - COMBINED-GRAVITY-VC-<=165mm-(100,150]-NORTHEAST-WAR_TIME | VC |  |  | Combined | No | ≤165mm |  | 21.2 Combined sewers |  | War_time | North-East |  | 105.9385 | 8.4844 | 1.6969 | 2.5 | 0.32125 | +/-50% | Yes | 16.0176 | 2 | 44
Public_sewer - COMBINED-GRAVITY-VC-<=165mm-(100,150]-SWANSEA | VC |  |  | Combined | No | ≤165mm |  | 21.2 Combined sewers |  |  | Swansea |  | 269.508 | 18.1808 | 3.6362 | 2.5 | -0.45447 | +/-50% | Yes | 13.4919 | 2 | 50
Public_sewer - COMBINED-GRAVITY-VC-<=165mm-(100,150]-VALLEYS | VC |  |  | Combined | No | ≤165mm |  | 21.2 Combined sewers |  |  | Valleys |  | 339.3894 | 9.6964 | 1.9393 | 2.5 | 0.22428 | +/-50% | Yes | 5.7141 | 1 | 79
Public_sewer - COMBINED-GRAVITY-VC-<=165mm-(100,150]-WESTERN | VC |  |  | Combined | No | ≤165mm |  | 21.2 Combined sewers |  |  | Western |  | 283.3252 | 21.817 | 4.3634 | 2.5 | -0.74536 | +/-50% | No | 15.4007 | 2 | 47
Public_sewer - COMBINED-GRAVITY-VC-<=165mm-(150,225]-GWENT | VC |  |  | Combined | No | ≤165mm |  | 21.2 Combined sewers |  |  | Gwent |  | 228.0339 | 14.5447 | 2.9089 | 2.5 | -0.16357 | +/-50% | Yes | 12.7566 | 2 | 53
Public_sewer - COMBINED-GRAVITY-VC-<=165mm-(150,225]-SWANSEA | VC |  |  | Combined | No | ≤165mm |  | 21.2 Combined sewers |  |  | Swansea |  | 156.6609 | 12.1206 | 2.4241 | 2.5 | 0.030356 | +/-50% | Yes | 15.4736 | 2 | 46
Public_sewer - COMBINED-GRAVITY-VC-<=165mm-(150,225]-VALLEYS | VC |  |  | Combined | No | ≤165mm |  | 21.2 Combined sewers |  |  | Valleys |  | 259.3739 | 9.6964 | 1.9393 | 2.5 | 0.22428 | +/-50% | Yes | 7.4768 | 1 | 69
Public_sewer - COMBINED-GRAVITY-VC->165mm and <=320mm-(150,225] | VC |  |  | Combined | No | >165mm and ≤320mm; |  | 21.2 Combined sewers |  |  |  |  | 783.2805 | 14.5447 | 2.9089 | 2.5 | -0.16357 | +/-50% | Yes | 3.7138 | 1 | 88
Public_sewer - COMBINED-GRAVITY-VC->165mm and <=320mm-(150,225]-GWENT | VC |  |  | Combined | No | >165mm and ≤320mm; |  | 21.2 Combined sewers |  |  | Gwent |  | 259.7462 | 10.3533 | 2.0707 | 2.5 | 0.17174 | +/-50% | Yes | 7.9718 | 1 | 68
Public_sewer - COMBINED-GRAVITY-VC->165mm and <=320mm-(150,225]-NORTHEAST | VC |  |  | Combined | No | >165mm and ≤320mm; |  | 21.2 Combined sewers |  |  | North-East |  | 375.6428 | 10.9085 | 2.1817 | 2.5 | 0.12732 | +/-50% | Yes | 5.8079 | 1 | 78
Public_sewer - COMBINED-GRAVITY-VC->165mm and <=320mm-(150,225]-SWANSEA | VC |  |  | Combined | No | >165mm and ≤320mm; |  | 21.2 Combined sewers |  |  | Swansea |  | 207.1651 | 8.4844 | 1.6969 | 2.5 | 0.32125 | +/-50% | Yes | 8.1909 | 1 | 66
Public_sewer - COMBINED-GRAVITY-VC->165mm and <=320mm-(150,225]-VALLEYS | VC |  |  | Combined | No | >165mm and ≤320mm; |  | 21.2 Combined sewers |  |  | Valleys |  | 337.8506 | 20.6049 | 4.121 | 2.5 | -0.6484 | +/-50% | No | 12.1977 | 2 | 56
Public_sewer - COMBINED-GRAVITY-VC->165mm and <=320mm-(225,300] | VC |  |  | Combined | No | >165mm and ≤320mm; |  | 21.2 Combined sewers |  |  |  |  | 407.0486 | 13.3326 | 2.6665 | 2.5 | -0.066609 | +/-50% | Yes | 6.5509 | 1 | 73
Public_sewer - COMBINED-GRAVITY-VC->165mm and <=320mm-(225,300]-GWENT | VC |  |  | Combined | No | >165mm and ≤320mm; |  | 21.2 Combined sewers |  |  | Gwent |  | 120.3671 | 8.4844 | 1.6969 | 2.5 | 0.32125 | +/-50% | Yes | 14.0975 | 2 | 49
Public_sewer - COMBINED-GRAVITY-VC->165mm and <=320mm-(225,300]-SWANSEA | VC |  |  | Combined | No | >165mm and ≤320mm; |  | 21.2 Combined sewers |  |  | Swansea |  | 311.9131 | 20.6049 | 4.121 | 2.5 | -0.6484 | +/-50% | No | 13.212 | 2 | 51
Public_sewer - COMBINED-GRAVITY-VC->165mm and <=320mm-(225,300]-VALLEYS | VC |  |  | Combined | No | >165mm and ≤320mm; |  | 21.2 Combined sewers |  |  | Valleys |  | 160.0428 | 9.6964 | 1.9393 | 2.5 | 0.22428 | +/-50% | Yes | 12.1173 | 2 | 57
Public_sewer - FOUL | Not used |  |  | Foul | No |  |  | 21.1 Foul sewers |  |  |  |  | 276.2875 | 8.4844 | 1.6969 | 2.5 | 0.32125 | +/-50% | Yes | 6.1417 | 1 | 75
Public_sewer - FOUL-GRAVITY | Not used |  |  | Foul | No |  |  | 21.1 Foul sewers |  |  |  |  | 1001.7564 | 25.4532 | 5.0906 | 2.5 | -1.0363 | +/-50% | No | 5.0817 | 1 | 83
Public_sewer - FOUL-GRAVITY-VC-<=165mm-(100,150] | VC |  |  | Foul | No | ≤165mm |  | 21.1 Foul sewers |  |  |  |  | 941.0092 | 9.6964 | 1.9393 | 2.5 | 0.22428 | +/-50% | Yes | 2.0609 | 1 | 104
Public_sewer - FOUL-GRAVITY-VC-<=165mm-(100,150]-GWENT-PRE_PRIVATISATION | VC |  |  | Foul | No | ≤165mm |  | 21.1 Foul sewers |  | Pre-Privatisation | Gwent |  | 326.7399 | 10.9085 | 2.1817 | 2.5 | 0.12732 | +/-50% | Yes | 6.6772 | 1 | 71
Public_sewer - FOUL-GRAVITY-VC-<=165mm-(100,150]-NORTHEAST | VC |  |  | Foul | No | ≤165mm |  | 21.1 Foul sewers |  |  | North-East |  | 655.5974 | 10.9085 | 2.1817 | 2.5 | 0.12732 | +/-50% | Yes | 3.3278 | 1 | 91
Public_sewer - FOUL-GRAVITY-VC-<=165mm-(100,150]-SWANSEA | VC |  |  | Foul | No | ≤165mm |  | 21.1 Foul sewers |  |  | Swansea |  | 234.3549 | 21.817 | 4.3634 | 2.5 | -0.74536 | +/-50% | No | 18.6188 | 2 | 40
Public_sewer - FOUL-GRAVITY-VC-<=165mm-(100,150]-WESTERN | VC |  |  | Foul | No | ≤165mm |  | 21.1 Foul sewers |  |  | Western |  | 354.3534 | 14.7603 | 2.9521 | 2.5 | -0.18082 | +/-50% | Yes | 8.3308 | 1 | 64
Public_sewer - FOUL-GRAVITY-VC-<=165mm-(150,225] | VC |  |  | Foul | No | ≤165mm |  | 21.1 Foul sewers |  |  |  |  | 586.5723 | 14.5447 | 2.9089 | 2.5 | -0.16357 | +/-50% | Yes | 4.9592 | 1 | 85
Public_sewer - FOUL-GRAVITY-VC-<=165mm-(150,225]-SWANSEA-PRE_PRIVATISATION | VC |  |  | Foul | No | ≤165mm |  | 21.1 Foul sewers |  | Pre-Privatisation | Swansea |  | 96.0328 | 8.4844 | 1.6969 | 2.5 | 0.32125 | +/-50% | Yes | 17.6698 | 2 | 42
Public_sewer - FOUL-GRAVITY-VC-<=165mm-(150,225]-SWANSEA-WAR_TIME | VC |  |  | Foul | No | ≤165mm |  | 21.1 Foul sewers |  | War_time | Swansea |  | 163.0688 | 8.4844 | 1.6969 | 2.5 | 0.32125 | +/-50% | Yes | 10.4059 | 1 | 60
Public_sewer - FOUL-GRAVITY-VC->165mm and <=320mm-(150,225] | VC |  |  | Foul | No | >165mm and ≤320mm; |  | 21.1 Foul sewers |  |  |  |  | 807.8514 | 21.817 | 4.3634 | 2.5 | -0.74536 | +/-50% | No | 5.4012 | 1 | 80
Public_sewer - FOUL-GRAVITY-VC->165mm and <=320mm-(225,300]-SWANSEA | VC |  |  | Foul | No | >165mm and ≤320mm; |  | 21.1 Foul sewers |  |  | Swansea |  | 168.3352 | 10.9085 | 2.1817 | 2.5 | 0.12732 | +/-50% | Yes | 12.9605 | 2 | 52
Public_sewer - OTHER | Not used |  |  | Other | No |  |  | 21.4 Other wastewater network pipes |  |  |  |  | 441.9896 | 4.8482 | 0.96964 | 2.5 | 0.61214 | +/-50% | No | 2.1938 | 1 | 102
Public_sewer - SURFACE WATER | Not used |  |  | Surface Water | No |  |  | 21.3 Surface water sewers |  |  |  |  | 1059.8638 | 8.4844 | 1.6969 | 2.5 | 0.32125 | +/-50% | Yes | 1.601 | 1 | 110
Public_sewer - SURFACE WATER-GRAVITY-VC | VC |  |  | Surface Water | No |  |  | 21.3 Surface water sewers |  |  |  |  | 877.7104 | 9.6964 | 1.9393 | 2.5 | 0.22428 | +/-50% | Yes | 2.2095 | 1 | 100
Public_sewer - SURFACE WATER-GRAVITY-VC-<=165mm-(100,150] | VC |  |  | Surface Water | No | ≤165mm |  | 21.3 Surface water sewers |  |  |  |  | 714.4569 | 8.4844 | 1.6969 | 2.5 | 0.32125 | +/-50% | Yes | 2.3751 | 1 | 98
Public_sewer - SURFACE WATER-GRAVITY-VC->165mm and <=320mm-(150,225] | VC |  |  | Surface Water | No | >165mm and ≤320mm; |  | 21.3 Surface water sewers |  |  |  |  | 1021.9851 | 16.9688 | 3.3938 | 2.5 | -0.3575 | +/-50% | Yes | 3.3207 | 1 | 92
Rising mains - DIAM_GT_320 | Not used | [6 empty] | 21.7 Sewage pumping mains |  |  |  |  | 81.035 | 3.5716 | 0.71432 | 1 | 0.28568 | +/-50% | Yes | 8.815 | 1 | 63
Rising mains - DIAM_GT_320-COMBINED-RISING MAIN->320mm and <=625mm | Not used |  |  | Combined |  | >320mm and ≤625mm; |  | 21.7 Sewage pumping mains |  |  |  |  | 111.5427 | 3.5716 | 0.71432 | 1 | 0.28568 | +/-50% | Yes | 6.404 | 1 | 74
Rising mains - DIAM_GT_320-COMBINED-RISING MAIN->320mm and <=625mm-PLASTIC_PE-DCWW-(300,375]-1981_2000-NORTHWEST-B15_1990-TREBORTH_NEW | PE | 1981 to 2000 |  | Combined |  | >320mm and ≤625mm; |  | 21.7 Sewage pumping mains |  | DCWW | North-West |  | 2.7084 | 4.7622 | 0.95243 | 1 | 0.04757 | +/-50% | Yes | 351.6521 | 3 | 11
Rising mains - DIAM_GT_320-COMBINED-RISING MAIN->625mm and <=1500mm-VC-DCWW-(675,750] | VC |  |  | Combined |  | >625mm and ≤1500mm; |  | 21.7 Sewage pumping mains |  | DCWW |  |  | 15.9486 | 4.7622 | 0.95243 | 1 | 0.04757 | +/-50% | Yes | 59.7186 | 1 | 29
Rising mains - DIAM_GT_320-FOUL-RISING MAIN->320mm and <=625mm-PLASTIC_PVC-PRE_PRIVATISATION-(300,375]-1961_1980-GWENT-B13_1970-NASH | PVC | 1961 to 1980 |  | Foul |  | >320mm and ≤625mm; |  | 21.7 Sewage pumping mains |  | Pre-Privatisation | Gwent |  | 1.5358 | 10.7148 | 2.143 | 1 | -1.143 | +/-50% | No | 1395.3202 | 5 | 3
Rising mains - DIAM_LT_320 | Not used | [6 empty] | 21.7 Sewage pumping mains |  |  |  |  | 116.7606 | 10.7724 | 2.1545 | 2.5 | 0.13821 | +/-50% | Yes | 18.4521 | 1 | 41
Rising mains - DIAM_LT_320-COMBINED-RISING MAIN-<=165mm | Not used |  |  | Combined |  | ≤165mm |  | 21.7 Sewage pumping mains |  |  |  |  | 124.9194 | 21.4297 | 4.2859 | 2.5 | -0.71437 | +/-50% | No | 34.3096 | 1 | 34
Rising mains - DIAM_LT_320-COMBINED-RISING MAIN-<=165mm-AC-PRE_PRIVATISATION-(0,100] | AC |  |  | Combined |  | ≤165mm |  | 21.7 Sewage pumping mains |  | Pre-Privatisation |  |  | 4.557 | 9.5243 | 1.9049 | 2.5 | 0.23806 | +/-50% | Yes | 418.0051 | 3 | 9
Rising mains - DIAM_LT_320-COMBINED-RISING MAIN-<=165mm-FERROUS_1-PRE_PRIVATISATION | Ferrous_1 |  |  | Combined |  | ≤165mm |  | 21.7 Sewage pumping mains |  | Pre-Privatisation |  |  | 38.7931 | 10.7148 | 2.143 | 2.5 | 0.14281 | +/-50% | Yes | 55.241 | 1 | 30
Rising mains - DIAM_LT_320-COMBINED-RISING MAIN-<=165mm-FERROUS_2-PRE_PRIVATISATION-(100,150] | Ferrous_2 |  |  | Combined |  | ≤165mm |  | 21.7 Sewage pumping mains |  | Pre-Privatisation |  |  | 8.2699 | 10.7148 | 2.143 | 2.5 | 0.14281 | +/-50% | Yes | 259.1286 | 3 | 13
Rising mains - DIAM_LT_320-COMBINED-RISING MAIN-<=165mm-PLASTIC_PVC-PRE_PRIVATISATION | PVC |  |  | Combined |  | ≤165mm |  | 21.7 Sewage pumping mains |  | Pre-Privatisation |  |  | 24.6651 | 14.2865 | 2.8573 | 2.5 | -0.14292 | +/-50% | Yes | 115.8433 | 1 | 21
Rising mains - DIAM_LT_320-COMBINED-RISING MAIN-<=165mm-PLASTIC_PVC-PRE_PRIVATISATION-(0,100]-1961_1980-WESTERN-B13_1970 | PVC | 1961 to 1980 |  | Combined |  | ≤165mm |  | 21.7 Sewage pumping mains |  | Pre-Privatisation | Western |  | 6.7851 | 8.3338 | 1.6668 | 2.5 | 0.3333 | +/-50% | Yes | 245.6507 | 2 | 14
Rising mains - DIAM_LT_320-COMBINED-RISING MAIN-<=165mm-PLASTIC_PVC-PRE_PRIVATISATION-(100,150]-1961_1980-NORTHWEST-B13_1970 | PVC | 1961 to 1980 |  | Combined |  | ≤165mm |  | 21.7 Sewage pumping mains |  | Pre-Privatisation | North-West |  | 4.1045 | 8.3338 | 1.6668 | 2.5 | 0.3333 | +/-50% | Yes | 406.0792 | 3 | 10
Rising mains - DIAM_LT_320-COMBINED-RISING MAIN-<=165mm-STEEL-PRE_PRIVATISATION | Other |  |  | Combined |  | ≤165mm |  | 21.7 Sewage pumping mains |  | Pre-Privatisation |  |  | 2.5574 | 8.3338 | 1.6668 | 2.5 | 0.3333 | +/-50% | Yes | 651.7342 | 4 | 6
Rising mains - DIAM_LT_320-COMBINED-RISING MAIN->165mm and <=320mm | Not used |  |  | Combined |  | >165mm and ≤320mm; |  | 21.7 Sewage pumping mains |  |  |  |  | 91.7608 | 9.5243 | 1.9049 | 2.5 | 0.23806 | +/-50% | Yes | 20.759 | 1 | 37
Rising mains - DIAM_LT_320-COMBINED-RISING MAIN->165mm and <=320mm-FERROUS_1-PRE_PRIVATISATION | Ferrous_1 |  |  | Combined |  | >165mm and ≤320mm; |  | 21.7 Sewage pumping mains |  | Pre-Privatisation |  |  | 36.8494 | 17.8581 | 3.5716 | 2.5 | -0.42865 | +/-50% | Yes | 96.9246 | 1 | 22
Rising mains - DIAM_LT_320-COMBINED-RISING MAIN->165mm and <=320mm-FERROUS_2 | Ferrous_2 |  |  | Combined |  | >165mm and ≤320mm; |  | 21.7 Sewage pumping mains |  |  |  |  | 79.0703 | 20.2391 | 4.0478 | 2.5 | -0.61913 | +/-50% | No | 51.1928 | 1 | 31
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm | Not used |  |  | Foul |  | ≤165mm |  | 21.7 Sewage pumping mains |  |  |  |  | 63.8025 | 20.2391 | 4.0478 | 2.5 | -0.61913 | +/-50% | No | 63.4432 | 1 | 27
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-AC-PRE_PRIVATISATION-(100,150]-1961_1980 | AC | 1961 to 1980 |  | Foul |  | ≤165mm |  | 21.7 Sewage pumping mains |  | Pre-Privatisation |  |  | 11.1418 | 8.3338 | 1.6668 | 2.5 | 0.3333 | +/-50% | Yes | 149.5941 | 2 | 16
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-FERROUS_1-PRE_PRIVATISATION | Ferrous_1 |  |  | Foul |  | ≤165mm |  | 21.7 Sewage pumping mains |  | Pre-Privatisation |  |  | 35.0463 | 10.7148 | 2.143 | 2.5 | 0.14281 | +/-50% | Yes | 61.1469 | 1 | 28
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-FERROUS_1-PRE_PRIVATISATION-(100,150]-1961_1980 | Ferrous_1 | 1961 to 1980 |  | Foul |  | ≤165mm |  | 21.7 Sewage pumping mains |  | Pre-Privatisation |  |  | 25.2119 | 16.6675 | 3.3335 | 2.5 | -0.3334 | +/-50% | Yes | 132.2197 | 2 | 19
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-FERROUS_2 | Ferrous_2 |  |  | Foul |  | ≤165mm |  | 21.7 Sewage pumping mains |  |  |  |  | 35.7472 | 11.9054 | 2.3811 | 2.5 | 0.04757 | +/-50% | Yes | 66.6087 | 1 | 26
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-FERROUS_2-DCWW-(0,100] | Ferrous_2 |  |  | Foul |  | ≤165mm |  | 21.7 Sewage pumping mains |  | DCWW |  |  | 13.5355 | 9.5243 | 1.9049 | 2.5 | 0.23806 | +/-50% | Yes | 140.7303 | 2 | 17
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-FERROUS_2-PRE_PRIVATISATION-(0,100] | Ferrous_2 |  |  | Foul |  | ≤165mm |  | 21.7 Sewage pumping mains |  | Pre-Privatisation |  |  | 14.3821 | 16.6675 | 3.3335 | 2.5 | -0.3334 | +/-50% | Yes | 231.782 | 2 | 15
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-PLASTIC_PE-DCWW | PE |  |  | Foul |  | ≤165mm |  | 21.7 Sewage pumping mains |  | DCWW |  |  | 164.7623 | 12.1886 | 2.4377 | 2.5 | 0.024908 | +/-50% | Yes | 14.7954 | 1 | 48
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-PLASTIC_PE-DCWW-(0,100]-1981_2000 | PE | 1981 to 2000 |  | Foul |  | ≤165mm |  | 21.7 Sewage pumping mains |  | DCWW |  |  | 59.2678 | 13.0959 | 2.6192 | 2.5 | -0.047673 | +/-50% | Yes | 44.1923 | 1 | 33
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-PLASTIC_PE-DCWW-(0,100]-2001_2020-WESTERN | PE | 2001 to 2020 |  | Foul |  | ≤165mm |  | 21.7 Sewage pumping mains |  | DCWW | Western |  | 45.2748 | 7.5631 | 1.5126 | 2.5 | 0.39495 | +/-50% | Yes | 33.41 | 1 | 35
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-PLASTIC_PVC-DCWW | PVC |  |  | Foul |  | ≤165mm |  | 21.7 Sewage pumping mains |  | DCWW |  |  | 21.625 | 9.5243 | 1.9049 | 2.5 | 0.23806 | +/-50% | Yes | 88.086 | 1 | 23
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-PLASTIC_PVC-PRE_PRIVATISATION | PVC |  |  | Foul |  | ≤165mm |  | 21.7 Sewage pumping mains |  | Pre-Privatisation |  |  | 23.4757 | 8.3338 | 1.6668 | 2.5 | 0.3333 | +/-50% | Yes | 70.9992 | 1 | 25
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-PLASTIC_PVC-PRE_PRIVATISATION-(0,100]-1941_1960-WESTERN-B11_1950-CAMROSE | PVC | 1941 to 1960 |  | Foul |  | ≤165mm |  | 21.7 Sewage pumping mains |  | Pre-Privatisation | Western |  | 1.0614 | 13.0959 | 2.6192 | 2.5 | -0.047673 | +/-50% | Yes | 2467.6394 | 5 | 2
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-PLASTIC_PVC-PRE_PRIVATISATION-(0,100]-1961_1980 | PVC | 1961 to 1980 |  | Foul |  | ≤165mm |  | 21.7 Sewage pumping mains |  | Pre-Privatisation |  |  | 19.0043 | 13.0959 | 2.6192 | 2.5 | -0.047673 | +/-50% | Yes | 137.8207 | 2 | 18
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-PLASTIC_PVC-PRE_PRIVATISATION-(0,100]-1961_1980-CENTRAL-B13_1970-COWBRIDGE | PVC | 1961 to 1980 |  | Foul |  | ≤165mm |  | 21.7 Sewage pumping mains |  | Pre-Privatisation | Central |  | 4.2683 | 20.2391 | 4.0478 | 2.5 | -0.61913 | +/-50% | No | 948.3393 | 4 | 4
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-PLASTIC_PVC-PRE_PRIVATISATION-(0,100]-1961_1980-NORTHWEST | PVC | 1961 to 1980 |  | Foul |  | ≤165mm |  | 21.7 Sewage pumping mains |  | Pre-Privatisation | North-West |  | 18.2632 | 10.7148 | 2.143 | 2.5 | 0.14281 | +/-50% | Yes | 117.338 | 1 | 20
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-PLASTIC_PVC-PRE_PRIVATISATION-(0,100]-1961_1980-WESTERN-B13_1970-LLANGADOG | PVC | 1961 to 1980 |  | Foul |  | ≤165mm |  | 21.7 Sewage pumping mains |  | Pre-Privatisation | Western |  | 2.8209 | 8.3338 | 1.6668 | 2.5 | 0.3333 | +/-50% | Yes | 590.8484 | 4 | 8
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-PLASTIC_PVC-PRE_PRIVATISATION-(0,100]-1961_1980-WESTERN-B13_1970-NEWGALE | PVC | 1961 to 1980 |  | Foul |  | ≤165mm |  | 21.7 Sewage pumping mains |  | Pre-Privatisation | Western |  | 5.1904 | 8.3338 | 1.6668 | 2.5 | 0.3333 | +/-50% | Yes | 321.1247 | 3 | 12
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-PLASTIC_PVC-WAR_TIME-(0,100]-1921_1940-WESTERN-B10_1940 | PVC | 1921 to 1940 |  | Foul |  | ≤165mm |  | 21.7 Sewage pumping mains |  | War_time | Western |  | 2.586 | 8.3338 | 1.6668 | 2.5 | 0.3333 | +/-50% | Yes | 644.5355 | 4 | 7
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-VC-PRE_PRIVATISATION-(0,100]-1961_1980-WESTERN-B13_1970-HENLLAN_NR_NEWCASTLE_EMLYN | VC | 1961 to 1980 |  | Foul |  | ≤165mm |  | 21.7 Sewage pumping mains |  | Pre-Privatisation | Western |  | 0.52691 | 9.5243 | 1.9049 | 2.5 | 0.23806 | +/-50% | Yes | 3615.1458 | 5 | 1
Rising mains - DIAM_LT_320-FOUL-RISING MAIN->165mm and <=320mm-FERROUS_2-DCWW-(225,300]-1981_2000-WESTERN-B15_1990-ABERYSTWYTH_GLAN_YR_AFON | Ferrous_2 | 1981 to 2000 |  | Foul |  | >165mm and ≤320mm; |  | 21.7 Sewage pumping mains |  | DCWW | Western |  | 4.1279 | 19.0486 | 3.8097 | 2.5 | -0.52389 | +/-50% | No | 922.9181 | 4 | 5
Unmapped PST - FOUL_COMBINED_SURFACE-PST-B99_UNKN-<=165mm-(100,150] | Not used |  |  |  | Yes | ≤165mm |  | 21.6 Formerly private sewers and lateral drains (s105A sewers) |  |  |  |  | 2407.0391 | 21.2763 | 4.2553 | 2.5 | -0.7021 | +/-50% | No | 1.7678 | 1 | 109
Unmapped PST - FOUL_COMBINED_SURFACE-PST-B99_UNKN-<=165mm-(100,150]-CENTRAL | Not used |  |  |  | Yes | ≤165mm |  | 21.6 Formerly private sewers and lateral drains (s105A sewers) |  |  | Central |  | 1477.4085 | 16.3902 | 3.278 | 2.5 | -0.31122 | +/-50% | Yes | 2.2188 | 1 | 99
Unmapped PST - FOUL_COMBINED_SURFACE-PST-B99_UNKN-<=165mm-(100,150]-GWENT | Not used |  |  |  | Yes | ≤165mm |  | 21.6 Formerly private sewers and lateral drains (s105A sewers) |  |  | Gwent |  | 1642.4457 | 16.39 | 3.278 | 2.5 | -0.3112 | +/-50% | Yes | 1.9958 | 1 | 107
Unmapped PST - FOUL_COMBINED_SURFACE-PST-B99_UNKN-<=165mm-(100,150]-NORTHEAST-1 | Not used |  |  |  | Yes | ≤165mm |  | 21.6 Formerly private sewers and lateral drains (s105A sewers) |  |  | North-East |  | 1230.7084 | 12.3309 | 2.4662 | 2.5 | 0.013528 | +/-50% | Yes | 2.0039 | 1 | 106
Unmapped PST - FOUL_COMBINED_SURFACE-PST-B99_UNKN-<=165mm-(100,150]-NORTHEAST-PRE_PRIVATISATION | Not used |  |  |  | Yes | ≤165mm |  | 21.6 Formerly private sewers and lateral drains (s105A sewers) |  | Pre-Privatisation | North-East |  | 714.5154 | 7.8691 | 1.5738 | 2.5 | 0.37048 | +/-50% | Yes | 2.2026 | 1 | 101
Unmapped PST - FOUL_COMBINED_SURFACE-PST-B99_UNKN-<=165mm-(100,150]-NORTHWEST-1 | Not used |  |  |  | Yes | ≤165mm |  | 21.6 Formerly private sewers and lateral drains (s105A sewers) |  |  | North-West |  | 892.2618 | 11.0211 | 2.2042 | 2.5 | 0.11831 | +/-50% | Yes | 2.4704 | 1 | 97
Unmapped PST - FOUL_COMBINED_SURFACE-PST-B99_UNKN-<=165mm-(100,150]-SWANSEA | Not used |  |  |  | Yes | ≤165mm |  | 21.6 Formerly private sewers and lateral drains (s105A sewers) |  |  | Swansea |  | 1392.1405 | 18.154 | 3.6308 | 2.5 | -0.45232 | +/-50% | Yes | 2.6081 | 1 | 96
Unmapped PST - FOUL_COMBINED_SURFACE-PST-B99_UNKN-<=165mm-(100,150]-SWANSEA-PRE_PRIVATISATION-1961_1980-BIN05_1961_1975 | Not used | 1961 to 1980 |  |  | Yes | ≤165mm |  | 21.6 Formerly private sewers and lateral drains (s105A sewers) |  | Pre-Privatisation | Swansea |  | 733.8924 | 9.7689 | 1.9538 | 2.5 | 0.21849 | +/-50% | Yes | 2.6622 | 1 | 95
Unmapped PST - FOUL_COMBINED_SURFACE-PST-B99_UNKN-<=165mm-(100,150]-VALLEYS | Not used |  |  |  | Yes | ≤165mm |  | 21.6 Formerly private sewers and lateral drains (s105A sewers) |  |  | Valleys |  | 737.969 | 13.1959 | 2.6392 | 2.5 | -0.055668 | +/-50% | Yes | 3.5763 | 1 | 90
Unmapped PST - FOUL_COMBINED_SURFACE-PST-B99_UNKN-<=165mm-(100,150]-VALLEYS-1 | Not used |  |  |  | Yes | ≤165mm |  | 21.6 Formerly private sewers and lateral drains (s105A sewers) |  |  | Valleys |  | 492.6086 | 10.4699 | 2.094 | 2.5 | 0.16241 | +/-50% | Yes | 4.2508 | 1 | 86
Unmapped PST - FOUL_COMBINED_SURFACE-PST-B99_UNKN-<=165mm-(100,150]-WESTERN-1 | Not used |  |  |  | Yes | ≤165mm |  | 21.6 Formerly private sewers and lateral drains (s105A sewers) |  |  | Western |  | 1145.3417 | 11.7673 | 2.3535 | 2.5 | 0.058615 | +/-50% | Yes | 2.0548 | 1 | 105
[12 empty] | Total | 37125.1966 | Total | 261.5469 | 267.5 | 0.022255 | +/-10% | Yes
[16 empty] | Average of averages | 0.019049 | +/-10% | Yes
Table and graph of cumulative annual average bursts (y-axis) versus cumulative mains length (x-axis)
Cohort Ref | Rank | Average annual collapses | Cumulative average annual collapses | Length | Cumulative length (km) | Grade
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-VC-PRE_PRIVATISATION-(0,100]-1961_1980-WESTERN-B13_1970-HENLLAN_NR_NEWCASTLE_EMLYN | 1 | 1.9049 | 1.9049 | 0.52691 | 0.52691 | 5 | [10 empty] | Sum of Sum of length (km) | Column Labels
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-PLASTIC_PVC-PRE_PRIVATISATION-(0,100]-1941_1960-WESTERN-B11_1950-CAMROSE | 2 | 2.6192 | 4.524 | 1.0614 | 1.5883 | 5 | [10 empty] | Row Labels | 1 | 2 | 3 | 4 | 5 | Grand Total
Rising mains - DIAM_GT_320-FOUL-RISING MAIN->320mm and <=625mm-PLASTIC_PVC-PRE_PRIVATISATION-(300,375]-1961_1980-GWENT-B13_1970-NASH | 3 | 2.143 | 6.667 | 1.5358 | 3.1241 | 5 | [10 empty] | 21.1 Foul sewers | 5113.2363 | 498.7228 |  |  |  | 5611.9591
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-PLASTIC_PVC-PRE_PRIVATISATION-(0,100]-1961_1980-CENTRAL-B13_1970-COWBRIDGE | 4 | 4.0478 | 10.7148 | 4.2683 | 7.3925 | 4 | [10 empty] | 21.2 Combined sewers | 6466.347 | 2353.7281 | 38.217 | 40.715 |  | 8899.0072
Rising mains - DIAM_LT_320-FOUL-RISING MAIN->165mm and <=320mm-FERROUS_2-DCWW-(225,300]-1981_2000-WESTERN-B15_1990-ABERYSTWYTH_GLAN_YR_AFON | 5 | 3.8097 | 14.5246 | 4.1279 | 11.5204 | 4 | [10 empty] | 21.3 Surface water sewers | 3674.0163 |  |  |  |  | 3674.0163
Rising mains - DIAM_LT_320-COMBINED-RISING MAIN-<=165mm-STEEL-PRE_PRIVATISATION | 6 | 1.6668 | 16.1913 | 2.5574 | 14.0778 | 4 | [10 empty] | 21.4 Other wastewater network pipes | 441.9896 |  |  |  |  | 441.9896
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-PLASTIC_PVC-WAR_TIME-(0,100]-1921_1940-WESTERN-B10_1940 | 7 | 1.6668 | 17.8581 | 2.586 | 16.6638 | 4 | [10 empty] | 21.6 Formerly private sewers and lateral drains (s105A sewers) | 16530.0827 | 645.1562 |  |  |  | 17175.239
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-PLASTIC_PVC-PRE_PRIVATISATION-(0,100]-1961_1980-WESTERN-B13_1970-LLANGADOG | 8 | 1.6668 | 19.5248 | 2.8209 | 19.4847 | 4 | [10 empty] | 21.7 Sewage pumping mains | 1188.6098 | 90.0607 | 24.8302 | 16.3606 | 3.1241 | 1322.9854
Rising mains - DIAM_LT_320-COMBINED-RISING MAIN-<=165mm-AC-PRE_PRIVATISATION-(0,100] | 9 | 1.9049 | 21.4297 | 4.557 | 24.0418 | 3 | [10 empty] | Grand Total | 33414.2817 | 3587.6678 | 63.0473 | 57.0756 | 3.1241 | 37125.1966
Rising mains - DIAM_LT_320-COMBINED-RISING MAIN-<=165mm-PLASTIC_PVC-PRE_PRIVATISATION-(100,150]-1961_1980-NORTHWEST-B13_1970 | 10 | 1.6668 | 23.0964 | 4.1045 | 28.1463 | 3
Rising mains - DIAM_GT_320-COMBINED-RISING MAIN->320mm and <=625mm-PLASTIC_PE-DCWW-(300,375]-1981_2000-NORTHWEST-B15_1990-TREBORTH_NEW | 11 | 0.95243 | 24.0489 | 2.7084 | 30.8547 | 3
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-PLASTIC_PVC-PRE_PRIVATISATION-(0,100]-1961_1980-WESTERN-B13_1970-NEWGALE | 12 | 1.6668 | 25.7156 | 5.1904 | 36.0451 | 3
Rising mains - DIAM_LT_320-COMBINED-RISING MAIN-<=165mm-FERROUS_2-PRE_PRIVATISATION-(100,150] | 13 | 2.143 | 27.8586 | 8.2699 | 44.315 | 3
Rising mains - DIAM_LT_320-COMBINED-RISING MAIN-<=165mm-PLASTIC_PVC-PRE_PRIVATISATION-(0,100]-1961_1980-WESTERN-B13_1970 | 14 | 1.6668 | 29.5253 | 6.7851 | 51.1 | 2
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-FERROUS_2-PRE_PRIVATISATION-(0,100] | 15 | 3.3335 | 32.8589 | 14.3821 | 65.4821 | 2
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-AC-PRE_PRIVATISATION-(100,150]-1961_1980 | 16 | 1.6668 | 34.5256 | 11.1418 | 76.6239 | 2
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-FERROUS_2-DCWW-(0,100] | 17 | 1.9049 | 36.4305 | 13.5355 | 90.1595 | 2
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-PLASTIC_PVC-PRE_PRIVATISATION-(0,100]-1961_1980 | 18 | 2.6192 | 39.0496 | 19.0043 | 109.1638 | 2
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-FERROUS_1-PRE_PRIVATISATION-(100,150]-1961_1980 | 19 | 3.3335 | 42.3832 | 25.2119 | 134.3756 | 2
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-PLASTIC_PVC-PRE_PRIVATISATION-(0,100]-1961_1980-NORTHWEST | 20 | 2.143 | 44.5261 | 18.2632 | 152.6388 | 1
Rising mains - DIAM_LT_320-COMBINED-RISING MAIN-<=165mm-PLASTIC_PVC-PRE_PRIVATISATION | 21 | 2.8573 | 47.3834 | 24.6651 | 177.304 | 1
Rising mains - DIAM_LT_320-COMBINED-RISING MAIN->165mm and <=320mm-FERROUS_1-PRE_PRIVATISATION | 22 | 3.5716 | 50.955 | 36.8494 | 214.1534 | 1
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-PLASTIC_PVC-DCWW | 23 | 1.9049 | 52.8599 | 21.625 | 235.7784 | 1
Public_sewer - COMBINED-CONNECTING SEWER-VC-<=165mm-(10,100] | 24 | 3.3187 | 56.1786 | 40.715 | 276.4935 | 4
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-PLASTIC_PVC-PRE_PRIVATISATION | 25 | 1.6668 | 57.8453 | 23.4757 | 299.9691 | 1
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-FERROUS_2 | 26 | 2.3811 | 60.2264 | 35.7472 | 335.7164 | 1
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm | 27 | 4.0478 | 64.2742 | 63.8025 | 399.5188 | 1
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-FERROUS_1-PRE_PRIVATISATION | 28 | 2.143 | 66.4172 | 35.0463 | 434.5651 | 1
Rising mains - DIAM_GT_320-COMBINED-RISING MAIN->625mm and <=1500mm-VC-DCWW-(675,750] | 29 | 0.95243 | 67.3696 | 15.9486 | 450.5137 | 1
Rising mains - DIAM_LT_320-COMBINED-RISING MAIN-<=165mm-FERROUS_1-PRE_PRIVATISATION | 30 | 2.143 | 69.5126 | 38.7931 | 489.3068 | 1
Rising mains - DIAM_LT_320-COMBINED-RISING MAIN->165mm and <=320mm-FERROUS_2 | 31 | 4.0478 | 73.5604 | 79.0703 | 568.3771 | 1
Public_sewer - COMBINED-CONNECTING SEWER-VC-<=165mm-(100,150]-VALLEYS | 32 | 1.6969 | 75.2573 | 38.217 | 606.5941 | 3
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-PLASTIC_PE-DCWW-(0,100]-1981_2000 | 33 | 2.6192 | 77.8765 | 59.2678 | 665.862 | 1
Rising mains - DIAM_LT_320-COMBINED-RISING MAIN-<=165mm | 34 | 4.2859 | 82.1624 | 124.9194 | 790.7813 | 1
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-PLASTIC_PE-DCWW-(0,100]-2001_2020-WESTERN | 35 | 1.5126 | 83.6751 | 45.2748 | 836.0561 | 1
Public_sewer - COMBINED-CONNECTING SEWER | 36 | 1.9393 | 85.6144 | 88.6948 | 924.7509 | 2
Rising mains - DIAM_LT_320-COMBINED-RISING MAIN->165mm and <=320mm | 37 | 1.9049 | 87.5192 | 91.7608 | 1016.5117 | 1
Public_sewer - COMBINED | 38 | 0.48482 | 88.004 | 23.4242 | 1039.9359 | 2
Public_sewer - COMBINED-GRAVITY-VC-<=165mm-(10,100] | 39 | 1.9393 | 89.9433 | 97.3858 | 1137.3217 | 2
Public_sewer - FOUL-GRAVITY-VC-<=165mm-(100,150]-SWANSEA | 40 | 4.3634 | 94.3067 | 234.3549 | 1371.6766 | 2
Rising mains - DIAM_LT_320 | 41 | 2.1545 | 96.4612 | 116.7606 | 1488.4372 | 1
Public_sewer - FOUL-GRAVITY-VC-<=165mm-(150,225]-SWANSEA-PRE_PRIVATISATION | 42 | 1.6969 | 98.1581 | 96.0328 | 1584.47 | 2
Mapped PST - FOUL-CONNECTING SEWER-VC-<=165mm-(10,100]-SWANSEA | 43 | 1.9476 | 100.1057 | 115.9491 | 1700.4191 | 2
Public_sewer - COMBINED-GRAVITY-VC-<=165mm-(100,150]-NORTHEAST-WAR_TIME | 44 | 1.6969 | 101.8025 | 105.9385 | 1806.3576 | 2
Public_sewer - COMBINED-GRAVITY-FERROUS_1 | 45 | 2.6665 | 104.4691 | 170.5831 | 1976.9408 | 2
Public_sewer - COMBINED-GRAVITY-VC-<=165mm-(150,225]-SWANSEA | 46 | 2.4241 | 106.8932 | 156.6609 | 2133.6017 | 2
Public_sewer - COMBINED-GRAVITY-VC-<=165mm-(100,150]-WESTERN | 47 | 4.3634 | 111.2566 | 283.3252 | 2416.9268 | 2
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-PLASTIC_PE-DCWW | 48 | 2.4377 | 113.6943 | 164.7623 | 2581.6892 | 1
Public_sewer - COMBINED-GRAVITY-VC->165mm and <=320mm-(225,300]-GWENT | 49 | 1.6969 | 115.3912 | 120.3671 | 2702.0563 | 2
Public_sewer - COMBINED-GRAVITY-VC-<=165mm-(100,150]-SWANSEA | 50 | 3.6362 | 119.0273 | 269.508 | 2971.5643 | 2
Public_sewer - COMBINED-GRAVITY-VC->165mm and <=320mm-(225,300]-SWANSEA | 51 | 4.121 | 123.1483 | 311.9131 | 3283.4774 | 2
Public_sewer - FOUL-GRAVITY-VC->165mm and <=320mm-(225,300]-SWANSEA | 52 | 2.1817 | 125.33 | 168.3352 | 3451.8125 | 2
Public_sewer - COMBINED-GRAVITY-VC-<=165mm-(150,225]-GWENT | 53 | 2.9089 | 128.239 | 228.0339 | 3679.8465 | 2
Mapped PST - COMBINED-CONNECTING SEWER-VC-<=165mm-(10,100] | 54 | 4.3272 | 132.5661 | 349.2982 | 4029.1446 | 2
Mapped PST - COMBINED | 55 | 2.1953 | 134.7614 | 179.909 | 4209.0536 | 2
Public_sewer - COMBINED-GRAVITY-VC->165mm and <=320mm-(150,225]-VALLEYS | 56 | 4.121 | 138.8824 | 337.8506 | 4546.9042 | 2
Public_sewer - COMBINED-GRAVITY-VC->165mm and <=320mm-(225,300]-VALLEYS | 57 | 1.9393 | 140.8217 | 160.0428 | 4706.9469 | 2
Mapped PST - COMBINED-GRAVITY-VC | 58 | 1.6601 | 142.4818 | 145.1436 | 4852.0905 | 1
Public_sewer - COMBINED-GRAVITY-BRICK->625mm and <=1500mm-(900,1050] | 59 | 1.6969 | 144.1787 | 156.8611 | 5008.9516 | 1
Public_sewer - FOUL-GRAVITY-VC-<=165mm-(150,225]-SWANSEA-WAR_TIME | 60 | 1.6969 | 145.8756 | 163.0688 | 5172.0204 | 1
Mapped PST - COMBINED-CONNECTING SEWER-VC-<=165mm-(100,150] | 61 | 2.9018 | 148.7773 | 282.5603 | 5454.5808 | 1
Public_sewer - COMBINED-GRAVITY-VC-<=165mm-(100,150]-GWENT | 62 | 3.6362 | 152.4135 | 372.4253 | 5827.006 | 1
Rising mains - DIAM_GT_320 | 63 | 0.71432 | 153.1278 | 81.035 | 5908.0411 | 1
Public_sewer - FOUL-GRAVITY-VC-<=165mm-(100,150]-WESTERN | 64 | 2.9521 | 156.0799 | 354.3534 | 6262.3944 | 1
Mapped PST - FOUL-CONNECTING SEWER-VC-<=165mm-(10,100]-GWENT | 65 | 1.7199 | 157.7998 | 207.8676 | 6470.262 | 1
Public_sewer - COMBINED-GRAVITY-VC->165mm and <=320mm-(150,225]-SWANSEA | 66 | 1.6969 | 159.4967 | 207.1651 | 6677.4271 | 1
Mapped PST - FOUL-LATERAL DRAIN | 67 | 1.5667 | 161.0634 | 194.7987 | 6872.2258 | 1
Public_sewer - COMBINED-GRAVITY-VC->165mm and <=320mm-(150,225]-GWENT | 68 | 2.0707 | 163.1341 | 259.7462 | 7131.9721 | 1
Public_sewer - COMBINED-GRAVITY-VC-<=165mm-(150,225]-VALLEYS | 69 | 1.9393 | 165.0733 | 259.3739 | 7391.3459 | 1
Mapped PST - FOUL-CONNECTING SEWER | 70 | 1.5849 | 166.6582 | 214.2602 | 7605.6061 | 1
Public_sewer - FOUL-GRAVITY-VC-<=165mm-(100,150]-GWENT-PRE_PRIVATISATION | 71 | 2.1817 | 168.8399 | 326.7399 | 7932.346 | 1
Mapped PST - FOUL-CONNECTING SEWER-VC-<=165mm-(100,150] | 72 | 3.0281 | 171.868 | 459.7311 | 8392.0771 | 1
Public_sewer - COMBINED-GRAVITY-VC->165mm and <=320mm-(225,300] | 73 | 2.6665 | 174.5345 | 407.0486 | 8799.1257 | 1
Rising mains - DIAM_GT_320-COMBINED-RISING MAIN->320mm and <=625mm | 74 | 0.71432 | 175.2489 | 111.5427 | 8910.6684 | 1
Public_sewer - FOUL | 75 | 1.6969 | 176.9457 | 276.2875 | 9186.956 | 1
Public_sewer - COMBINED-GRAVITY-VC-<=165mm-(100,150]-NORTHEAST-PRE_PRIVATISATION | 76 | 1.6969 | 178.6426 | 278.2664 | 9465.2224 | 1
Mapped PST - FOUL-GRAVITY | 77 | 1.7261 | 180.3687 | 285.0869 | 9750.3093 | 1
Public_sewer - COMBINED-GRAVITY-VC->165mm and <=320mm-(150,225]-NORTHEAST | 78 | 2.1817 | 182.5504 | 375.6428 | 10125.9521 | 1
Public_sewer - COMBINED-GRAVITY-VC-<=165mm-(100,150]-VALLEYS | 79 | 1.9393 | 184.4897 | 339.3894 | 10465.3415 | 1
Public_sewer - FOUL-GRAVITY-VC->165mm and <=320mm-(150,225] | 80 | 4.3634 | 188.8531 | 807.8514 | 11273.1929 | 1
Mapped PST - FOUL-GRAVITY-VC-<=165mm-(100,150] | 81 | 2.0799 | 190.933 | 399.6797 | 11672.8726 | 1
Public_sewer - COMBINED-GRAVITY-VC-<=165mm-(100,150] | 82 | 3.1513 | 194.0844 | 607.5084 | 12280.381 | 1
Public_sewer - FOUL-GRAVITY | 83 | 5.0906 | 199.175 | 1001.7564 | 13282.1374 | 1
Mapped PST - FOUL-CONNECTING SEWER-VC-<=165mm-(10,100] | 84 | 3.1381 | 202.3131 | 619.9458 | 13902.0832 | 1
Public_sewer - FOUL-GRAVITY-VC-<=165mm-(150,225] | 85 | 2.9089 | 205.222 | 586.5723 | 14488.6555 | 1
Unmapped PST - FOUL_COMBINED_SURFACE-PST-B99_UNKN-<=165mm-(100,150]-VALLEYS-1 | 86 | 2.094 | 207.316 | 492.6086 | 14981.2641 | 1
Public_sewer - COMBINED-GRAVITY | 87 | 1.6969 | 209.0129 | 400.3641 | 15381.6282 | 1
Public_sewer - COMBINED-GRAVITY-VC->165mm and <=320mm-(150,225] | 88 | 2.9089 | 211.9218 | 783.2805 | 16164.9087 | 1
Public_sewer - COMBINED-GRAVITY-VC | 89 | 3.3938 | 215.3155 | 947.234 | 17112.1426 | 1
Unmapped PST - FOUL_COMBINED_SURFACE-PST-B99_UNKN-<=165mm-(100,150]-VALLEYS | 90 | 2.6392 | 217.9547 | 737.969 | 17850.1116 | 1
Public_sewer - FOUL-GRAVITY-VC-<=165mm-(100,150]-NORTHEAST | 91 | 2.1817 | 220.1364 | 655.5974 | 18505.709 | 1
Public_sewer - SURFACE WATER-GRAVITY-VC->165mm and <=320mm-(150,225] | 92 | 3.3938 | 223.5302 | 1021.9851 | 19527.6941 | 1
Mapped PST - OTHER | 93 | 0.022291 | 223.5525 | 7.0107 | 19534.7048 | 1
Public_sewer - COMBINED-GRAVITY-CONC | 94 | 3.1513 | 226.7038 | 1072.0413 | 20606.7461 | 1
Unmapped PST - FOUL_COMBINED_SURFACE-PST-B99_UNKN-<=165mm-(100,150]-SWANSEA-PRE_PRIVATISATION-1961_1980-BIN05_1961_1975 | 95 | 1.9538 | 228.6576 | 733.8924 | 21340.6385 | 1
Unmapped PST - FOUL_COMBINED_SURFACE-PST-B99_UNKN-<=165mm-(100,150]-SWANSEA | 96 | 3.6308 | 232.2884 | 1392.1405 | 22732.7791 | 1
Unmapped PST - FOUL_COMBINED_SURFACE-PST-B99_UNKN-<=165mm-(100,150]-NORTHWEST-1 | 97 | 2.2042 | 234.4926 | 892.2618 | 23625.0409 | 1
Public_sewer - SURFACE WATER-GRAVITY-VC-<=165mm-(100,150] | 98 | 1.6969 | 236.1895 | 714.4569 | 24339.4978 | 1
Unmapped PST - FOUL_COMBINED_SURFACE-PST-B99_UNKN-<=165mm-(100,150]-CENTRAL | 99 | 3.278 | 239.4675 | 1477.4085 | 25816.9063 | 1
Public_sewer - SURFACE WATER-GRAVITY-VC | 100 | 1.9393 | 241.4068 | 877.7104 | 26694.6167 | 1
Unmapped PST - FOUL_COMBINED_SURFACE-PST-B99_UNKN-<=165mm-(100,150]-NORTHEAST-PRE_PRIVATISATION | 101 | 1.5738 | 242.9806 | 714.5154 | 27409.132 | 1
Public_sewer - OTHER | 102 | 0.96964 | 243.9503 | 441.9896 | 27851.1216 | 1
Mapped PST - FOUL | 103 | 0.0056592 | 243.9559 | 2.6975 | 27853.8191 | 1
Public_sewer - FOUL-GRAVITY-VC-<=165mm-(100,150] | 104 | 1.9393 | 245.8952 | 941.0092 | 28794.8283 | 1
Unmapped PST - FOUL_COMBINED_SURFACE-PST-B99_UNKN-<=165mm-(100,150]-WESTERN-1 | 105 | 2.3535 | 248.2487 | 1145.3417 | 29940.17 | 1
Unmapped PST - FOUL_COMBINED_SURFACE-PST-B99_UNKN-<=165mm-(100,150]-NORTHEAST-1 | 106 | 2.4662 | 250.7149 | 1230.7084 | 31170.8784 | 1
Unmapped PST - FOUL_COMBINED_SURFACE-PST-B99_UNKN-<=165mm-(100,150]-GWENT | 107 | 3.278 | 253.9929 | 1642.4457 | 32813.324 | 1
Mapped PST - SURFACE WATER | 108 | 1.6019 | 255.5947 | 844.9697 | 33658.2937 | 1
Unmapped PST - FOUL_COMBINED_SURFACE-PST-B99_UNKN-<=165mm-(100,150] | 109 | 4.2553 | 259.85 | 2407.0391 | 36065.3328 | 1
Public_sewer - SURFACE WATER | 110 | 1.6969 | 261.5469 | 1059.8638 | 37125.1966 | 1

## Out of cohort size
Cohort Ref (user specified) | Material | Age | Age | Type | Formerly private sewers and lateral drains (s105A sewers) (Yes/No) | Pipe size | Pipe size | CWW21 | Fracture potential | Era | Region | Catchment | Sum of length (km) | Sum of collapses (over 5 year period) | Average annual collapses | Nominal expected collapses | Annual collapse rate tolerance (+/-50% as far as practicable) | Tolerance | Within tolerance | Average annual collapses per 1000km | Grade | Rank | Reason for being outside of tolerance
Mapped PST - COMBINED-CONNECTING SEWER-VC-<=165mm-(10,100] | VC |  |  | Combined | Yes | ≤165mm |  | 21.6 Formerly private sewers and lateral drains (s105A sewers) |  |  |  |  | 349.2982 | 21.6358 | 4.3272 | 2.5 | -0.73086 | +/-50% | No | 12.3881 | 2 | 54
Mapped PST - FOUL | Not used |  |  | Foul | Yes |  |  | 21.6 Formerly private sewers and lateral drains (s105A sewers) |  |  |  |  | 2.6975 | 0.028296 | 0.0056592 | 2.5 | 0.99774 | +/-50% | No | 2.098 | 1 | 103 | All residual foul PST that have not been assigned a cohort
Mapped PST - OTHER | Not used |  |  | Other | Yes |  |  | 21.6 Formerly private sewers and lateral drains (s105A sewers) |  |  |  |  | 7.0107 | 0.11145 | 0.022291 | 2.5 | 0.99108 | +/-50% | No | 3.1796 | 1 | 93 | All PST which did not fit into combined, foul or surface water - very few collapses
Public_sewer - COMBINED | Not used |  |  | Combined | No |  |  | 21.2 Combined sewers |  |  |  |  | 23.4242 | 2.4241 | 0.48482 | 2.5 | 0.80607 | +/-50% | No | 20.6975 | 2 | 38 | Largest number of cohorts covering combined public sewers. This is the residual cohort when all others have been accounted for.
Public_sewer - COMBINED-GRAVITY-VC-<=165mm-(100,150]-WESTERN | VC |  |  | Combined | No | ≤165mm |  | 21.2 Combined sewers |  |  | Western |  | 283.3252 | 21.817 | 4.3634 | 2.5 | -0.74536 | +/-50% | No | 15.4007 | 2 | 47 | Not enough collapses at the more granular level.
Public_sewer - COMBINED-GRAVITY-VC->165mm and <=320mm-(150,225]-VALLEYS | VC |  |  | Combined | No | >165mm and ≤320mm; |  | 21.2 Combined sewers |  |  | Valleys |  | 337.8506 | 20.6049 | 4.121 | 2.5 | -0.6484 | +/-50% | No | 12.1977 | 2 | 56 | Not enough collapses at the more granular level.
Public_sewer - COMBINED-GRAVITY-VC->165mm and <=320mm-(225,300]-SWANSEA | VC |  |  | Combined | No | >165mm and ≤320mm; |  | 21.2 Combined sewers |  |  | Swansea |  | 311.9131 | 20.6049 | 4.121 | 2.5 | -0.6484 | +/-50% | No | 13.212 | 2 | 51 | Not enough collapses at the more granular level.
Public_sewer - FOUL-GRAVITY | Not used |  |  | Foul | No |  |  | 21.1 Foul sewers |  |  |  |  | 1001.7564 | 25.4532 | 5.0906 | 2.5 | -1.0363 | +/-50% | No | 5.0817 | 1 | 83 | All residual foul gravity public sewers that have not been assigned a cohort
Public_sewer - FOUL-GRAVITY-VC-<=165mm-(100,150]-SWANSEA | VC |  |  | Foul | No | ≤165mm |  | 21.1 Foul sewers |  |  | Swansea |  | 234.3549 | 21.817 | 4.3634 | 2.5 | -0.74536 | +/-50% | No | 18.6188 | 2 | 40
Public_sewer - FOUL-GRAVITY-VC->165mm and <=320mm-(150,225] | VC |  |  | Foul | No | >165mm and ≤320mm; |  | 21.1 Foul sewers |  |  |  |  | 807.8514 | 21.817 | 4.3634 | 2.5 | -0.74536 | +/-50% | No | 5.4012 | 1 | 80
Public_sewer - OTHER | Not used |  |  | Other | No |  |  | 21.4 Other wastewater network pipes |  |  |  |  | 441.9896 | 4.8482 | 0.96964 | 2.5 | 0.61214 | +/-50% | No | 2.1938 | 1 | 102 | All public gravity sewers which did not fit into combined, foul or surface water - very few collapses
Rising mains - DIAM_GT_320-FOUL-RISING MAIN->320mm and <=625mm-PLASTIC_PVC-PRE_PRIVATISATION-(300,375]-1961_1980-GWENT-B13_1970-NASH | PVC | 1961 to 1980 |  | Foul |  | >320mm and ≤625mm; |  | 21.7 Sewage pumping mains |  | Pre-Privatisation | Gwent |  | 1.5358 | 10.7148 | 2.143 | 1 | -1.143 | +/-50% | No | 1395.3202 | 5 | 3 | The most detailed level for cohorts and still high number of collapses.
Rising mains - DIAM_LT_320-COMBINED-RISING MAIN-<=165mm | Not used |  |  | Combined |  | ≤165mm |  | 21.7 Sewage pumping mains |  |  |  |  | 124.9194 | 21.4297 | 4.2859 | 2.5 | -0.71437 | +/-50% | No | 34.3096 | 1 | 34
Rising mains - DIAM_LT_320-COMBINED-RISING MAIN->165mm and <=320mm-FERROUS_2 | Ferrous_2 |  |  | Combined |  | >165mm and ≤320mm; |  | 21.7 Sewage pumping mains |  |  |  |  | 79.0703 | 20.2391 | 4.0478 | 2.5 | -0.61913 | +/-50% | No | 51.1928 | 1 | 31
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm | Not used |  |  | Foul |  | ≤165mm |  | 21.7 Sewage pumping mains |  |  |  |  | 63.8025 | 20.2391 | 4.0478 | 2.5 | -0.61913 | +/-50% | No | 63.4432 | 1 | 27 | When all more detailed cohorts are removed, this is the residual collapses and lengths within this cohort.
Rising mains - DIAM_LT_320-FOUL-RISING MAIN-<=165mm-PLASTIC_PVC-PRE_PRIVATISATION-(0,100]-1961_1980-CENTRAL-B13_1970-COWBRIDGE | PVC | 1961 to 1980 |  | Foul |  | ≤165mm |  | 21.7 Sewage pumping mains |  | Pre-Privatisation | Central |  | 4.2683 | 20.2391 | 4.0478 | 2.5 | -0.61913 | +/-50% | No | 948.3393 | 4 | 4 | The most detailed level for cohorts and still high number of collapses.
Rising mains - DIAM_LT_320-FOUL-RISING MAIN->165mm and <=320mm-FERROUS_2-DCWW-(225,300]-1981_2000-WESTERN-B15_1990-ABERYSTWYTH_GLAN_YR_AFON | Ferrous_2 | 1981 to 2000 |  | Foul |  | >165mm and ≤320mm; |  | 21.7 Sewage pumping mains |  | DCWW | Western |  | 4.1279 | 19.0486 | 3.8097 | 2.5 | -0.52389 | +/-50% | No | 922.9181 | 4 | 5 | The most detailed level for cohorts and still high number of collapses.
Unmapped PST - FOUL_COMBINED_SURFACE-PST-B99_UNKN-<=165mm-(100,150] | Not used |  |  |  | Yes | ≤165mm |  | 21.6 Formerly private sewers and lateral drains (s105A sewers) |  |  |  |  | 2407.0391 | 21.2763 | 4.2553 | 2.5 | -0.7021 | +/-50% | No | 1.7678 | 1 | 109 | Difficult to split this group further for unmapped PST.