## Notes
Please send to email inbox: | wcam@cyfoethnaturiolcymru.gov.uk or wcam@naturalresourceswales.gov.uk
Please name file using the following convention: | "EDM Return DCWW_Wales Water Annual 2017.xls"
Submission date: | Annual Return is required 2 months after the end of the reporting season (end February)
Spill is defined as: | ““spill” one or more overflow events within a period of 12 hours or less will be considered to be one spill, one or more overflow events extending over a period of greater than 12 hours up to 36 hours will be considered to be 2 spills. Each subsequent 24 hour duration counts as 1 additional spill and the whole of the 24 hour block is included.”

## EDM Annual DCWW
Associated Asset ID | Permitted Site Name | Permit Number | Activity Reference (if more than one discharge on permit) | Region | Sewerage Catchment | Receiving water | Shellfishery (Only populate for storm overflows that have Shellfish water EDM requirements) | Bathing Beach (Only populate for storm overflows that have bathing water EDM requirements) | Total Duration (hours in decimals) of all spills prior to processing through 12-24 hour counting method | Counted Spills using 12-24 block counting method | Significant' counted spills BW/SW (where available) | Percentage complete data | Spill Frequency Trigger on Permit (BW / SFW / N/A) | SFTP Trigger (x spills per year / y spills per bathing season) | SFTP Trigger Exceedance | Comments
72282 | TREVETHIN STORM TANKS CHURCH LANE | AA0009401 |  | SE | Gwent | Afon Lwyd - source to conf Dowlais Bk |  |  | 200.5 | 53 | 53 | 99.93
32155 | LOWER PONTNEWYDD SSO | AA0009701 |  | SE | Gwent | Afon Lwyd - source to conf Dowlais Bk |  |  | 214.5 | 51 | 44 | 98.95
32135 | PONTNEWYNYDD SSO | AA0010901 |  | SE | Gwent | Afon Lwyd - source to conf Dowlais Bk |  |  | 2 | 8 | 0 | 99.71
31979 | CRICKHOWELL SEWERAGE RELIEF SSO | AA0013001 |  | SE | Bridgend Hereford & Mid | R Usk conf Afon Crawnon to conf Gavenny R |  |  | 3.5 | 10 | 10 | 53.84 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
31442 | A SEWAGE PUMPING STATION ROBERTSON | AA0017101 |  | SE | South East | Pantyreos Bk - source to Barrack Hill |  |  | 88.75 | 27 | 27 | 99.71
32124 | PONTYPOOL-COEDYGRIC (PANTEG RO | AA0018801 |  | SE | Gwent | Afon Lwyd - source to conf Dowlais Bk |  |  | 20.5 | 15 | 10 | 99.02
32087 | CSO 17 SPRINGFIELD ESTATE PONTLLANF | AA0020501 |  | SE | Cardiff | Sirhowy R - Rock Villas to conf Afon Ebwy |  |  | 325.5 | 86 | 86 | 94.53
31983 | CRICKHOWELL SEWERAGE SYSTEM | AA0021101 |  | South West |  | Usk conf Afon Crawnon to conf Gavenny R |  |  | 34.75 | 17 | 17 | 99.8
32133 | NEWPORT PILLMAWR RD RELIEF SEW | AA0025201 |  | SE | Gwent | Pantyreos Bk - source to Barrack Hill |  |  | 7 | 19 | 4 | 99.37
71494 | CSO ADJ SHAFTESBURY PS NEWPORT | AA0025601 |  | South East |  | USK |  |  | 76.5 | 21 | 21 | 99.98
72143 | CLYDACH CSO | AA0032501 |  | SE | Gwent | R Clydach - source to conf R Usk |  |  | 565 | 78 | 68 | 99.79
31219 | MAESYGWARTHA PS | AA0032601 |  | SE | Gwent | R Clydach - source to conf R Usk |  |  | 1000 | 91 | 81 | 99.24
30795 | ABERBAIDEN STW MONMOUTH | AB0034102 |  | South East |  | Usk conf Afon Crawnon to conf Gavenny R |  |  | 415.5 | 58 | 58 | 97.25
31060 | RAGLAN STW CHEPSTOW ROAD RAGLAN | AB0036502 |  | SE | South East | Nant y Wilcae - source to conf Olway Bk |  |  | 67.75 | 22 | 17 | 99.82
30948 | LLANFOIST SEWAGE TREATMENT WORKS ME | AB0038202 |  | SE | South East | R Usk - conf R Gavenny to conf Olway Bk |  |  | 475 | 61 | 61 | 99.98
33110 | MILL STREET SCREENS SSO ABERGAVEN | AB0038301 |  | SE | Valleys | R Usk conf Afon Crawnon to conf Gavenny R |  |  | 110 | 49 | 49 | 99.92
33112 | RAGLAN SSO NO. 1 | AB0038701 |  | SE | South East | Nant y Wilcae - source to conf Olway Bk |  |  | 3 | 4 | 2 | 78.21 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
31990 | BRECON SHOWFIELDS CSO BRECON POWYS | AB0041401 |  | SW | Bridgend Hereford & Mid Wales | R Usk - conf Afon Senni to conf Afon Crawnon |  |  | 262.5 | 45 | 45 | 99.42
30809 | BRECON STW | AB0041502 |  | SE | South East | R Usk - conf Afon Senni to conf Afon Crawnon |  |  | 1390.75 | 79 | 79 | 99.94
31988 | BRECON SEWERAGE SYSTEM | AB0041601 |  | SW | Bridgend Hereford & Mid Wales | R Usk - conf Afon Senni to conf Afon Crawnon |  |  | - | - | - | 0 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
71495 | CSO 52 TT ELECTRONICS TREGWILYM IND | AB0044301 |  | SE | Gwent | Ebbw R - conf Ebbw Fach R to Maes-glas |  |  | 15.25 | 4 | 4 | 99.93
31114 | USK STW LLANBADOC MONMOUTHSHIRE | AB0044802 |  | SE | South East | R Usk - conf R Gavenny to conf Olway Bk |  |  | 1500.5 | 123 | 121 | 99.89
30825 | BWLCH (S) STW LLANGYNIDIR | AB0049401 |  | SE | South East | R Usk conf Afon Crawnon to conf Gavenny R |  |  | 843.5 | 145 | 128 | 99.94
31429 | USK ROAD PS USK ROAD CAERLEON | AB0049901 |  | SE | South East | Afon Lwyd - conf Dowlais Bk to Pont Sadwrn |  |  | - | - | - | 0 |  |  |  | Telemetry archiving issue - escalated through business as usual process
71491 | CAERLEON WWTW (STW) CSO CAERLEON | AB0050001 |  | SE | Valleys | Afon Lwyd - conf Dowlais Bk to Pont Sadwrn |  |  | 490 | 85 | 85 | 99.92
33400 | CSO FIELD NO 6258 RHIWDERIN | AB0054601 |  | SE | Gwent | Ebbw R - conf Ebbw Fach R to Maes-glas |  |  | 76 | 49 | 36 | 99.12
31050 | LLANFRECHFA STORM TANKS PONTHIR | AB0064001 |  | South East |  | Afon Lwyd - below Mon and Brecon Canal |  |  | 1445.5 | 101 | 101 | 93.29
31050 | LLANFRECHFA STORM TANKS PONTHIR | AB0064002 |  | South East |  | Afon Lwyd - below Mon and Brecon Canal |  |  | 129.75 | 28 | 28 | 93.29
30996 | NASH STW WEST NASH ROAD NEWPORT | AB0067102 |  | SE | South East | Monks Ditch - source to Wainbridge |  |  | 230 | 33 | 33 | 60.78 |  |  |  | Telemetry archiving issue - escalated through business as usual process
31425 | UNDERWOOD PS UNDERWOOD NEWPORT | AB0068201 |  | SE | South East | Monks Ditch - source to Wainbridge |  |  | 854.75 | 94 | 91 | 99.69
31999 | CSO ROGERSTONE ADJ THORNHILL GDNS | AB0073101 |  | SE | Gwent | Ebbw R - conf Ebbw Fach R to Maes-glas |  |  | 12.5 | 29 | 13 | 93.94
33593 | CSO 47 ALCAN WORKS ROGERSTONE | AB0073102 |  | SE | Gwent | Ebbw R - conf Ebbw Fach R to Maes-glas |  |  | 663.75 | 55 | 55 | 98.52
802 | Efailnewydd WWTW, Efailnewydd, Pwllheli, LL53 8TN | AB3292HB |  | N | North West | Rhyd-Hir |  |  | 1546.5 | 189 | 167 | 100
74557 | Deri CSO | AB3397HZ |  | SE | Cardiff |  |  |  | 398.75 | 72 | 72 | 99.99
31029 | Pandy STW Overflow | AB3493FU |  | SE | South East | Afon Honddu - source to conf R Monnow |  |  | 64.25 | 13 | 13 | 99.94
30891 | Great oak STW Overflow | AB3493ZB |  | SE | South East | Clawdd Bk - source to conf R Usk |  |  | 643 | 59 | 59 | 99.96
74710 | Berthglyd CSO | AB3494ZL |  | N | North | Gele |  |  | 17 | 15 | 5 | 99.39
817 | Garndolbenmaen | AB3495FT |  | N | North West | Dwyfawr - lower |  |  | 1058.5 | 100 | 100 | 100
477 | Rowen | AB3495HF |  | N | North West | Roe |  |  | 624.5 | 125 | 125 | 100
505 | Aberdaron STW | AB3495ZU |  | N | North West | Daron |  |  | 221.75 | 24 | 24 | 99.82
30842 | Christchurch STW Overflow | AB3496CK |  | SE | South East | Llwynau Bk - source to conf R Usk |  |  | 1209.75 | 132 | 132 | 99.55
763 | Chwilog STW Overflow | AB3496ZG |  | N | North West | Wen (Lleyn Peninsula) |  |  | 814.5 | 90 | 90 | 100
31002 | Newbridge on Wye STW Overflow | AB3497FZ |  | SE | South East | R Wye - conf Afon Elan to conf R Ithon |  |  | 166.75 | 38 | 38 | 99.98
811 | Y Ffor WwTW Storm Overflow | AB3497HE |  | North |  | Erch - lower |  |  | 3536.75 | 279 | 279 | 99.9
897 | Lithfaen STW Overflow | AB3497ZT |  | N | North West | Rhyd-Hir |  |  | 3318.75 | 155 | 155 | 99.97
31062 | Rhayader STW | AB3498CC |  | South East |  | Wye - conf to conf Afon Marteg to conf Afon Elan |  |  | 157.75 | 37 | 37 | 99.17
50741 | Combined Sewer Overflow at Pentrecwrt | AB3498ZF |  | SW | South West | Teifi - conf with Nant Wern-Macwydd to tidal limit |  |  | 3010.25 | 289 | 260 | 97.54
50769 | Rosemarket | AB3499CN |  | SW | South West | Westfield Pilll - headwaters to tidal limit |  |  | 429.5 | 86 | 76 | 99.96
72878 | Ynys Bridge 1 CSO Tongwynlais Cardiff | AB3590FB_01 |  | SE | South East | R Taff - conf Rhondda R to Castle Street |  |  | 84.25 | 19 | 19 | 79.2 |  |  |  | Communications issue, resolved in October 2021.
72877 | Ynys Bridge 2 CSO Tongwynlais Cardiff | AB3590FB_02 |  | SE | South East | R Taff - conf Rhondda R to Castle Street |  |  | 355.75 | 39 | 39 | 97.98
72688 | Gaddarn Reach SPS | AB3595HZ |  | SW | South West | Westfield Pilll - headwaters to tidal limit |  |  | 0 | 0 | 0 | 100
70923 | Sticle Path CSO | AB3596ZT |  | SW | West | Nant Cwm Croes y Ceiliog - HW to Tidal Limit |  |  | 132 | 58 | 58 | 99.59
72697 | Maes Y Fyynon SPS | AB3597CC |  | SW | South West | Brandy Brook - headwaters to tidal limit |  |  | 0 | 0 | 0 | 100
52139 | Pembroke Dock Sycamore St | AB3597FE |  | SW | West | Cocheston Pill - headwaters to tidal limit |  |  | 6.25 | 11 | 6 | 98.78
51125 | Porthyrhyd SPS | AB3598CN |  | SW | South West | Gwendraeth Fach - headwaters to tidal limit |  |  | 1042.75 | 77 | 77 | 100
72964 | Waungoch SPS | AB3598FW |  | SW | South West | Gwili - headwaters to tidal limit |  |  | 1.25 | 2 | 1 | 100
31084 | St Fagans STW Storm | AB3599CV |  | SE | Central | Ely R - conf Nant Clun to Allot Gardens, Ely |  |  | 1504.75 | 147 | 147 | 99.93
51001 | Llanddarog SPS | AB3691FU |  | SW | South West | Gwendraeth Fach - headwaters to tidal limit |  |  | 251.5 | 32 | 31 | 100
50908 | Cynwyl Village Bridge SPS | AB3691HG |  | SW | West | Gochen - headwaters to confluence with Duad |  |  | 41 | 8 | 7 | 86.96 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
72324 | Combined Sewer Overflow at Sketty Green | AB3694FF |  | SW | Swansea | Swansea Bay |  | Swansea Bay | 109 | 21 | 21 | 99.46 | BW | 5 in Bathing Season
72752 | Nelson Quay SPS CSO | AB3794CH |  | SW | South West | Castle Pill - headwaters to tidal limit |  |  | 0 | 0 | 0 | 100
72687 | Honeyborough SPS CSO | AB3794FZ |  | SW | South West | Westfield Pilll - headwaters to tidal limit |  |  | 0 | 0 | 0 | 100
70927 | Carmarthen Pentremeurig Road CSO | AB3794HE |  | SW | West | Tawelon - headwaters to tidal limit |  |  | 6.75 | 12 | 12 | 67.51 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
52623 | Park Hinds CSO | AB3794ZT |  | SW | South West | Tywi - Bishop's Pond to conf with Gwili and TL |  |  | 54 | 5 | 5 | 100
71343 | Llanelli – O/S Thomas Brothers | AB3795CC |  | SW | West | Lliedi - headwaters to tidal limit |  |  | 0 | 0 | 0 | 99.73
71347 | Llanybydder – Oriel Jones | AB3795FE |  | SW | West | Duar - headwaters to confluence with Teifi |  |  | 14.5 | 13 | 9 | 57.05 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
51165 | St Clears Pumping Station | AB3795ZF |  | SW | South West | Holyhead Bay |  |  | 2233.25 | 212 | 197 | 100
72429 | Pentremeurig Road CSO | AB3796CN |  | SW | West | Tawelon - headwaters to tidal limit |  |  | 0 | 0 | 0 | 99.99
72015 | Pencader Bridge | AB3796FW |  | SW | West | Talog - headwaters to confluence with Tyweli |  |  | 215.75 | 25 | 24 | 99.45
53061 | Cwmdwrfran SPS | AB3796ZZ |  | SW | South West | Gwili - Duad conf to conf with Tywi at spring TL |  |  | 3.25 | 3 | 3 | 98.32
72023 | Carmarthen Market | AB3797CV |  | SW | West | Tywi - Bishop's Pond to conf with Gwili and TL |  |  | 2.5 | 6 | 3 | 99.38
72484 | Ffos y Ffin | AB3797FR |  | SW | West | Ceri Brook - headwaters to tidal limit |  |  | 87.75 | 27 | 22 | 89.59 |  |  |  | Communications issue, resolved in November 2021.
71375 | Llanelli Head Post Office | AB3797HY |  | SW | West | Lliedi - headwaters to tidal limit |  |  | 23 | 20 | 20 | 99.45
50674 | Llangynog STW | AB3798CA | [6 empty] | 2.5 | 2 | 2 | 99.44
30820 | BRYNMAWR STW BLACKROCK BRYNMAWR | AC0085602 |  | SE | South East | R Clydach - source to conf R Usk |  |  | - | - | - | 0 |  |  |  | Telemetry archiving issue - escalated through business as usual process
33332 | CSO 21 REAR OF CAPEL Y BABEL | AC0088301 |  | SE | Gwent | Sirhowy R - Rock Villas to conf Afon Ebwy |  |  | 333.5 | 48 | 48 | 99.27
32004 | CSO 36 CWMCARN HIGH SCHOOL CHAPEL F | AC0092301 |  | SE | Gwent | Ebbw R - conf Ebbw Fach R to Maes-glas |  |  | 223 | 29 | 29 | 38.99 |  |  |  | Communications issue, resolved in August 2021.
30855 | CRICKHOWELL STW ABERGAVENNY ROAD | AC0094702 |  | SE | South East | R Usk conf Afon Crawnon to conf Gavenny R |  |  | 903.5 | 112 | 110 | 99.9
32136 | PONTYPOOL CHARLESVILLE TRUNK SEWAR | AC0108801 |  | SE | Gwent | Afon Lwyd - source to conf Dowlais Bk |  |  | 1560.5 | 103 | 94 | 98.9
70365 | BLAENAVON TRUNK SEWER CSO BRIDGE ST | AC0108901 |  | SE | Gwent | Afon Lwyd - source to conf Dowlais Bk |  |  | 275.25 | 69 | 57 | 99.14
31154 | BRECON - WATTON 10 METRES SOUTH OF | AC0109202 |  | SE | South East | R Usk - conf Afon Senni to conf Afon Crawnon |  |  | 278.25 | 66 | 66 | 99.65
33343 | TREDEGAR SSO | AC0109801 |  | SE | Cardiff | Sirhowy R - source to Rock Villas |  |  | 0 | 0 | 0 | 98.41
33346 | WESTERN VALLEY TRUNK SEWER SSO | AC0109802 |  | SE | Valleys | Sirhowy R - source to Rock Villas |  |  | 41.5 | 45 | 25 | 91.7
71204 | PONTYGOF SSO EBBW VALE | AC0109901 |  | SE | Valleys | Ebbw R - source to conf Ebbw Fach R |  |  | 79.25 | 22 | 15 | 89.91 |  |  |  | Communications issue, resolved in December 2021.
32020 | CWM SSO | AC0110101 |  | South East |  | Ebbw R - source to conf Ebbw Fach R |  |  | - | - | - | 0 |  |  |  | Communications issue - access issue
33262 | SENNYBRIDGE STW | AD0000601 |  | South East |  | Usk - conf Afon Senni to conf Afon Crawnon |  |  | 2.25 | 6 | 6 | 99.91
30853 | CRAY STW | AD0000801 |  | SE | South East | Unnamed trib - source to conf Afon Senni |  |  | 1.75 | 4 | 4 | 98.84
31104 | TRECASTLE STW | AD0001001 |  | SE | South East | R Usk - conf Afon Hydfer to conf Afon Crai |  |  | 592 | 86 | 79 | 99.99
31099 | TALYBONT SEWAGE TREATMENT WORKS TAL | AD0001702 |  | SE | South East | Caerfanell - source to conf R Usk |  |  | 130.5 | 30 | 22 | 99.99
33330 | A COMBINED SEWER OVERFLOW CSO 119 | AD0002801 |  | SE | Gwent | Ebbw R - conf Ebbw Fach R to Maes-glas |  |  | 1022 | 86 | 86 | 98.73
32086 | CSO OPP WHITE LION COTTAGES TREDEGR | AD0002901 |  | SE | Valleys | Sirhowy R - source to Rock Villas |  |  | 94.5 | 30 | 21 | 75.46 |  |  |  | Communications issue, resolved in April 2021.
32085 | A CSO AT THE REAR OF HILL REST | AD0002902 |  | SE | Valleys | Sirhowy R - source to Rock Villas |  |  | 192.75 | 56 | 56 | 99.66
32084 | CSO 32084 SCWRFA ROAD TREDEGAR | AD0002903 |  | SE | Valleys | Sirhowy R - source to Rock Villas |  |  | 95 | 29 | 21 | 99.93
32083 | CSO OPP 1 DUKESTOWN ROAD TREDEGAR | AD0002904 |  | SE | Valleys | Sirhowy R - source to Rock Villas |  |  | 151.25 | 37 | 32 | 99.94
32081 | A CSO AT REAR OF CHURCH SQ TREDEGAR | AD0002906 |  | SE | Valleys | Sirhowy R - source to Rock Villas |  |  | 103.75 | 42 | 42 | 99.94
71573 | CSO 8 EDWARD TERRACE TREDEGAR | AD0002908 |  | SE | Valleys | Sirhowy R - source to Rock Villas |  |  | 167 | 63 | 63 | 99.05
32077 | A CSO OPPOSITE NO1 PARK PLACE | AD0002909 |  | SE | Valleys | Sirhowy R - source to Rock Villas |  |  | 168.25 | 63 | 48 | 98.93
32076 | WVTS-TREDEGAR (MH G94) SSO | AD0002910 |  | SE | Valleys | Sirhowy R - source to Rock Villas |  |  | 14.75 | 24 | 10 | 67.54 |  |  |  | Communications issue - access issue
32075 | CSO 32075 OPPOSITE GARIBALDI BRIDGE | AD0002911 |  | SE | Valleys | Sirhowy R - source to Rock Villas |  |  | 174 | 45 | 45 | 99.93
32074 | WVTS-TREDEGAR (MH G91) SSO | AD0002912 |  | SE | Valleys | Sirhowy R - source to Rock Villas |  |  | 13.25 | 31 | 10 | 99.12
71572 | CSO OPP 121 VALE TERRACE TREDEGAR | AD0002913 |  | SE | Valleys | Sirhowy R - source to Rock Villas |  |  | 0.25 | 1 | 0 | 99.62
32071 | CSO AT POCHIN CRESCENT TREDEGAR | AD0002915 |  | SE | Valleys | Sirhowy R - source to Rock Villas |  |  | 273.5 | 69 | 69 | 98.56
32067 | WVTS-TREDEGAR (MH G57) SSO | AD0002919 |  | SE | Valleys | Sirhowy R - source to Rock Villas |  |  | 57.25 | 19 | 11 | 82.35 |  |  |  | Communications issue, resolved in May 2021.
32080 | TREDEGAR BROMPTON TIPS WVTS SS | AD0004801 |  | SE | Valleys | Sirhowy R - source to Rock Villas |  |  | 34.75 | 11 | 11 | 99.27
33335 | WVTS-NORTH CELYNEN COLLIERY SS | AD0004813 |  | SE | Gwent | Ebbw R - conf Ebbw Fach R to Maes-glas |  |  | 4.75 | 6 | 6 | 99.12
70356 | WVTS-NANTYGLO (FORGE ROW) SSO | AD0004816 |  | SE | Valleys | Ebbw Fach R - source to conf Ebbw R |  |  | 1 | 3 | 1 | 99.61
33336 | WVTS-NANTYGLO STATION SSO | AD0004817 |  | SE | South East | Ebbw Fach R - source to conf Ebbw R |  |  | 2 | 3 | 2 | 99.89
32090 | CSO 105 SIX BELLS COLLIERY ABERTI | AD0004820 |  | SE | Valleys | Ebbw Fach R - source to conf Ebbw R |  |  | 9 | 7 | 7 | 99.16
32050 | CSO 16 WOODFIELD ROW BLACKWOOD | AD0004823 |  | SE | Valleys | Sirhowy R - Rock Villas to conf Afon Ebwy |  |  | 101.25 | 47 | 47 | 98.02
32169 | VIADUCT ROAD CSO GARNIFFAITH ABERSY | AD0007801 |  | SE | Gwent | The Cwm Ffrwd |  |  | 564.75 | 98 | 98 | 99.01
71794 | HOSPITAL ROAD CSO ST JOHNS AMBULAN | AD0007901 |  | SE | Gwent | Afon Lwyd - source to conf Dowlais Bk |  |  | 203 | 60 | 60 | 99.74
32122 | LOWER NEW INN (PONTYFELIN LANE | AD0008001 |  | SE | East |  |  |  | 1050.25 | 128 | 128 | 98.45
32162 | (RAILWAY TERRACE) SEBASTAPOL | AD0008101 |  | SE | Gwent | Afon Lwyd - source to conf Dowlais Bk |  |  | 73.75 | 37 | 37 | 99.33
32127 | LEISURE CENTRE SSO TROSNANT STREET | AD0008301 |  | SE | Gwent | Afon Lwyd - source to conf Dowlais Bk |  |  | 240.5 | 58 | 58 | 99
32021 | WVTS-CWM (DUFFRYN PLACE) SSO | AD0008601 |  | SE | Valleys | Ebbw R - source to conf Ebbw Fach R |  |  | 3.75 | 7 | 3 | 99.37
33379 | WVTS-CWM (MH D41) SSO | AD0008603 |  | SE | Valleys | Ebbw R - source to conf Ebbw Fach R |  |  | 0.25 | 1 | 0 | 90.31
32025 | CSO 31 ADJ STEELWORKS RD CAR PARK | AD0008604 |  | SE | Valleys | Ebbw R - source to conf Ebbw Fach R |  |  | 88.25 | 26 | 26 | 99.94
32027 | CSO 29 OPP THE CROFT STEELWORKS RD | AD0008605 |  | SE | Valleys | Ebbw R - source to conf Ebbw Fach R |  |  | 89 | 27 | 27 | 99.94
74640 | CSO NO.32031 EBBW VALE RUGBY GROUND | AD0008607 |  | SE | Valleys | Ebbw R - source to conf Ebbw Fach R |  |  | 1.75 | 1 | 1 | 99.8
32033 | RIVERSIDE DOCTORS SURGERY EBBW VALE | AD0008610 |  | SE | Valleys | Ebbw R - source to conf Ebbw Fach R |  |  | 777.5 | 89 | 89 | 99.94
32103 | NANTYGLO SEWER NO 6 SSO | AD0008801 |  | SE | Valleys | Ebbw Fach R - source to conf Ebbw R |  |  | 1 | 3 | 1 | 95.58
32102 | NANTYGLO SEWER NO 5 SSO | AD0008901 |  | SE | Valleys | Ebbw Fach R - source to conf Ebbw R |  |  | 0 | 0 | 0 | 99.89
32097 | WEST SIDE SEWER SSO | AD0009001 |  | SE | South East | Ebbw Fach R - source to conf Ebbw R |  |  | 8.25 | 8 | 8 | 99.3
32092 | WVTS-ABERTILLERY (GLANDWR STRE | AD0009302 |  | SE | Valleys | Ebbw Fach R - source to conf Ebbw R |  |  | 13.75 | 18 | 6 | 99.56
32091 | WVTS-SIX BELLS SSO | AD0009303 |  | SE | Valleys | Ebbw Fach R - source to conf Ebbw R |  |  | 7 | 14 | 5 | 99.23
32110 | WVTS-BROOKSIDE ROW, CWMTILLERY SSO | AD0009305 |  | SE | South East | Ebbw Fach R - source to conf Ebbw R |  |  | 555 | 105 | 92 | 97.44
32109 | WVTS-ABERTILLERY (DIVISION STR | AD0009306 |  | SE | Cardiff | Ebbw Fach R - source to conf Ebbw R |  |  | 93.75 | 41 | 41 | 99.09
32088 | CSO 38 BROOKLANDS SSO PONTYWAUN | AD0009407 |  | SE | Gwent | Ebbw R - conf Ebbw Fach R to Maes-glas |  |  | 94.25 | 53 | 38 | 97.74
32047 | CSO 18 OLD TRAM ROAD SSO PONTLLANF | AD0009505 |  | SE | Cardiff | Sirhowy R - Rock Villas to conf Afon Ebwy |  |  | 181 | 54 | 54 | 99.31
32044 | CSO 20 OLD MILL NEWPORT ROAD | AD0009506 |  | SE | Valleys | Sirhowy R - Rock Villas to conf Afon Ebwy |  |  | 1025.25 | 108 | 108 | 99.13
32043 | WVTS-WYLLIE HALT SSO | AD0009507 |  | SE | Gwent | Sirhowy R - Rock Villas to conf Afon Ebwy |  |  | 64 | 22 | 13 | 96.38
32042 | WVTS-CWMFELINFACH SSO | AD0009508 |  | SE | Gwent | Sirhowy R - Rock Villas to conf Afon Ebwy |  |  | 0 | 0 | 0 | 99.32
32038 | WVTS-WATTSVILLE (RECREATION GR | AD0009510 |  | SE | Cardiff | Sirhowy R - Rock Villas to conf Afon Ebwy |  |  | 26.75 | 36 | 15 | 98.56
71571 | CSO CWM ROAD ARGOED CAERPHILLY | AD0009905 |  | SE | Gwent | Sirhowy R - source to Rock Villas |  |  | 47.25 | 19 | 19 | 99.53
32144 | LIMEKILN ROAD SSO PONTYPOOL | AD0010601 |  | SE | Gwent | Afon Lwyd - source to conf Dowlais Bk |  |  | 0.25 | 1 | 0 | 99.35
32123 | PONTYPOOL-COEDYGRIC (PANTEG RO | AD0010604 |  | SE | Gwent | Afon Lwyd - source to conf Dowlais Bk |  |  | 438.5 | 84 | 84 | 95.11
72140 | ABERSYCHAN CSO COED-YR-EOS FARM | AD0010605 |  | SE | Gwent | Afon Lwyd - source to conf Dowlais Bk |  |  | - | - | - | 0 |  |  |  | Data unreliable from 01/01/2021 to 31/12/2021. Due to erratic telemetry signal. Instrumentation task escalated through business as usual for instrumentation defect.
32128 | HANBURY ROAD SSO PONTYPOOL | AD0010611 |  | SE | Gwent | Afon Lwyd - source to conf Dowlais Bk |  |  | 24.5 | 33 | 18 | 96.87
32126 | PONTYPOOL (PONTYMOILE) SSO | AD0010612 |  | SE | Gwent | Afon Lwyd - source to conf Dowlais Bk |  |  | 852.75 | 100 | 100 | 98.71
32146 | RISING SUN BRIDGE SS CWMAVON | AD0010616 |  | SE | Gwent | Afon Lwyd - source to conf Dowlais Bk |  |  | 81.25 | 50 | 34 | 97.55
32164 | Overflow at Albion Road | AD0010620 |  | SE | Gwent | Trosnant Brook |  |  | - | - | - | 0 |  |  |  | Data unreliable from 01/01/2021 to 31/12/2021. Due to erratic telemetry signal. Instrumentation task escalated through business as usual for instrumentation defect.
32119 | CHAPEL LANE SSO EDLOGAN | AD0010621 |  | SE | Gwent | Afon Lwyd - source to conf Dowlais Bk |  |  | 109.5 | 29 | 22 | 99.33
71658 | PONTYPOOL (LIMEKILN ROAD BRIDG | AD0010622 |  | SE | Cardiff | Afon Lwyd - source to conf Dowlais Bk |  |  | 351 | 58 | 58 | 82.49 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
32142 | LEIGH ROAD SSO PONTYPOOL | AD0010623 |  | SE | Gwent | Afon Lwyd - source to conf Dowlais Bk |  |  | 0 | 0 | 0 | 99.32
32139 | PONTNEWYNYDD - MILL ROAD | AD0010625 |  | SE | Gwent | Afon Lwyd - source to conf Dowlais Bk |  |  | 0 | 0 | 0 | 99.62
32157 | PORTHMAWR ROAD SSO CWMBRAN | AD0013201 |  | SE | Gwent | Cwmbran Brook |  |  | 334.25 | 86 | 74 | 98.07
32160 | PONTNEWYDDSSO STANLEY PLACE CWMBRAN | AD0013401 |  | SE | Gwent | Afon Lwyd - source to conf Dowlais Bk |  |  | 12.25 | 21 | 7 | 99.3
32151 | TY COCH CSO TY COCH WAY CWMBRAN , | AD0013701 |  | SE | Gwent | Dowlais Bk - source to conf Afon Lwyd |  |  | 382.25 | 61 | 61 | 98.91
32117 | LLANTARNAM (CONVENT GROUNDS) S | AD0013801 |  | SE | Gwent | Afon Lwyd - source to conf Dowlais Bk |  |  | 4.75 | 8 | 8 | 93.57
32158 | CWMBRAN (WOODSIDE ROAD) SSO | AD0014001 |  | SE | Gwent | Cwmbran Brook |  |  | 0 | 0 | 0 | 95.69
72138 | COED FARM CSO CWMAVON BLAENAVON | AD0014801 |  | SE | Gwent | Afon Lwyd - source to conf Dowlais Bk |  |  | 14.5 | 22 | 9 | 99.93
70364 | FORGESIDE CSO IRON BRIDGE PICNIC | AD0015001 |  | SE | Gwent | Afon Lwyd - source to conf Dowlais Bk |  |  | 92.5 | 19 | 17 | 99.64
32300 | A CSO AT JACKSONS BRIDGE | AE1001303 |  | SE | Valleys | R Taff - conf Taf Fechan to conf R Cynon |  |  | 315.25 | 78 | 78 | 99.54
73520 | NEW ROAD SEWERAGE SYSTEM (REDESIGNE | AE1006001 | [6 empty] | 2897.75 | 150 | 150 | 99.79
32532 | CSO GELLIFAELOG SCHOOL ROCKY ROAD | AE1006601 |  | SE | Valleys | Nant Morlais - source to conf R Taff |  |  | 154.5 | 59 | 59 | 99.35
32526 | TRELEWIS - REAR OF GLYNBARGOED | AE1010601 |  | SE | Valleys | Pandy Brook Source to Taff Bargoed |  |  | 470.5 | 126 | 126 | 95.58
31333 | NANT TALWG PS BARRY | AE1010701 |  | SE | Central | River Nant Talwg |  | Cold Knap | 7.5 | 4 | 4 | 95.45 | BW | 5 in Bathing Season
32319 | CSO GYLFACH ROAD PORTH RHONDDA | AE1016301 |  | SE | Cardiff | Rhondda R - source to conf Afon Rhondda Fach |  |  | 1200 | 157 | 157 | 99.94
33504 | HIRWAUN - ON TRAMWAY | AE2001601 |  | South East |  | Afon Cynon - source to conf Aman R |  |  | 0.25 | 1 | 1 | 75.39 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
32466 | HARRIET STREET CSO, opposite Arthur's Place | AE2001801 |  | SE | Cardiff | Afon Cynon - source to conf Aman R |  |  | 0.5 | 2 | 2 | 95.77
32513 | CSO AT TUDOR TCE BACK LANE ABERDARE | AE2002301 |  | SE | Valleys | Afon Cynon - source to conf Aman R |  |  | 1.25 | 5 | 5 | 99.79
32522 | ABERNANT - OUTSIDE 10 FORGE TI | AE2002401 |  | SE | Valleys | Nant Wenallt |  |  | 28.25 | 34 | 18 | 79.97 |  |  |  | Communications issue, resolved in June 2021.
32512 | CSO AT BOTTOM MONK STREET | AE2002701 |  | SE | Valleys | Afon Cynon - source to conf Aman R |  |  | 301 | 63 | 63 | 81.18 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
73370 | ABERAMAN - CARDIFF RD/GWAWR ST | AE2003001 |  | SE | Cardiff | Aman R - source to conf Afon Cynon |  |  | 0 | 0 | 0 | 98.68
32508 | STORM WATER OVERFLOW LOCATION NO.22 | AE2003601 |  | SE | Valleys | R Cynon - conf Aman R to conf R Taff |  |  | 56.75 | 25 | 25 | 99.81
32498 | GODREAMAN - ALONGSIDE REAR OF | AE2004801 |  | SE | Cardiff | Aman R - source to conf Afon Cynon |  |  | 2 | 5 | 3 | 95.45
33507 | ROBERTSTOWN - OUTSIDE 1 WELLIN | AE2005701 |  | SE | Cardiff | Afon Cynon - source to conf Aman R |  |  | 0 | 0 | 0 | 64.66 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
70064 | A Combined Sewer Overflow Rear Of In Lane, R/O 89 Corneswell Rd | AE2015001 |  | SE | Central | The Sully Brook |  | Jacksons Bay Barry | 1 | 4 | 4 | 99.62 | BW | 5 in Bathing Season
33262 | HARTLAND ROAD LLANRUMNEY CARDIFF | AE2015302 |  | SE | Central | Rhymney R - conf Nant Cylla to Chapel Wood |  |  | 0 | 0 | 0 | 99.92
32258 | CARDIFF-PENYLAN ROAD UNDER BRIDGE | AE2015304 |  | SE | Cardiff | Unnamed trib - source to conf Rhymney R |  |  | 0 | 0 | 0 | 99.62
71834 | EAST ORCHARD CASTLE CSO ST ATHAN | AE2017101 |  | SE | Cardiff | Thaw - headwaters to confluence with Kenson |  |  | 154.5 | 23 | 22 | 97.65
71835 | CASTLETON WOODS RILLS VALLEY CSO | AE2017102 |  | SE | Cardiff | Thaw - headwaters to confluence with Kenson |  |  | 83.5 | 54 | 54 | 97.55
72513 | STORMWATER OVERFLOWS | AE2017201 |  | SE | Cardiff | Rhymney R - conf Nant Cylla to Chapel Wood |  |  | 237.75 | 104 | 104 | 70.39 |  |  |  | Data unreliable from 01/01 - 27/03/2021. Due to erratic telemetry signal. Communications issue from 27/03 to 12/04/21.
72533 | ABERBARGOED - REAR OF BEDWELLT | AE2017305 |  | SE | Gwent | Rhymney R - Nant Bargod Rhymni to conf Nant Cyl |  |  | 3.75 | 14 | 1 | 98.78
32234 | BARGOED COLLIERY SSO | AE2017307 |  | SE | Cardiff | Rhymney R - Nant Bargod Rhymni to conf Nant Cyl |  |  | 1.5 | 4 | 1 | 99.32
71944 | HIGH STREET GLAN-Y-NANT PENGAM | AE2017309 |  | SE | Cardiff | Rhymney R - Nant Bargod Rhymni to conf Nant Cyl |  |  | 16.5 | 13 | 9 | 99.2
33256 | FLEUR-DE-LYS - REAR OF GLANDDU | AE2017311 |  | SE | Cardiff | Monks Ditch - source to Wainbridge |  |  | 1 | 2 | 1 | 98.09
32217 | FLEUR-DE-LIS - REAR OF VICTORI | AE2017316 |  | SE | Gwent | Rhymney R - Nant Bargod Rhymni to conf Nant Cyl |  |  | 0 | 0 | 0 | 99.62
32202 | CSO DOWNSTREAN SUNNYBANK FM BEDWAS | AE2017401 |  | SE | Gwent | Rhymney R - conf Nant Cylla to Chapel Wood |  |  | - | - | - | 0 |  |  |  | Communications issue - access issue
32279 | RHYDYFELIN - CARDIFF ROAD - OP | AE2017701 |  | SE | Cardiff | R Taff - conf Rhondda R to Castle Street |  |  | 0.5 | 1 | 1 | 77.96 |  |  |  | Communications issue, resolved in October 2021.
32282 | YNYSANGHARAD HIGH LEVEL RELIEF CSO | AE2017703 |  | SE | Cardiff | R Taff - conf Rhondda R to Castle Street |  |  | 0 | 0 | 0 | 96.43
33553 | GLYN STREET CSO GLYN ST YNYSYBWL | AE2018203 |  | SE | Valleys | Nant Clydach - source to conf R Taff |  |  | 478.25 | 94 | 94 | 99.1
32358 | TREHERBERT-BLAENCWM ROAD/TYDRA | AE2018401 |  | SE | Valleys | Rhondda R - source to conf Afon Rhondda Fach |  |  | 124.75 | 24 | 20 | 96.26
32355 | TREHERBERT - JUNCTION BUTE ST/ | AE2018402 |  | SE | Valleys | Rhondda R - source to conf Afon Rhondda Fach |  |  | 0.75 | 2 | 1 | 99.83
32348 | TREORCHY - M/H AT SIDE OF BOYS | AE2018404 |  | SE | Valleys | Rhondda R - source to conf Afon Rhondda Fach |  |  | 0 | 0 | 0 | 93.46
31225 | REES STREET PUIMPING STATION GELLI | AE2018407 |  | SE | Central | Rhondda R - source to conf Afon Rhondda Fach |  |  | 40.25 | 29 | 29 | 99.93
71792 | GELLIGALED PK CSO YSTRAD RHONDDA | AE2018408 |  | SE | Valleys | Rhondda R - source to conf Afon Rhondda Fach |  |  | 390.5 | 78 | 78 | 98.11
31293 | LLWYNYPIA PS OFF OAKFIELD TERRACE | AE2018409 |  | SE | Central | Rhondda R - source to conf Afon Rhondda Fach |  |  | 53.5 | 39 | 29 | 99.93
32322 | DINAS - DINAS RD STATION ROAD | AE2018411 |  | SE | Valleys | Rhondda R - source to conf Afon Rhondda Fach |  |  | 387.5 | 110 | 110 | 97.31
31416 | A PS AT TREHAFOD COUNTY PRIMARY SCH | AE2018414 |  | SE | Central | Rhondda R - conf Afon Rhondda Fach to conf R Ta |  |  | 65.75 | 69 | 69 | 99.91
32359 | WATTSTOWN-BAILEY ST LAND RECLA | AE2018415 |  | SE | Valleys | Rhondda Fawr River |  |  | 15 | 13 | 7 | 99.12
32360 | FURNACE ROAD CSO PONTYGWAITH RCT | AE2018416 |  | SE | Valleys | Afon Rhondda Fach - source to conf Rhondda R |  |  | 0 | 0 | 0 | 99.31
31194 | CWM BARRY SPS PORTHKERRY PARK | AE2019303 |  | SE | Central | Barry Brook |  | Cold Knap | 8.25 | 6 | 6 | 99.58 | BW | 5 in Bathing Season
31335 | NANT TALWG WAY PUMPING STATION | AE2019305 |  | SE | Central | Nant Talwg |  | Cold Knap | 0 | 0 | 0 | 99.07 | BW | 5 in Bathing Season
32417 | MOUNTIAN ASH - NR ELECTRICITY OXFOR | AE2020201 |  | SE | Valleys | R Cynon - conf Aman R to conf R Taff |  |  | 409.5 | 94 | 78 | 99.01
31066 | Rhydlafar WwTW | AE2021601 |  | SE | Central |  |  |  | 341.75 | 97 | 97 | 99.94
32565 | PENRHIWFER ASHDALE ROAD | AE2025203 |  | SE | Valleys | Ely R - source to conf Nant Mychydd |  |  | 3 | 3 | 2 | 99.53
70433 | TONYREFAIL POLICE STN REAR OF NO.7 | AE2025207 |  | SE | Valleys | Ely R - source to conf Nant Mychydd |  |  | 0 | 0 | 0 | 99.69
32536 | MERTHYR - CWM RHYD-Y-BEDD BALACLAVA | AE2025301 |  | SE | Valleys | Nant Morlais - source to conf R Taff |  |  | 0 | 0 | 0 | 99.89
32535 | THE BONT MERTHYR TYDFIL | AE2025302 |  | SE | Valleys | Nant Morlais - source to conf R Taff |  |  | 320.25 | 74 | 74 | 68.49 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
32538 | CSO GOITRE LANE MERTHYR TYDFIL | AE2025303 |  | SE | Valleys | Nant Morlais - source to conf R Taff |  |  | 9.5 | 15 | 15 | 99.27
32534 | DOWLAIS - JUNCTION NEW ROAD/BA | AE2025304 |  | SE | Valleys | Nant Morlais - source to conf R Taff |  |  | 0 | 0 | 0 | 99.89
32531 | A CSO AT WATERLOO HOUSE MERTHYR | AE2025305 |  | SE | Central | Nant Morlais - source to conf R Taff |  |  | 584.25 | 107 | 107 | 98.84
32530 | CSO TREVITHICK MONUMENT MERTHYR | AE2025307 |  | SE | Valleys | Nant Morlais - source to conf R Taff |  |  | 158.25 | 56 | 56 | 98.06
32294 | CSO PONT RHUN MERTHYR TYDFIL | AE2025310 |  | SE | Valleys | R Taff - conf Taf Fechan to conf R Cynon |  |  | 111.75 | 32 | 32 | 99.87
32302 | TRUNK SEWER 5 CSO | AE2025312 |  | SE | Valleys | R Taff - conf Taf Fechan to conf R Cynon |  |  | 94.5 | 16 | 16 | 89.39 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
71776 | A CSO AT REAR OF MEMORIAL HOSPITAL | AF3001301 |  | SE | Valleys | Rhymney R - source to conf Nant Bargod Rhymni |  |  | 128 | 36 | 31 | 99.2
71775 | CSO NEAR RHYMNEY STATION | AF3001302 |  | SE | Valleys | Rhymney R - source to conf Nant Bargod Rhymni |  |  | 220.5 | 54 | 54 | 98.64
71789 | CSO AT NEW TREDEGAR ADJ RHOSYN GWYN | AF3001304 |  | SE | Valleys | Rhymney R - source to conf Nant Bargod Rhymni |  |  | 304.25 | 33 | 33 | 100
32193 | RHYMNEY VALLEY TRUNK SEWER STO | AF3001309 |  | SE | Cardiff | Rhymney R - conf Nant Cylla to Chapel Wood |  |  | 0 | 0 | 0 | 99.35
30851 | COWBRIDGE STW COWBRIDGE VALE OF GLA | AF3010501 |  | SE | Central | Thaw - headwaters to confluence with Kenson |  |  | 505.25 | 45 | 44 | 41.42 |  |  |  | Communications issue, resolved in August 2021.
30861 | CYNON VALLEY STW GLYNCOCH PONTY | AF4001901 |  | SE | Central | R Taff - conf R Cynon to conf Rhondda R |  |  | 2197.25 | 128 | 128 | 99.99
70383 | PENRHIWCEIBER POINT D SSO | AF4004904 |  | SE | Valleys | R Cynon - conf Aman R to conf R Taff |  |  | 23.5 | 31 | 18 | 99.63
32525 | BEDLINOG- BOWLING GREEN | AF4024701 |  | SE | Central | Taff Bargoed |  |  | 425.75 | 68 | 63 | 98.85
30854 | CREIGIAU SEWAGE TREATMENT WORKS HOE | AF4024801 |  | SE | Central | Nant Dowlais - source to conf Ely R |  |  | 1231 | 77 | 77 | 99.65
70105 | FERNDALE BANANA TIP SSO OLD SCHOOL | AF4029003 |  | South East |  | Afon Rhondda Fach - source to conf Rhondda R |  |  | 361.75 | 47 | 47 | 99.93
32446 | CSO AT BOTTOM MONK STREET (Station St Aberdare) | AG0001204 |  | SE | Valleys | Afon Cynon - source to conf Aman R |  |  | 0 | 0 | 0 | 99.89
30843 | CILFYNYDD STW CILFYNYDD PONTYPRID | AG0004601 |  | SE | Central | R Taff - conf R Cynon to conf Rhondda R |  |  | 2125.25 | 125 | 125 | 100
30870 | DUFFRYN ISAF STW | AG0008301 |  | SE | Central | Ely R - source to conf Nant Mychydd |  |  | 1087 | 75 | 75 | 99.94
32649 | A SEWAGE PUMPING STATION FONMON PAR | AG0013901 |  | SE | Central | Kenson - conf with Waycock to conf with Thaw |  |  | 0 | 0 | 0 | 97.7
32579 | RHIWSAESON STW RHIWSAESON LLANTRIS | AG0019402 |  | SE | Central | Nant Clun - source to conf Ely R |  |  | 1698.5 | 203 | 125 | 99.91
32647 | SPS MILLFIELD DRIVE COWBRIDGE | AJ0028001 |  | SE | Central | Thaw - headwaters to confluence with Kenson |  |  | 3.5 | 1 | 1 | 99.94
31428 | TONTEG EMERGENCY STORM O/F | AN0008001 |  | SE | Valleys | R Taff - conf Rhondda R to Castle Street |  |  | 710.25 | 126 | 126 | 99.94
31781 | MISKIN SEWAGE PUMPING STATION MISKI | AN0010001 |  | SE | Central | Ely R - conf Nant Clun to Allot Gardens, Ely |  |  | 117.25 | 29 | 29 | 99.81
30808 | COSLECH STW | AN0010102 |  | SE | Central | Ely R - conf Nant Clun to Allot Gardens, Ely |  |  | 1172.5 | 130 | 130 | 99.94
32121 | GRIFFITHSTOWN SUBSIDIARY SEWER | AN0013901 |  | SE | Gwent | Afon Lwyd - source to conf Dowlais Bk |  |  | 684.25 | 98 | 98 | 94.56
72379 | OPPOSITE LODORE | AN0014801 |  | SE | Hereford | R Ithon - conf Camddwr Bk to conf R Wye |  |  | 226.25 | 57 | 57 | 97.19
32266 | CAERPHILLY-M/J PARK SWO | AN0016502 |  | SE | Cardiff | Nant y Aber - source to conf Rhymney R |  |  | 0.5 | 2 | 0 | 99.14
33093 | GROESFAEN PS | AN0019002 |  | SE | Cardiff | Nant Clun - source to conf Ely R |  |  | 222.25 | 44 | 44 | 99.93
32291 | TROEDYRHIW YEW STR SSO | AN0021101 |  | SE | Valleys | R Taff - conf Taf Fechan to conf R Cynon |  |  | 11.25 | 9 | 9 | 99.35
32945 | Barry Town SPS (long sea outfall) | AN0021801 |  | SE | Central | Barry Brook - headwaters to tidal limit |  |  | 2236 | 205 | 205 | 99.81
31161 | BRYNSADLER PUMPING STATION CLUN ELY | AN0022902 |  | SE | Central | Ely R - conf Nant Clun to Allot Gardens, Ely |  |  | 17 | 5 | 5 | 99.86
32306 | CARDIFF-CAEDELYN PARK SSO | AN0025701 |  | SE | Cardiff | Rhydwaedlyd Brook |  |  | 26.5 | 34 | 34 | 99.04
32539 | M'TYDFIL-TAI MAWR LANE SSO | AN0027701 |  | SE | Cardiff | R Taff - conf Taf Fechan to conf R Cynon |  |  | 147 | 34 | 34 | 99.19
71162 | SPS AT THE MARL PLAYING FIELDS GRAN | AN0028601 |  | SE | Central | R Taff - conf Rhondda R to Castle Stre |  |  | 0 | 0 | 0 | 99.93
70056 | PILL SOUTH B PUMPING STATION | AN0031501 |  | SE | South East | Pantyreos Bk - source to Barrack Hill |  |  | 244.5 | 75 | 75 | 99.93
70055 | PILL NORTH PS NORTH OCTOPUS RDBT | AN0031701 |  | SE | South East | Pantyreos Bk - source to Barrack Hill |  |  | 176.5 | 80 | 80 | 99.98
31345 | A SEWAGE PUMPING STATION PARK STREE | AN0033901 |  | SE | Central | R Taff - conf Rhondda R to Castle Stre |  |  | 1.25 | 3 | 3 | 99.94
71490 | COMBINED SEWER OVERFLOW | AN0034301 |  | South East |  | Usk |  |  | 0 | 0 | 0 | 99.57
31140 | BARRY DOCKS PS CSO OFF WIMBOURNE RD | AN0037801 |  | SE | Central | Barry No. 2 Dock |  | Jacksons | 213 | 183 | 183 | 99.93
72168 | TRELAI PARK STORM SEWAGE PS | AN0044501 |  | SE | Cardiff | Ely R - conf Nant Clun to Allot Garden |  |  | 77.5 | 41 | 41 | 99.91
33326 | YSTRADYRODWG/PONTYPRIDD TRUNK | AN0045101 |  | SE | Central | Unnamed trib - source to conf Rhymney R |  |  | 127.5 | 20 | 20 | 99.99
72095 | PENARTH LLANDOUGH MOORS CARDIFF | AN0047801 |  | SE | Central | Ely R - conf Nant Clun to Allot Gardens, Ely |  | Jacksons Bay Barry | 17 | 15 | 9 | 97.78
32099 | BLAINA SURGERY ROAD SSO | AN0055601 |  | SE | Valleys | Ebbw Fach R - source to conf Ebbw R |  |  | 198.5 | 51 | 51 | 86.81 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
32009 | CSO 33 REAR BRYNGWYN ROAD/HIGH ST | AN0056601 |  | SE | Gwent | Ebbw R - conf Ebbw Fach R to Maes-glas |  |  | 126 | 57 | 57 | 94.66
33094 | BARRY TOWN PS (EMER) ISLAND CAR PK | AN0060501 |  | SE | Central | Barry Harbour |  | Cold Knap | 10.5 | 19 | 19 | 99.56 | BW | 5 in Bathing Season
33449 | BARRY ISLAND PS | AN0060601 |  | SE | Central | Barry Old Harbour |  | Cold Knap | 0 | 0 | 0 | 99.34 | BW | 5 in Bathing Season
32945 | BARRY TOWN PS ISLAND CAR PARK BARRY (Short Sea Outfall) | AN0060701 |  | SE | Central | Severn Estuary |  | Cold Knap | 71.25 | 65 | 65 | 98.18 | BW | 5 in Bathing Season
32946 | KNAP PS BARRY VALE OF GLAMORGAN | AN0060901 |  | SE | Central | Bristol Channel |  | Cold Knap | 0.75 | 2 | 2 | 99.82 | BW | 5 in Bathing Season
33097 | KNAPP SEWAGE PUMPING STATION BARRY | AN0061001 |  | SE | Central | Bristol Channel |  | Cold Knap | - | - | - | 0 | BW | 5 in Bathing Season |  | Communications issue - access issue
32585 | PENYCOEDCAE SEWAGE PUMPING STATION | AN0066201 |  | SE | Cardiff | Rhondda R - source to conf Afon Rhondda Fach |  |  | 10.5 | 21 | 21 | 99.93
32024 | EBBW VALE VICTORIA RECLAMATION SCHE | AN0069601 |  | SE | Valleys | Ebbw R - source to conf Ebbw Fach R |  |  | 234.5 | 32 | 32 | 99.33
33722 | YNYSDDU PUMPING STATION PONTYCLUN | AN0071301 |  | SE | Central | Ely R - conf Nant Clun to Allot Gardens, Ely |  |  | 61.75 | 8 | 8 | 99.87
31178 | CARDIFF WESTERN DISTRICT PS | AN0072301 |  | SE | Central | Ely R - conf Nant Clun to Allot Garden |  |  | 114.75 | 8 | 8 | 94.2
31909 | NORTH ROAD CSO NORTH RD BUILTH WELL | AN0074701 |  | SE | Bridgend Hereford & Mid Wales | R Wye - conf R Irfon to Brewardine Br |  |  | 14 | 7 | 7 | 99
31908 | THE STRAND CSO CHURCH ST BUILTH WEL | AN0074801 |  | SW | Bridgend Hereford & Mid Wales | R Wye - conf R Irfon to Brewardine Br |  |  | 170.5 | 48 | 48 | 61.56 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
71355 | TALGARTH - ALONG THE GREEN | AN0075001 |  | SE | Bridgend Hereford & Mid | R Ennig - source to conf Afon Llynfi |  |  | 3.25 | 7 | 7 | 99.61
31952 | BRONLLYS BRIDGE - MANHOLE ADJA | AN0075101 |  | SE | Bridgend Hereford & Mid | Afon Llynfi - conf Dulas Bk to conf R Wye |  |  | 0 | 0 | 0 | 96.29
30949 | LLANFRYNACH - 100 YARDS DOWNST | AN0075201 |  | SE | South East |  |  |  | 204.75 | 25 | 24 | 99.91
32189 | TRECASTLE - IN FIELD WEST OF BRYNAW | AN0075301 |  | SE | Cardiff | R Usk - conf Afon Hydfer to conf Afon Crai |  |  | 30.75 | 4 | 4 | 99.32
32185 | TALYBONT - ACROSS BROOK FROM M | AN0075401 |  | SE | Bridgend Hereford & Mid | Caerfanell - source to conf R Usk |  |  | 7.75 | 5 | 2 | 99.35
71353 | WEUN CHAPEL PARK TOILETS RHAYADER | AN0075701 |  | SE | Bridgend Hereford & Mid Wales | R Wye - conf to conf Afon Marteg to co |  |  | 0 | 0 | 0 | 98.16
31907 | LLANELWEDD - SCOUT HUT STATION ROAD | AN0075901 |  | SE | Bridgend Hereford & Mid Wales | R Wye - conf R Irfon to Brewardine Br |  |  | 38.75 | 4 | 4 | 99.1
31906 | LLANELWEDD PRIMARY SCHOOL BRIDGE | AN0076001 |  | SE | Bridgend Hereford & Mid Wales | R Wye - conf R Irfon to Brewardine Br |  |  | 149.25 | 28 | 26 | 99.39
71336 | LLANDEWI - TOLL HOUSE | AN0076101 |  | SW | West | R Ithon - conf Camddwr Bk to conf R Wye |  |  | 730 | 64 | 63 | 72.87 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
31449 | LLANDRINDOD WELLS - ITHON ROAD | AN0076201 |  | SE | South East | R Ithon - conf Camddwr Bk to conf R Wye |  |  | 3.5 | 1 | 1 | 100
32312 | CSO AT PWLLGWAUN SHEPHERD STREET | AN0079801 |  | SE | Cardiff | Rhondda R - conf Afon Rhondda Fach to conf R Ta |  |  | 30.5 | 21 | 12 | 97.95
70398 | MILL ST CSO CAR PK ADJ PLAS CARMEL | AN0080101 |  | SE | Cardiff | Rhondda R - conf Afon Rhondda Fach to conf R Ta |  |  | 39 | 33 | 33 | 76.49 |  |  |  | Communications issue, resolved in April 2021.
32281 | PONTYPRIDD-WEST STR SSO | AN0080401 |  | SE | Valleys | R Taff - conf R Cynon to conf Rhondda R |  |  | - | - | - | 0 |  |  |  | Communications issue - access issue
31915 | MONMOUTH TOWN PUMPING STATION STORM SEWAGE OVERFLOW | AN0083602 |  | SE | South East | The River Monnow |  |  | 3.75 | 7 | 7 | 42.46 |  |  |  | Data unreliable from 01/01 to 30/07/2021. Due to static telemetry signal, resolved
72322 | CRICKHOWELL - BULLPIT MEADOW S | AN0085701 |  | SW | Bridgend Hereford & Mid | R Usk conf Afon Crawnon to |  |  | 3 | 7 | 7 | 80.78 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
31976 | LEGAR CSO FIELD OPP PARK FARM LODGE | AN0085901 |  | SE | Bridgend Hereford & Mid | R Usk conf Afon Crawnon to |  |  | 1071.75 | 111 | 111 | 99.8
32261 | A CSO HEATHWAY ROAD CSO O/S 87 HEAT | AN0086001 |  | SE | Cardiff | Unnamed trib - source to conf Rhymney R |  |  | 45.25 | 44 | 44 | 88.07 |  |  |  | Communications issue, resolved in August 2021.
31386 | BRIDGE ROAD SS ST MELLONS CARDIFF | AN0086101 |  | SE | South East | Rhymney R - conf Nant Cylla to Chapel Wood |  |  | 233.75 | 16 | 15 | 99.61
70093 | MILL MUSTON ROAD CSO ASSET 32549 | AN0086201 |  | SE | Cardiff | Ely R - conf Nant Clun to Allot Gardens, Ely |  |  | 12.25 | 31 | 31 | 92.49
32550 | PLYMOUTH WOOD ROAD CSO ELY CARDIFF | AN0086301 |  | SE | Central | Severn Estuary |  |  | 4.75 | 13 | 13 | 99.02
70447 | CSO HIGHWAY BY TY MAWR HSE CARDIFF | AN0086701 |  | SE | Cardiff | R Taff - conf Rhondda R to Castle Street |  |  | 12 | 26 | 26 | 99.35
32271 | HAVELOCK STREET/WOOD ST SSO | AN0087201 |  | SE | Cardiff | R Taff - conf Rhondda R to Castle Street |  |  | 5.75 | 12 | 12 | 99.39
30955 | LLANGURIG P.S. - OVERFLOW | AN0087501 |  | SE | South East | R Wye - conf Afon Bidno to conf Afon M |  |  | 371.5 | 57 | 52 | 99.83
31187 | LLANGYNIDR P.S. - OVERFLOW | AN0087601 |  | SE | South East | Nant Cleisfer - source to conf R Usk |  |  | 104.5 | 43 | 37 | 97.09
31223 | CRICKHOWELL - BRIDGE END CAR P | AN0087701 |  | South East |  | Usk conf Afon Crawnon to conf Gavenny R |  |  | 21 | 6 | 4 | 99.9
33057 | TROEDYRHIW PS | AN0087901 |  | SE | Central | River Taff |  |  | 18.75 | 5 | 4 | 97.83
31348 | PENTRE - VOLUNTEER STREET PUMP | AN0088001 |  | SE | Central | Rhondda R - source to conf Afon Rhondda Fach |  |  | 26 | 54 | 54 | 99.93
32582 | BRYNTEG PARK PUMPING STATION BEDDAU | AN0088401 |  | SE | Central | Nant Clun - source to conf Ely R |  |  | 9 | 6 | 4 | 99.62
31288 | LLANHARRY PS PONTYCLUN RCT | AN0088501 |  | SE | Central | Ely R - conf Nant Clun to Allot Gardens, Ely |  |  | 1.5 | 2 | 2 | 100
31435 | WESTWOOD RISE PUMPING STATION | AN0088701 |  | SE | Central | Nant Talwg |  | Cold Knap | 8.75 | 6 | 6 | 98.05 | BW | 5 in Bathing Season
31393 | CSO and EO at Penarth Stonylands Pumping Station | AN0089001 |  | SE | Cardiff | Cadoxton - headwaters to tidal limit |  |  | 301.5 | 39 | 37 | 99.28
72150 | ELY VALLEY ROAD CSO, | AN0089901 |  | SE | Valleys | Ely R - source to conf Nant Mychydd |  |  | 885.75 | 89 | 89 | 80.68 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
33304 | TONYREFAIL - MILL STREET | AN0090001 |  | SE | Valleys | Ely R - source to conf Nant Mychydd |  |  | 0 | 0 | 0 | 99.34
32564 | TONYREFAIL - WAUNRHYDD ROAD | AN0090101 |  | SE | Valleys | Ely R - source to conf Nant Mychydd |  |  | 102.25 | 26 | 25 | 99.05
32286 | GREENFIELD VICTORIA BRIDGE | AN0090601 |  | SE | Valleys | R Taff - conf Taf Fechan to conf R Cynon |  |  | 121 | 25 | 25 | 89.16 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
71679 | QUAKERS YARD - NEAR PUBLIC HOU | AN0090701 |  | SE | Valleys | R Taff - conf Taf Fechan to conf R Cynon |  |  | 0 | 0 | 0 | 99.62
32288 | 3RD TRUNK CSO SOUTH OF GLAN YR AFON | AN0090801 |  | SE | South East | R Taff - conf Taf Fechan to conf R Cynon |  |  | 2 | 6 | 6 | 99.89
32289 | TRUNK CSO 2A OFF ABERFAN ROAD | AN0090901 |  | SE | Cardiff | R Taff - conf Taf Fechan to conf R Cynon |  |  | 0 | 0 | 0 | 59.13 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
32296 | CSO WILLOW GAS WORKS MERTHYR TYDFIL | AN0091001 |  | SE | Valleys | R Taff - conf Taf Fechan to conf R Cynon |  |  | - | - | - | 0 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
32528 | MERTHYR TYDFIL - PENTREBACH DIXS FI | AN0091101 |  | SE | Valleys | R Taff - conf Taf Fechan to conf R Cynon |  |  | 288 | 73 | 73 | 97.98
32295 | TROEDYRHIW - SITE OF JOHN'S CH | AN0091301 |  | SE | Cardiff | R Taff - conf Taf Fechan to conf R Cynon |  |  | 24 | 31 | 31 | 94.97
32298 | CSO COLLEGE CAR PK MERTHYR TYDFIL | AN0091401 |  | SE | Valleys | R Taff - conf Taf Fechan to conf R Cynon |  |  | 207 | 43 | 43 | 98.34
32264 | LANSBURY PARK ESTATE | AN0092201 |  | SE | Gwent | Rhymney R - conf Nant Cylla to Chapel Wood |  |  | 1012.5 | 112 | 112 | 94.2
32225 | BEHIND WILLIAM STREET TIR Y BERTH | AN0092501 |  | SE | Gwent | Rhymney R - Nant Bargod Rhymni to conf Nant Cyl |  |  | 155 | 54 | 38 | 91.52
32218 | HENGOED - OLD PRINCE ALBERT VI | AN0092701 |  | SE | Gwent | Rhymney R - Nant Bargod Rhymni to conf Nant Cyl |  |  | 0.25 | 1 | 0 | 96.61
32217 | OLD PRINCE ALBERT HOTEL HENGOED | AN0092801 |  | SE | South East | Rhymney R - Nant Bargod Rhymni to conf Nant Cylla |  |  | 0 | 0 | 0 | 99.62
32209 | A CSO AT YSTRAD MYNACH BRIDGE | AN0093601 |  | SE | Cardiff | Rhymney R - conf Nant Cylla to Chapel Wood |  |  | 65.25 | 65 | 65 | 95.96
32207 | ASSET NO 32207 CELTIC STEEL FACTORY | AN0093801 |  | SE | Cardiff | Rhymney R - conf Nant Cylla to Chapel Wood |  |  | 1 | 4 | 0 | 96.93
32256 | TWYN CARNO - CARNO BUTE HOUSE | AN0093901 |  | SE | Valleys | Rhymney R - source to conf Nant Bargod Rhymni |  |  | 136.5 | 47 | 33 | 96.94
32252 | PONTLOTTYN - RECREATION GROUND | AN0094101 |  | SE | Cardiff | Rhymney R - source to conf Nant Bargod Rhymni |  |  | 97.5 | 36 | 23 | 99.27
32251 | PONTLOTTYN - TYNEWYDD FARM | AN0094201 |  | SE | Cardiff | Rhymney R - source to conf Nant Bargod Rhymni |  |  | 135.5 | 38 | 38 | 96.28
32237 | A CSO AT BIRTHDIR NEAR STATION | AN0095001 |  | SE | Valleys | Rhymney R - source to conf Nant Bargod Rhymni |  |  | 13.75 | 6 | 4 | 99.93
32267 | ABERBARGOED BRIDGE | AN0095101 |  | SE | Cardiff | Rhymney R - Nant Bargod Rhymni to conf Nant Cyl |  |  | 502.25 | 153 | 153 | 97.84
32197 | MACHEN UPPER - FORGE ROAD | AN0096001 |  | SE | Cardiff | Rhymney R - conf Nant Cylla to Chapel Wood |  |  | 2 | 7 | 1 | 99.27
32483 | PENDERYN - TANK IN FIELD RAKED SCRE | AN0096501 |  | SE | Cardiff | Aman R - source to conf Afon Cynon |  |  | 854.75 | 103 | 96 | 96.82
32484 | RHIGOS - OUTSIDE NO. 4C HEOL-Y-GRAIG | AN0096601 |  | SE | South East | Sychryd - headwaters to confluence with Mellte |  |  | 91.25 | 46 | 24 | 97.25
32476 | WEST BANK OF RIVER SOUTH OF A455 BR | AN0097101 |  | SE | Valleys | Afon Cynon - source to conf Aman R |  |  | 416.75 | 76 | 76 | 99.93
32473 | HIRWAUN - REAR OF GARDEN 66 TR | AN0098601 |  | SE | Valleys | Afon Cynon - source to conf Aman R |  |  | 178.5 | 60 | 43 | 99.13
32474 | HIRWAUN - REAR OF GARDEN 70 TR | AN0098701 |  | SE | Cardiff | Afon Cynon - source to conf Aman R |  |  | 0.25 | 1 | 1 | 99.5
32471 | REAR OF ST WINIFREDS CHURCH HIRWA | AN0098801 |  | SE | South East | Afon Cynon - source to conf Aman R |  |  | 0.25 | 1 | 0 | 99.89
32481 | HIRWAUN - REAR OF BUTE TERRACE | AN0099001 |  | SE | South East | Afon Cynon - source to conf Aman R |  |  | 85.75 | 25 | 14 | 99.52
32397 | TANK NEAR PIT CSO YNYSYBWL | AN0099301 |  | SE | Cardiff | Nant Clydach - source to conf R Taff |  |  | 676 | 110 | 110 | 97.67
32396 | FLUSHING STATIONS CSO YNYSYBWL | AN0099601 |  | SE | Cardiff | Nant Clydach - source to conf R Taff |  |  | 190.75 | 69 | 69 | 98.6
32500 | CWMAMAN - SOUTSIDE FFORCHAMAN | AN0100101 |  | SE | Cardiff | R Taff - conf R Cynon to conf Rhondda R |  |  | 0 | 0 | 0 | 99.89
32427 | ABERCWMBOI - OUTSIDE CAPCOCH I PARK | AN0100301 |  | SE | Cardiff | Aman R - source to conf Afon Cynon |  |  | 1.75 | 4 | 4 | 99.61
32425 | ABERCWMBOI - REAR OF 69/70 BRO | AN0100501 |  | SE | Valleys | R Cynon - conf Aman R to conf R Taff |  |  | - | - | - | 0 |  |  |  | Data unreliable from 01/01 to 31/12/2021. Due to erratic telemetry signal. Instrumentation task escalated through business as usual for instrumentation defect.
32437 | OPPOSITE SCALES HOUSE,CWMBACH | AN0100701 |  | SE | Valleys | Afon Cynon - source to conf Aman R |  |  | 284.5 | 85 | 65 | 97.72
32436 | REAR OF 13 BRONHAUL CWMBACH | AN0100801 |  | SE | Valleys | R Cynon - conf Aman R to conf R Taff |  |  | 19.25 | 12 | 6 | 99.43
32431 | CWMBACH - OUTSIDE 45 BRYNGOLWG | AN0100901 |  | SE | Valleys | R Cynon - conf Aman R to conf R Taff |  |  | 0 | 0 | 0 | 62.37 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
32435 | CSO OPPOSITE NO 1 CROWN ROW CWMBACH | AN0101001 |  | SE | Valleys | R Cynon - conf Aman R to conf R Taff |  |  | 7 | 10 | 10 | 99.36
32434 | CWMBACH - NEAR 44 BRO DEG | AN0101101 |  | SE | Valleys | R Cynon - conf Aman R to conf R Taff |  |  | 138.5 | 45 | 37 | 99.11
32439 | CWMBACH - OUTSIDE BRO DEG | AN0101201 |  | SE | Valleys | R Cynon - conf Aman R to conf R Taff |  |  | 380.75 | 70 | 55 | 98.18
32595 | BARRY - ST HILLARY RISE (REAR | AN0102801 |  | SE | Central | Unnamed Stream |  | Jacksons Bay Barry | 0.25 | 1 | 0 | 99.62
71828 | WHITEWELL ROAD CSO 1 BARRY | AN0104601 |  | SE | Central | Cadoxton - headwaters to tidal limit |  | Jacksons Bay Barry | 1.25 | 5 | 0 | 95.33 | BW | 5 in Bathing Season
71829 | WHITEWELL ROAD CSO 2 BARRY | AN0104701 |  | SE | Central | Coldbrook |  | Jacksons Bay Barry | 154.75 | 27 | 17 | 95.35 | BW | 5 in Bathing Season
71857 | MERTHYR DYFAN ROAD CSO BARRY | AN0104801 |  | SE | Central | Coldbrook |  | Jacksons Bay Barry | - | - | - | 0 | BW | 5 in Bathing Season |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
71825 | DANIEL STREET CSO DANIEL STREET | AN0105001 |  | SE | Central | Coldbrook |  | Jacksons Bay Barry | 12 | 7 | 7 | 99.67 | BW | 5 in Bathing Season
72096 | FOOTPATH R/O WESTBURY CLOSE BARRY | AN0105101 |  | SE | Central | Coldbrook |  | Jacksons Bay Barry | 17.25 | 22 | 22 | 99.83 | BW | 5 in Bathing Season | YES
72125 | PRICE AVENUE CSO BARRY | AN0105301 |  | SE | Central | Coldbrook |  | Jacksons Bay Barry | 1.75 | 7 | 7 | 99.75 | BW | 5 in Bathing Season
32627 | COLDBROOK ROAD EAST 1 BARRY | AN0105401 |  | SE | Central | Coldbrook |  | Jacksons Bay Barry | 0 | 0 | 0 | 70.54 | BW | 5 in Bathing Season |  | Communications issue, resolved in August 2021.
32624 | BARRY - COLDBROOK ROAD EAST | AN0105501 |  | SE | Central | Cadoxton - headwaters to tidal limit |  |  | 28.75 | 25 | 25 | 98.69
32137 | PONTNEWYNYDD - MILL ROAD | AN0106101 |  | SE | Gwent | Afon Lwyd - source to conf Dowlais Bk |  |  | 703 | 103 | 103 | 98.79
72598 | CSO AT REAR OF SCHOOL ST TON PENTRE | AN0106901 |  | SE | Valleys | Rhondda R - source to conf Afon Rhondda Fach |  |  | 0.75 | 3 | 0 | 99.33
33273 | WENVOE SEWAGE PUMPING STATION | AN0107701 |  | South East |  | Cadoxton - headwaters to tidal limit |  |  | 249.25 | 20 | 20 | 91.9
71557 | RHOOSE STATION R'D CSO RHOOSE BARRY | AN0107801 |  | SE | Central | The Rhoose Brook |  | Cold Knap Barry | 0 | 0 | 0 | 99.75
32430 | CWMBACH - SIDE OF POLICE HOUSE | AN0107901 |  | SE | Valleys | R Cynon - conf Aman R to conf R Taff |  |  | 32.25 | 15 | 12 | 99.44
32432 | CWMBACH - NEAR 29 MAESHYFRYD | AN0108001 |  | SE | Cardiff | R Cynon - conf Aman R to conf R Taff |  |  | 1.25 | 4 | 4 | 99.62
70376 | CWMBACH - DUFFRYN HOTEL CAR PA | AN0108301 |  | SE | Cardiff | Aman R - source to conf Afon Cynon |  |  | 43.5 | 8 | 8 | 40.45 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
33509 | CEFNPENNAR- ADJACENT LOW ROW S | AN0108401 |  | SE | Cardiff | R Cynon - conf Aman R to conf R Taff |  |  | 33.25 | 7 | 7 | 83.11 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
32421 | MOUNTAIN ASH - OUTSIDE 10 HAMI | AN0108501 |  | SE | Valleys | R Cynon - conf Aman R to conf R Taff |  |  | 0 | 0 | 0 | 62.09 |  |  |  | Communications issue, resolved in May 2021.
32423 | MOUNTAIN ASH - CWMPENNAR ABOVE CENO | AN0108701 |  | SE | Cardiff | R Cynon - conf Aman R to conf R Taff |  |  | 102.75 | 29 | 29 | 99.72
32415 | NEAR COMMUNITY HALL NEWTOWN | AN0108801 |  | SE | Valleys | R Cynon - conf Aman R to conf R Taff |  |  | 75.25 | 24 | 24 | 99.13
33510 | MISKIN - OPPOSITE MISKIN HOTEL | AN0108901 |  | SE | Valleys | R Cynon - conf Aman R to conf R Taff |  |  | 379.5 | 82 | 82 | 98.89
32410 | GLASBROOK PENRHIWCEIBER | AN0109201 |  | SE | Valleys | R Cynon - conf Aman R to conf R Taff |  |  | 201.25 | 53 | 53 | 99.32
32411 | PENRHIWCEIBER STATION | AN0109301 |  | SE | Cardiff | R Cynon - conf Aman R to conf R Taff |  |  | 420.25 | 55 | 55 | 98.6
32407 | CSO PONTCYNON PIPE BRIDGE ABERCYNON | AN0109601 |  | SE | Valleys | R Cynon - conf Aman R to conf R Taff |  |  | 966.5 | 89 | 89 | 98.71
31419 | REGENT ST CSO TREORCHY RHONDDA | AN0110901 |  | SE | Central | Rhondda R - source to conf Afon Rhondda Fach |  |  | 1803 | 154 | 154 | 99.95
32420 | TOWNHALL, OLD CARDIFF ROAD, MOUNTAIN ASH | AN0111201 |  | SE | Valleys | R Cynon - conf Aman R to conf R Taff |  |  | - | - | - | 0 |  |  |  | Data unreliable from 01/01/2021 to 31/12/2021. Due to static telemetry signal. Instrumentation task escalated through business as usual for instrumentation defect.
32400 | BUTCHERS FIELD CSO CLYDACH PK YNYSY | AN0111601 |  | SE | Valleys | Nant Clydach - source to conf R Taff |  |  | 162.5 | 30 | 27 | 87.58 |  |  |  | Communications issue, resolved in August 2021.
32506 | ABERAMAN - JUNCTION DAVID STRE | AN0111801 |  | SE | Valleys | Afon Cynon - source to conf Aman R |  |  | 58.75 | 7 | 7 | 99.33
32507 | ABERAMAN - OUTSIDE 20 GLANCYNO | AN0111901 |  | SE | Valleys | Afon Cynon - source to conf Aman R |  |  | 1.75 | 2 | 1 | 99.02
32490 | ABERAMAN - OUTSIDE POLICE STAT | AN0112101 |  | SE | Cardiff | Aman R - source to conf Afon Cynon |  |  | 4.75 | 12 | 2 | 99.5
32442 | ABERAMAN - BOTTOM OF WIND STRE NR L | AN0112301 |  | SE | Valleys | Afon Cynon - source to conf Aman R |  |  | 31.5 | 29 | 14 | 94.47
32510 | ABERAMAN - LAND SOUTH EAST OF | AN0112501 |  | SE | Cardiff | Aman R - source to conf Afon Cynon |  |  | 43.25 | 25 | 16 | 89.04 |  |  |  | Communications issue, resolved in March 2021.
32468 | PENYWAUN - REAR OF 37/39 ERW L | AN0112701 |  | SE | Cardiff | Aman R - source to conf Afon Cynon |  |  | 22.5 | 37 | 19 | 99.33
32464 | ABERDARE FORECOURT CSO LLWYDC | AN0112901 |  | SE | Valleys | Afon Cynon - source to conf Aman R |  |  | 357.5 | 64 | 64 | 99.92
32519 | A CSO AT FIELD ADJACENT TO DAVID ST | AN0113301 |  | SE | Valleys | Afon Cynon - source to conf Aman R |  |  | - | - | - | 0 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
32458 | OPPOSITE ARTHURS PLACE TRECYNON | AN0113801 |  | SE | Cardiff | Aman R - source to conf Afon Cynon |  |  | 738.5 | 104 | 96 | 99.93
31294 | CHURCH LANE STW CHURCH ROAD | AN0114101 |  | South East |  | Wye - Scithwen Bk to Brewardine Br |  |  | 252.25 | 57 | 57 | 99.88
71838 | A CSO AT ELIZABETH ST ABERDARE | AN0116701 |  | SE | Central | Afon Cynon - source to conf Aman R |  |  | 83.25 | 46 | 46 | 99.19
32386 | CSO REAR OF CHUBB FACTORY HIGHFIELD | AN0117401 |  | SE | Valleys | Afon Rhondda Fach - source to conf Rhondda R |  |  | 195 | 47 | 47 | 88.76 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
32387 | CSO AT REAR OF BLAKE STREET MAERDY | AN0117501 |  | SE | Cardiff | Afon Rhondda Fach - source to conf Rhondda R |  |  | 297 | 64 | 64 | 95.89
32362 | JUNCT OF BRONDEG AND PENRHYS ST CSO | AN0117701 |  | SE | Cardiff | Afon Rhondda Fach - source to conf Rhondda R |  |  | 1.75 | 3 | 1 | 99.62
32381 | PENYCRAIG - TYLACELYN ROAD | AN0117901 |  | SE | South East | Rhondda R - source to conf Afon Rhondda Fach |  |  | 24.25 | 27 | 13 | 86.48 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
71313 | A CSO JUNCT DUNRAVEN ST & TYLACELYN | AN0118001 |  | SE | Valleys | Rhondda R - source to conf Afon Rhondda Fach |  |  | 225.25 | 81 | 81 | 99.19
32382 | PENYGRAIG - JUNCTION NANTGWYN | AN0118301 |  | SE | Cardiff | Rhondda R - source to conf Afon Rhondda Fach |  |  | 5.75 | 19 | 19 | 99.16
32309 | GLANNANT ST/DINAS ROAD CSO | AN0118401 |  | SE | Valleys | Rhondda R - source to conf Afon Rhondda Fach |  |  | 273.75 | 71 | 56 | 98.76
32389 | PENYGRAIG - PENYGRAIG ROAD | AN0118501 |  | SE | Cardiff | Rhondda R - source to conf Afon Rhondda Fach |  |  | 136.5 | 49 | 49 | 99.01
32320 | CYMMER ROAD CSO DINAS PORTH | AN0118601 |  | SE | Cardiff | Rhondda R - source to conf Afon Rhondda Fach |  |  | 0.75 | 3 | 3 | 91.96
32315 | CSO AT CADWGAN TERRACE TREHAFOD | AN0118801 |  | SE | Valleys | Rhondda R - conf Afon Rhondda Fach to conf R Ta |  |  | 0 | 0 | 0 | 99.73
32365 | EAST ROAD CSO TYLORSTOWN RHONDDA | AN0119001 |  | SE | Valleys | Afon Rhondda Fach - source to conf Rhondda R |  |  | 0.5 | 2 | 0 | 99.59
32374 | CSO @ JUNCT COMMERCIAL & GEORGE ST | AN0119601 |  | SE | Valleys | Afon Rhondda Fach - source to conf Rhondda R |  |  | 106.25 | 27 | 18 | 99.06
32375 | STATION RD CSO FERNDALE RCT | AN0119701 |  | SE | Valleys | Afon Rhondda Fach - source to conf Rhondda R |  |  | 739.75 | 99 | 83 | 83.77 |  |  |  | Communications issue from 03/12 to 12/12/21 and from 23/12/ to 31/12/2021, resolved.
32379 | BLAENLLECHAU TAFF ST CSO | AN0119901 |  | SE | South East | Afon Rhondda Fach - source to conf Rhondda R |  |  | 288 | 58 | 42 | 98.18
32380 | SCHOOL STREET CSO FERNDALE RCT | AN0122101 |  | SE | Valleys | Afon Rhondda Fach - source to conf Rhondda R |  |  | 112.25 | 52 | 41 | 98.86
32337 | JUNCT YSTRAD/CHURCH ROAD YSTRAD | AN0122201 |  | SE | Gwent | Rhondda R - source to conf Afon Rhondda Fach |  |  | 307 | 124 | 100 | 77.42 |  |  |  | Data unreliable from 01/08 to 27/09/2021. Due to erratic telemetry signal, issue resolved.
32332 | CSO HIGHWAY ADJ 18 RIVER ST YSTRAD | AN0122501 |  | SE | Valleys | Rhondda R - source to conf Afon Rhondda Fach |  |  | 11.25 | 41 | 4 | 99.34
32328 | CSO OFF YNYSCYNON ROAD TREALAW | AN0122601 |  | SE | Cardiff | Rhondda R - source to conf Afon Rhondda Fach |  |  | 14 | 9 | 9 | 99.73
32390 | CSO AT LLWYNYPIA RD TONYPANDY | AN0122701 |  | SE | Cardiff | Rhondda R - source to conf Afon Rhondda Fach |  |  | 123.5 | 66 | 48 | 98.87
32391 | A CSO AT TONYPANDY | AN0123001 |  | SE | Cardiff | Rhondda R - source to conf Afon Rhondda Fach |  |  | 19.25 | 9 | 7 | 99.77
31417 | TREHERBERT PUMPING STATION PARK CL | AN0123601 |  | SE | Central | Rhondda R - source to conf Afon Rhondda Fach |  |  | 0 | 0 | 0 | 99.94
32353 | TREHERBERT - REAR OF GEORGE ST | AN0123901 |  | SE | Cardiff | Rhondda R - source to conf Afon Rhondda Fach |  |  | 217.25 | 44 | 41 | 99.17
32352 | TREHERBERT - OPPOSITE RAILWAY | AN0124001 |  | SE | Cardiff | Rhondda R - source to conf Afon Rhondda Fach |  |  | 0 | 0 | 0 | 100
32394 | CSO JUNCTION OF PARK CRESCENT AND S | AN0124201 |  | SE | Cardiff | Rhondda R - source to conf Afon Rhondda Fach |  |  | 0 | 0 | 0 | 12.88 |  |  |  | Communications issue - access issue
32395 | CWMPARC - RAILWAY TERRACE | AN0124301 |  | SE | Valleys | Rhondda R - source to conf Afon Rhondda Fach |  |  | 27 | 22 | 12 | 99.47
32338 | PENTRE - LLEWELLYN STREET | AN0124701 |  | SE | South East | Rhondda R - source to conf Afon Rhondda Fach |  |  | 0 | 0 | 0 | 99.81
33104 | TRELYN PARK . . | AN0153501 |  | SE | Cardiff | Rhymney R - Nant Bargod Rhymni to conf Nant Cyl |  |  | 0.25 | 1 | 0 | 95.74
33106 | OAKS END CLOSE PENPEDAIRHEOL , | AN0153701 |  | SE | Central | Nant Cylla - source to conf Rhymney R |  |  | 179.75 | 59 | 59 | 99.28
33109 | ISLWYN RD WATTSVILLE , | AN0154001 |  | SE | Gwent | Sirhowy R - Rock Villas to conf Afon Ebwy |  |  | 1.75 | 6 | 1 | 99.64
33113 | PANTY PWDIN . . | AN0154401 |  | SE | Cardiff | Berthin Bk - source to conf R Usk |  |  | 86.5 | 18 | 18 | 97.91
33115 | RAILWAY COTTAGE . . | AN0154601 |  | SE | South East | Olway Bk - conf Pill Bk to conf R Usk |  |  | 0 | 0 | 0 | 99.61
33117 | CSO 42 92 TREDEGAR ST CROSS KEYS | AN0154801 |  | SE | Cardiff | Sirhowy R - Rock Villas to conf Afon Ebwy |  |  | 144.25 | 16 | 16 | 99.93
33118 | CSO 41 OUTSIDE 21 GLADSTONE STREET | AN0154901 |  | SE | Gwent | Ebbw R - conf Ebbw Fach R to Maes-glas |  |  | 1.5 | 6 | 0 | 99.61
72328 | R.O.COBDEN STREET . . | AN0155201 |  | SE | Gwent | Ebbw R - conf Ebbw Fach R to Maes-glas |  |  | 0 | 0 | 0 | 99.62
72386 | BRROKLAND TERRACE REC GROUND CSO | AN0155301 |  | SE | Gwent | Afon Lwyd - source to conf Dowlais Bk |  |  | 274.5 | 53 | 53 | 99.93
33123 | ROSE COTTAGE LLANFRECHFA , | AN0155401 |  | SE | Gwent | Afon Lwyd - source to conf Dowlais Bk |  |  | - | - | - | 0 |  |  |  | Communications issue - access issue
33124 | WARREN SLADE SEWAGE PUMPING STATION | AN0155501 |  | SE | Cardiff | Sturch Pill - source to conf R Severn Estuary |  |  | 10 | 21 | 21 | 96.18
33125 | WELSH STREET CHEPSTOW , | AN0155601 |  | SE | Valleys | Sturch Pill - source to conf R Severn Estuary |  |  | 148.75 | 77 | 77 | 99.93
33129 | WARREN SLADE SEWAGE PUMPING STATION | AN0156001 |  | SE | Valleys | Sturch Pill - source to conf R Severn Estuary |  |  | 4.75 | 8 | 8 | 39.28 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
33131 | MAPLE CLOSE UNDERWOOD NEWPORT | AN0156201 |  | SE | Gwent | Monks Ditch - source to Wainbridge |  |  | 5 | 6 | 4 | 95.68
72130 | PARK PLACE CSO | AN0156701 |  | SE | Cardiff | R Taff - conf Rhondda R to Castle Street |  |  | 1.25 | 2 | 2 | 99.97
33137 | PWLLGWAUN ROAD CSO | AN0156801 |  | SE | Cardiff | Rhondda R - conf Afon Rhondda Fach to conf R Ta |  |  | 7 | 12 | 4 | 95.67
33141 | A CSO AT LANELAY CRESCENT MAESYCOED | AN0157201 |  | SE | Cardiff | Rhondda R - conf Afon Rhondda Fach to conf R Ta |  |  | 4.5 | 10 | 10 | 98.9
33143 | LLANTWIT ROAD (A) TREFOREST , | AN0157401 |  | SE | Cardiff | R Taff - conf Rhondda R to Castle Street |  |  | 2.5 | 7 | 7 | 99.61
33147 | A COMBINED SEWER OVERFLOW TREBERTH | AN0157801 |  | SE | Gwent | Monks Ditch - source to Wainbridge |  |  | 0 | 0 | 0 | 88.11 |  |  |  | Communications issue - access issue
71604 | REAR OF 11 ROBERTSONS WAY CSO, MALP | AN0158001 |  | SE | Gwent | Pantyreos Bk - source to Barrack Hill |  |  | 4 | 13 | 2 | 57.15 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
33150 | CSO 48 TREGWILYM CLOSE ROGERSTONE | AN0158101 |  | SE | Gwent | Ebbw R - conf Ebbw Fach R to Maes-glas |  |  | 39 | 47 | 47 | 84.15 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
33151 | BRYNGLAS ROAD NEWPORT NEWPORT CBC | AN0158201 |  | SE | Cardiff | Pantyreos Bk - source to Barrack Hill |  |  | 5.25 | 18 | 18 | 99.51
71487 | MALPAS ROAD CSO | AN0158401 |  | SE | Valleys | Pantyreos Bk - source to Barrack Hill |  |  | 1479.75 | 153 | 153 | 99.94
73324 | ROMAN REACH CAERLEON NEWPORT | AN0158501 |  | SE | Gwent | Afon Lwyd - conf Dowlais Bk to Pont Sadwrn |  |  | 2 | 7 | 1 | 99.39
33156 | ST CADOCS HOSPITAL NEWPORT | AN0158701 |  | SE | Gwent | Afon Lwyd - conf Dowlais Bk to Pont Sadwrn |  |  | 138.75 | 72 | 54 | 98.87
33168 | LISWERRY RD/ABERTHAW RD NEWPORT , | AN0159901 |  | SE | Cardiff | Pantyreos Bk - source to Barrack Hill |  |  | 4.75 | 14 | 14 | 79.85 |  |  |  | Communications issue, resolved in April 2021.
33169 | CHEPSTOW RD NEAR NO. 589 NEWPORT , | AN0160001 |  | SE | Cardiff | Pantyreos Bk - source to Barrack Hill |  |  | 0 | 0 | 0 | 89.03 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
33170 | CHEPSTOW ROAD CSO | AN0160101 |  | SE | Valleys | Llwynau Bk - source to conf R Usk |  |  | 8.75 | 23 | 23 | 99.93
32224 | WILLIAM STREET FLEUR-DE-LYS , | AN0160601 |  | SE | Cardiff | Rhymney R - Nant Bargod Rhymni to conf Nant Cyl |  |  | 0.25 | 1 | 0 | 99.62
33176 | HA'PENNYS SITE . . | AN0161301 |  | SE | Gwent | R Clydach - source to conf R Usk |  |  | 32.75 | 37 | 20 | 99.25
33178 | HOSPITAL ROAD | AN0161501 |  | SE | Gwent | Afon Lwyd - source to conf Dowlais Bk |  |  | 0.5 | 2 | 0 | 99.57
71793 | CWMAVON CSO NEAR ROSE COTTAGE | AN0161801 |  | SE | Gwent | Afon Lwyd - source to conf Dowlais Bk |  |  | 7.5 | 12 | 3 | 93.9
33182 | ABERNANT RUGBY CLUB CSO | AN0161901 |  | SE | Gwent | Afon Cynon - source to conf Aman R |  |  | 74 | 26 | 26 | 98.52
33183 | MIKES FIELD CSO ABERAMAN | AN0162001 |  | SE | Valleys | Aman R - source to conf Afon Cynon |  |  | 1191 | 105 | 105 | 97.82
32265 | STORM SEWAGE OVERFLOW AT CROSSWAYS RETAIL/BUSINESS PARK CAERPHILLY | AN0164002 |  | SE | South East | Nant y Aber - source to conf Rhymney R |  |  | 58.5 | 21 | 21 | 99.22
72737 | CEFN GORWYDD | AN0180001 |  | SE | South East | R Irfon - conf Cledan to conf Tirabad Dulas |  |  | 109 | 26 | 20 | 99.97
33734 | HARROWBY ST SSO BUTETOWN CARDIFF | AN0185101 |  | SE | Central | R Taff - conf Rhondda R to Castle Stre |  |  | 974.25 | 120 | 120 | 99.93
33555 | PENYGAWSI - SSO | AN0187601 |  | SE | Cardiff | Nant Clun - source to conf Ely R |  |  | 108.5 | 46 | 46 | 99.99
33556 | LANELAY PARK - SSO | AN0187701 |  | SE | Valleys | Ely R - conf Nant Mychydd to conf Nant Clun |  |  | 304.75 | 93 | 93 | 100
33558 | STATION ROAD MAERDY RHONDDA | AN0220301 |  | SE | Cardiff | Afon Rhondda Fach - source to conf Rhondda R |  |  | 114 | 15 | 15 | 12.18 |  |  |  | Communications issue, resolved in November 2021.
33583 | SULLY MOORS P S PENARTH | AN0223001 |  | SE | Central | Cadoxton - headwaters to tidal limit |  |  | 0 | 0 | 0 | 99.94 | BW | 5 in Bathing Season
32228 | PENGAM-REAR OF GLANYRAFON HOUS COMM | AN0223501 |  | SE | Cardiff | Rhymney R - Nant Bargod Rhymni to conf Nant Cyl |  |  | 259.75 | 82 | 67 | 99.22
33909 | PONTYPOOL - ADJACENT SNATCHWOO | AN0224101 |  | SE | Gwent | Afon Lwyd - source to conf Dowlais Bk |  |  | 6 | 11 | 11 | 99.53
32638 | WENVOE CSO STATION ROAD EAST BARRY | AN0224301 |  | SE | Central | Wrinstone Brook |  | Jacksons Bay Barry | 6.5 | 5 | 5 | 97.27 | BW | 5 in Bathing Season
31438 | WHITEBRIDGE PS PETERSTON SUPER ELY | AN0225001 |  | SE | Central | Ely R - conf Nant Clun to Allot Gardens, Ely |  |  | 57 | 18 | 16 | 99.88
30857 | CROSSGATES WTW CROSSGATES POWYS | AN0226801 |  | SE | South East | R Ithon - conf Camddwr Bk to conf R Wye |  |  | 159.75 | 33 | 33 | 99.38
31960 | RIDGEBOURNE CATCHMENT AREA LLANDRI | AN0228401 |  | SW | Hereford | R Ithon - conf Camddwr Bk to conf R Wye |  |  | 79.5 | 37 | 37 | 99.68
33496 | A SEWAGE PS TREDOGAN ASSET NO33586 | AN0228601 |  | SE | Central | Waycock - headwaters to confluence with Kenson |  |  | 0.25 | 1 | 0 | 99.91
33499 | FONTYGARY SPS AND LOWER FONTYGARY S | AN0228701 |  | SE | Central | Bristol Channel Inner North |  | Cold Knap Barry | 92.5 | 14 | 13 | 99.99 | BW | 5 in Bathing Season
33519 | A SEWAGE PUMPING STATION RHOOSE SPS | AN0228801 |  | SE | Central | Bristol Channel |  | Cold Knap Barry | 73.5 | 18 | 13 | 98.81
33498 | A SEWAGE PS PORTHKERRY SPS ASSET NO | AN0228901 |  | SE | Central | The Whitelands Brook |  | Cold Knap | 161 | 16 | 15 | 97.12
70429 | SSO ADJACENT TO PARISH ROAD BEDDA | AN0229801 |  | SE | Cardiff | Nant Clun - source to conf Ely R |  |  | 794 | 139 | 139 | 98.09
33649 | BREWERS ARMS SSO DOWLAIS MERTHYR T | AN0230601 |  | SE | Valleys | Nant Morlais - source to conf R Taff |  |  | 2.25 | 6 | 6 | 99.41
33522 | CSO BARGOED , , | AN0231701 |  | SE | Valleys | Rhymney R - Nant Bargod Rhymni to conf Nant Cyl |  |  | 112.25 | 45 | 45 | 75.07 |  |  |  | Communications issue, resolved in August 2021.
30844 | CILMERY STW | AN0232101 |  | SE | South East | Afon Chwefru - source to conf R Irfon |  |  | 1314.75 | 153 | 132 | 99.97
31410 | CAPEL FARM PS EMERGENCY TONYREFAI | AN0234001 |  | SE | Central | Nant Mychydd - source to conf Ely R |  |  | 258 | 29 | 28 | 81.54 |  |  |  | Communications issue, resolved in September 2021.
72422 | PS NEAR GLYNDWR ROAD PENARTH CARDI | AN0235401 |  | SE | Central | Cadoxton - headwaters to tidal limit |  |  | 32 | 59 | 59 | 99.94
32054 | CWM GELLI SSO CWMGELLI BLACKWOOD , | AN0237201 |  | SE | Cardiff | Sirhowy R - Rock Villas to conf Afon Ebwy |  |  | 33.25 | 22 | 14 | 42.61 |  |  |  | Communications issue - access issue
73355 | CWMBACH SPS CANAL RD CWMBACH | AN0237701 |  | SE | Central |  |  |  | 13.75 | 2 | 2 | 99.75
33746 | SION STREET SEWAGE PUMPING STATION | AN0238301 |  | SE | Central | R Taff - conf R Cynon to conf Rhondda R |  |  | 0 | 0 | 0 | 99.97
31143 | BETTWS LANE SPS NEWPORT , | AN0239701 |  | SE | South East | Pantyreos Bk - source to Barrack Hill |  |  | 39.25 | 10 | 10 | 98.53
71166 | LOWER MILL STREET CSO PONTYPRIDD | AN0241501 |  | SE | Valleys | Rhondda R - conf Afon Rhondda Fach to conf R Ta |  |  | 28.75 | 8 | 8 | 99.94
31363 | RHYDYNANT PS (ADJ TO 49) PONTYCLUN | AN0242701 |  | SE | Central | Ely R - conf Nant Clun to Allot Gardens, Ely |  |  | 0 | 0 | 0 | 99.94
31306 | MAES YR FELIN PUMPING STATION | AN0242801 |  | SE | Central | Ely R - conf Nant Clun to Allot Gardens, Ely |  |  | 0 | 0 | 0 | 99.86
73029 | PENARTH HEAD SEWAGE PUMPING STATION | AN0242901 |  | SE | Central | SEVERN LOWER |  | Jacksons Bay Barry | 31.5 | 21 | 21 | 99.91
33771 | KYMIN PS PENARTH CARDIFF (27) | AN0243001 |  | SE | Central | SEVERN LOWER |  | Jacksons Bay Barry | 165.5 | 75 | 75 | 99.99 | BW | 16 in Bathing Season | YES
32541 | COGAN PS PENARTH CARDIFF , | AN0243101 |  | SE | Central | Ely R - conf Nant Clun to Allot Garden |  |  | 2.75 | 7 | 7 | 99.9
33763 | MARINA PUMPING STATION, PENARTH, S.GLAMORGAN | AN0243201 |  | SE | Central | Severn Estuary |  | Jacksons Bay Barry | 40.5 | 33 | 33 | 97.19
33764 | ATLANTIC TRADING EST PS BARRY , | AN0243401 |  | SE | Central | River Cadoxton |  | Jacksons | 0 | 0 | 0 | 86.97 | BW | 5 in Bathing Season |  | Data unreliable from 01/01 to 06/02/2021. Due to static telemetry signal, resolved.
72372 | BROCKHILL RISE & LAVERNOCK RD SSO'S (51) | AN0243501 |  | SE | Central | Bristol Channel |  | Jacksons Bay Barry | 194.5 | 67 | 67 | 99.92 | BW | 31 in Bathing Season | YES
32563 | REAR OF 76 MILL STREET TONYREFAIL | AN0245101 |  | SE | Valleys | Ely R - source to conf Nant Mychydd |  |  | 128 | 38 | 31 | 99.2
31078 | SENNYBRIDGE STW (STORM) , , | AN0246901 |  | SE | South East | R Usk - conf Afon Senni to conf Afon Crawnon |  |  | 1150.25 | 123 | 118 | 80.09 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
71170 | CURRAN PS DUMBALLS RD IND EST | AN0249801 |  | SE | Central | R Taff - conf Rhondda R to Castle Stre |  |  | 0.5 | 1 | 1 | 99.95
33387 | MERTHYR (LINES BRIDGE) CSO , , | AN0250201 |  | SE | Cardiff | R Taff - conf Taf Fechan to conf R Cynon |  |  | 113.75 | 37 | 23 | 99.31
32105 | ABERTILLERY (GLAN EBBW TER) , , | AN0250301 |  | SE | Valleys | Ebbw Fach R - source to conf Ebbw R |  |  | 91.25 | 50 | 33 | 92.17
33532 | ABERTILLERY (9 TILLERY ST) CSO , | AN0250401 |  | SE | Valleys | Ebbw Fach R - source to conf Ebbw R |  |  | 0 | 0 | 0 | 99.83
33190 | CSO OLD GLOBE PUBLIC HOUSE | AN0250501 |  | SE | Gwent | Ebbw R - conf Ebbw Fach R to Maes-glas |  |  | 94.75 | 93 | 93 | 97.48
33186 | RISCA (ST MARYS STREET) CSO , , | AN0250901 |  | SE | Gwent | Ebbw R - conf Ebbw Fach R to Maes-glas |  |  | 0.25 | 1 | 0 | 99.62
33189 | RISCA (TREDEGAR TERRACE) CSO , , | AN0251001 |  | SE | Gwent | Ebbw R - conf Ebbw Fach R to Maes-glas |  |  | 0.25 | 1 | 0 | 99.62
33188 | RISCA (MILL STREET) CSO , , | AN0251201 |  | SE | Gwent | Ebbw R - conf Ebbw Fach R to Maes-glas |  |  | 18.25 | 41 | 16 | 90.9
33193 | CSO NO.33193 TREDEGAR PARK GOLF CLU | AN0251301 |  | SE | Gwent | Ebbw R - conf Ebbw Fach R to Maes-glas |  |  | 603.75 | 94 | 94 | 94.48
33397 | CSO 5/6 FORGE LANE BASSALEG | AN0251401 |  | SE | Gwent | Ebbw R - conf Ebbw Fach R to Maes-glas |  |  | 0 | 0 | 0 | 99.62
33177 | ROSEMARY LANE CAR PARK (CSO) PONT | AN0261001 |  | SE | Gwent | Afon Lwyd - source to conf Dowlais Bk |  |  | 0 | 0 | 0 | 51.36 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
33927 | ST ALBANS SCHOOL (CSO) PONTYPOOL | AN0261101 |  | SE | Gwent | Afon Lwyd - source to conf Dowlais Bk |  |  | 248 | 61 | 61 | 91.84
70085 | A COMBINED SEWER OVERFLOW FISHPONDS | AN0262001 |  | SE | Cardiff | Rhymney R - conf Nant Cylla to Chapel Wood |  |  | 8.75 | 15 | 7 | 99.85
31359 | PWLLMEYRIC SPS (CSO) MONOUTH , | AN0265701 |  | SE | Gwent | Mounton Bk - source to R Severn Estuary |  |  | 1814 | 86 | 86 | 23.57 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
71274 | OCEAN PARK PUMPING STATION, TREMORFA, FORESHORE, ROVER WAY, BUTETOWN, CARDIFF | AN0267601 |  | SE | Central | Severn Estuary |  |  | 2 | 6 | 6 | 99.93
71727 | PILTON VALE CSO PILTON VALE MALPAS | AN0270901 |  | SE | Gwent | Pantyreos Bk - source to Barrack Hill |  |  | 104.75 | 25 | 23 | 96.13
72563 | TRAFFIC ISLAND, BELOW RAILWAY VIADUCT, FACTORY ROAD, BARGOED | AN0276201 |  | SE | South East | Nant Bargod Rhymni - source to conf Rhymney R |  |  | 53.25 | 28 | 19 | 98.33
31244 | HARTRIDGE SPS RINGLAND WAY NEWPORT | AN0276301 |  | SE | South East | Great-Spytty Reen - source to conf R Usk |  |  | 14 | 7 | 7 | 99.93
33726 | COG MOORS STW CDIFF RD DINAS POWYS | AN0280002 |  | SE | Central | SEVERN LOWER |  |  | 684.75 | 54 | 54 | 99.85
71664 | ABERPORTH ROAD, CARDIFF | AN028260101 |  | SE | Central | Whitchurch Bk - source to conf R Taff |  |  | 7.25 | 4 | 4 | 99.06
70407 | CSO 90414 | AN0287601 |  | SE | Gwent | Rhymney R - conf Nant Cylla to Chapel Wood |  |  | 15.5 | 11 | 11 | 99.08
32194 | A CSO 700M SE OF PLAS MACHEN COTAGE | AN0287701 |  | SE | Gwent | Rhymney R - conf Nant Cylla to Chapel Wood |  |  | 1911.5 | 116 | 116 | 99.83
32230 | APPROX 30M WEST OF NO 7 HIGH STREET | AN0287801 |  | SE | Gwent | Rhymney R - Nant Bargod Rhymni to conf Nant Cyl |  |  | 46 | 38 | 38 | 98.12
71704 | APPROX 40M SW OF FORGE ENG | AN0288001 |  | SE | Gwent | Rhymney R - conf Nant Cylla to Chapel Wood |  |  | 94 | 26 | 26 | 94.14
31222 | GARN PS CRICKHOWELL | AN0290601 |  | South East |  | Usk conf Afon Crawnon to conf Gavenny R |  |  | 136.75 | 56 | 56 | 99.53
72523 | PLEASANT VIEW CSO | AN0291201 |  | South East |  | Aman R - source to conf Afon Cynon |  |  | 249.25 | 74 | 74 | 83.06 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
31269 | PS AT CORPORATION ROAD LISWERRY | AN0293901 |  | SE | South East | USK |  |  | 596 | 135 | 135 | 99.94
33402 | MAESGLAS PS OFF MAESGLAS AV | AN0300301 |  | SE | South East | USK |  |  | 1289.25 | 181 | 181 | 99.94
33192 | CSO ASSET NO 90411 PENGAM | AN0301601 |  | SE | Gwent | Rhymney R - Nant Bargod Rhymni to conf Nant Cyl |  |  | 20.5 | 36 | 36 | 99.39
73173 | CHEPSTOW NORTH FAIRFIELD SPS | AN0302601 |  | SE | South East | Monks Ditch - source to Wainbridge |  |  | 307.25 | 97 | 89 | 99.93
71270 | CHEPSTOW NORTH SPS THE BACK | AN0302701 |  | SE | South East | WYE |  |  | 61.25 | 63 | 63 | 99.92
71705 | APPROX 85M EAST OF MARGARET STREET | AN0303401 |  | SE | Gwent | Rhymney R - Nant Bargod Rhymni to conf Nant Cyl |  |  | 66.75 | 43 | 43 | 99
31173 | CALDICOT SPS CALDICOT STW SITE | AN0303801 |  | SE | South East | SEVERN LOWER |  |  | 0 | 0 | 0 | 99.97
71904 | CHEPSTOW SOUTH SPS HUNGER PILL STW | AN0303901 |  | SE | South East | Monks Ditch - source to Wainbridge |  |  | 470 | 95 | 95 | 99.96
71389 | MAGOR SPS MAGOR STW SITE NEWPORT | AN0304001 |  | SE | South East | SEVERN LOWER |  |  | 0 | 0 | 0 | 99.92
71664 | ABERPORTH RD CSO CARDIFF | AN0304201 |  | SE | South East | R Taff - conf Rhondda R to Castle Street |  |  | 7.25 | 4 | 4 | 99.06
31134 | ABERCYNON PS WOOD RD ABERCYNON | AN0304801 |  | SE | Central | R Taff - conf R Cynon to conf Rhondda R |  |  | 883.25 | 84 | 84 | 99.95
71275 | CSO CAR PARK ABERCYNON RUGBY CLUB | AN0304901 |  | SE | Cardiff | R Cynon - conf Aman R to conf R Taff |  |  | 0.25 | 1 | 1 | 73.01 |  |  |  | Communications issue, resolved in April 2021.
71907 | RHYMNEY VALLEY TRUNK SEWER CSO | AN0305901 |  | SE | Cardiff | Rhymney R - conf Nant Cylla to Chapel Wood |  |  | 2025.5 | 135 | 135 | 89.58 |  |  |  | Data unreliable from 10/04 to 17/05/2021 . Due to static telemetry signal, resolved
71682 | WESTERN VALLEY TRUNK SEWER CSO | AN0306001 |  | SE | Cardiff | SEVERN LOWER |  |  | 3986.25 | 229 | 229 | 99.97
71235 | CARDIFF CENTRAL SPS TREMORFA | AN0306101 |  | South East |  | SEVERN LOWER |  |  | 287 | 82 | 82 | 99.94
31176 | CARDIFF EAST DISTRICT LONG OUTFALL | AN0308501 |  | SE | Central | Unnamed trib - source to conf Rhymney R |  |  | 710.75 | 71 | 71 | 99.85
32190 | CARDIFF EASTERN DISTRICT | AN0308601 |  | South East |  | SEVERN LOWER |  |  | 710.75 | 71 | 71 | 99.85
33345 | CSO LADIES ROW TREDEGER | AN0313101 |  | SE | Cardiff | Sirhowy R - source to Rock Villas |  |  | 5.75 | 8 | 3 | 99.51
71253 | CSO ABERAMAN IND EST ABERAMAN | AN0313301 |  | SE | Valleys | R Cynon - conf Aman R to conf R Taff |  |  | 1231 | 108 | 108 | 99.93
71657 | ST JOHN THE BAPTIST SCHOOL CWMDARE | AN0313401 |  | SE | Valleys | Afon Cynon - source to conf Aman R |  |  | - | - | - | 0 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
33340 | CSO 62A TREDEGAR RD EBBW VALE | AN0314901 |  | SE | Valleys | Ebbw R - source to conf Ebbw Fach R |  |  | 42 | 22 | 16 | 94.22
73415 | CSO AVENUE DE CLICHY MERTHYR | AN0315501 |  | SE | Valleys | R Taff - conf Taf Fechan to conf R Cynon |  |  | 43.25 | 28 | 28 | 99.86
32250 | ABERTYSSWG CSO ADJ DYFFRYN FARM | AN0315601 |  | SE | Cardiff | Rhymney R - source to conf Nant Bargod Rhymni |  |  | 580 | 88 | 88 | 98.49
32253 | A CSO AT PONTLOTTYN | AN0315701 |  | SE | Gwent | Rhymney R - source to conf Nant Bargod Rhymni |  |  | 547.25 | 88 | 88 | 99.94
32280 | CASTLE INN SSO ASSET NO 32280 | AN0316101 |  | SE | Valleys | R Taff - conf Rhondda R to Castle Street |  |  | - | - | - | 0 |  |  |  | Communications issue - ongoing investigation
32311 | A CSO AT PWLLGWAUN MILLFIELD | AN0316301 |  | SE | Cardiff | Rhondda R - conf Afon Rhondda Fach to conf R Ta |  |  | 749.25 | 112 | 112 | 98.81
31970 | CAERLEON TOWN SEWAGE PUMPING STATIO | AN0317201 |  | SE | Cardiff | Pantyreos Bk - source to Barrack Hill |  |  | 86 | 74 | 74 | 97.15
71498 | NEW RHONDDA CSO TONYPANDY | AN0318001 |  | SE | Valleys | Rhondda R - source to conf Afon Rhondda Fach |  |  | 523.5 | 91 | 91 | 98.97
71791 | A CSO AT CLYDACH VALE DAVIES STREET | AN0318101 |  | SE | Central | Rhondda R - source to conf Afon Rhondda Fach |  |  | 508 | 106 | 106 | 89.57 |  |  |  | Communications issue from 04/01/ to 03/02/2021, resolved.
32580 | NEW SOCIETY GARAGE CSO | AN0318601 |  | SE | Cardiff | Nant Clun - source to conf Ely R |  |  | 92 | 41 | 34 | 99.93
31353 | FAIRVIEW PUMPING STATION | AN0318701 |  | SE | Central | Ely R - conf Nant Clun to Allot Gardens, Ely |  |  | 0 | 0 | 0 | 94.91
31199 | DAN Y BRYN PS BRYNSADLER PONTYCLUN | AN0318801 |  | SE | Central | Ely R - conf Nant Clun to Allot Gardens, Ely |  |  | 0.25 | 1 | 0 | 99.93
71251 | COGAN STORM TANK COGAN PENARTH | AN0318901 |  | SE | Central | Ely R - conf Nant Clun to Allot Gardens, Ely |  |  | 0 | 0 | 0 | 99.62
71168 | A CSO AT TONGWYNLAIS RECREATION GRD | AN0319201 |  | SE | Cardiff | R Taff - conf Rhondda R to Castle Street |  |  | 1873.75 | 97 | 97 | 82.88 |  |  |  | Communications issue from 02/06 to 11/08/21, resolved.
71399 | CSO AT ABERBARGOED VIADUCT | AN0320301 |  | SE | Gwent | Nant Bargod Rhymni - source to conf Rhymney R |  |  | 456.75 | 48 | 48 | 99.94
33372 | A CSO @ COEDCAE HOUSE RASSAU | AN0321201 |  | SE | Central | Ebbw R - source to conf Ebbw Fach R |  |  | 78 | 24 | 15 | 98.69
33344 | A CSO AT NO9 MORGAN STREET TREDEGAR | AN0327101 |  | SE | Valleys | Sirhowy R - source to Rock Villas |  |  | 46 | 26 | 14 | 97.13
32055 | CSO 61 MARKHAM COLLIERY TERDEGAR | AN0327201 |  | SE | Gwent | Sirhowy R - source to Rock Villas |  |  | 28.25 | 12 | 12 | 99.62
30884 | GLASBURY STW GLASBURY NR HAY ON WYE | AN0330101 |  | SE | South East | R Wye - conf R Irfon to Brewardine Br |  |  | 436 | 40 | 36 | 99.91
71151 | A CSO AT TAFF STREET PONTYPRIDD | AN0330401 |  | SE | Valleys | R Taff - conf R Cynon to conf Rhondda R |  |  | 0.25 | 1 | 0 | 99.55
32212 | CSO AT MAESYCWMMER JUST OFF A472 | AN0331201 |  | SE | Gwent | Rhymney R - Nant Bargod Rhymni to conf Nant Cyl |  |  | 158.75 | 58 | 46 | 99.07
33155 | CSO ASSET NO 33155 PENGAM FORD ROAD | AN0331301 |  | SE | Cardiff | Rhymney R - Nant Bargod Rhymni to conf Nant Cyl |  |  | 862.25 | 105 | 105 | 99.45
32208 | TREDOMEN AFC CSO YSTRAD MYNACH | AN0331401 |  | SE | Gwent | Rhymney R - conf Nant Cylla to Chapel Wood |  |  | 1226.5 | 98 | 98 | 99.94
33365 | A CSO AT TREDEGAR ROAD EBBW VALE | AN0331501 |  | SE | Valleys | Ebbw R - source to conf Ebbw Fach R |  |  | 0.5 | 2 | 0 | 99.65
71199 | TREHERBERT IND EST CSO TREHERBERT | AN0331801 |  | SE | Central | Rhondda R - source to conf Afon Rhondda Fach |  |  | 72.75 | 33 | 29 | 99.93
71165 | RHYDFELIN CSO OFF LIONEL TERRACE | AN0332301 |  | SE | Valleys | R Taff - conf Rhondda R to Castle Street |  |  | 2058 | 172 | 172 | 99.93
71167 | YNYSANGHARAD PARK CSO PONTYPRIDD | AN0332401 |  | SE | Cardiff | R Taff - conf Rhondda R to Castle Street |  |  | 120.75 | 28 | 28 | 99.99
71161 | LONG ROW CSO BLAENLLECHAU FERNDALE | AN0332801 |  | SE | Valleys | Afon Rhondda Fach - source to conf Rhondda R |  |  | 0.75 | 1 | 1 | 76.03 |  |  |  | Communications issue, resolved in October 2021.
71159 | REAR OF TAFF STREET CSO FERNDALE | AN0332901 |  | SE | Valleys | Afon Rhondda Fach - source to conf Rhondda R |  |  | 0 | 0 | 0 | 99.69
71158 | CSO REAR OF FIR STREET FERNDALE | AN0333001 |  | SE | Valleys | Afon Rhondda Fach - source to conf Rhondda R |  |  | 772.25 | 106 | 100 | 98.14
32377 | STATION ROAD NR RAOD BRIDGE CSO | AN0333101 |  | SE | Valleys | Afon Rhondda Fach - source to conf Rhondda R |  |  | 0 | 0 | 0 | 1.92 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
32371 | FERNDALE BANANA TIP SSO ADDITIONAL | AN0333201 |  | SE | Valleys | Afon Rhondda Fach - source to conf Rhondda R |  |  | 674.75 | 80 | 80 | 98.98
32367 | FERNDALE BANANA TIP SSO | AN0333301 |  | SE | Valleys | Afon Rhondda Fach - source to conf Rhondda R |  |  | 527.25 | 95 | 95 | 98.5
30884 | GLASBURY STW GLASBURY NR HAY ON WYE | AN0333501 |  | SE | South East | R Wye - conf R Irfon to Brewardine Br |  |  | 0.75 | 1 | 1 | 75.49 |  |  |  | Data unreliable from 01/01 to 31/03/2021. Due to erratic telemetry signal, resolved.
70352 | CSO LAND ADJ CWAELOD Y WAUN VILLAS | AN0334901 |  | SE | Cardiff | Rhymney R - Nant Bargod Rhymni to conf Nant Cyl |  |  | 64.75 | 26 | 26 | 94.93
71144 | CSO CROSSBROOK STREET PONTYPRIDD | AN0337101 |  | SE | Valleys | R Taff - conf R Cynon to conf Rhondda R |  |  | 535.5 | 78 | 78 | 98.8
71297 | CSO NR BETAHNIA COTTAGES NEW TREDEG | AN0337801 |  | SE | South East | Rhymney R - source to conf Nant Bargod Rhymni |  |  | 179.5 | 62 | 62 | 98.84
73420 | BEULAH SPS BEULAH POWYS | AN0337901 |  | SE | South East | Afon Cammarch - source to conf R Irfon |  |  | 2027 | 206 | 198 | 99.65
32364 | CSO OPP 37 EDMONDES ST TYLORSTOWN | AN0350101 |  | SE | Valleys | Afon Rhondda Fach - source to conf Rhondda R |  |  | 623.75 | 100 | 100 | 98.43
71189 | FERNDALE ROAD CSO TYLORSTOWN RCT | AN0350301 |  | SE | Valleys | Afon Rhondda Fach - source to conf Rhondda R |  |  | 705.25 | 76 | 76 | 99.1
71188 | PONTYGWAITH BRIDGE CSO ASSET 71188 | AN0350401 |  | SE | Valleys | Afon Rhondda Fach - source to conf Rhondda R |  |  | 132.5 | 53 | 53 | 98.07
70106 | CSO REAR OF TYLORSTOWM PRIMARY SCHL | AN0350501 |  | SE | Valleys | Afon Rhondda Fach - source to conf Rhondda R |  |  | 1147.5 | 133 | 122 | 98.18
32037 | CSO 49 NR VICARAGE GLEBE HOUSE | AN0351101 |  | SE | Gwent | Ebbw R - conf Ebbw Fach R to Maes-glas |  |  | 5 | 17 | 17 | 99.41
33333 | CSO 19 GRYPHON CONCRETE PRODUCTS | AN0351301 |  | SE | Valleys | Sirhowy R - Rock Villas to conf Afon Ebwy |  |  | 467.5 | 67 | 67 | 97.4
30988 | MONMOUTH STW REDBROOK ROAD MONMOUTH | AN0353501 |  | SE | South East | R Wye - conf Walford Bk to Bigsweir Br |  |  | 724.25 | 63 | 61 | 100
70394 | THE MEADS CSO REAR OF 91 PLAS CWRT | AN0354101 |  | SE | Gwent | Dowlais Bk - source to conf Afon Lwyd |  |  | 111.25 | 33 | 29 | 99.2
70063 | PETERSTON SUPER ELY STW CSO MAIN AV | AN0355001 |  | SE | Central | Ely R - conf Nant Clun to Allot Gardens, Ely |  |  | 57.5 | 26 | 20 | 98.23
73563 | PONTSTICILL WWTW | AN0356601 |  | SE | West | Taf Fechan - source to conf Afon Taf Fawr |  |  | 1316.25 | 76 | 76 | 99.91
71576 | COLCOT ROAD/CLAUDE ROAD ASSEST NO | AN0356801 |  | SE | Central | Barry Brook (culverted) |  | Cold Knap | 0 | 0 | 0 | 99.58
71299 | TON PENTRE PS CSO TONT PENTRE RCT | AN0357201 |  | SE | Central | Rhondda R - source to conf Afon Rhondda Fach |  |  | 910 | 138 | 138 | 91.08
30942 | LLANDRINDOD WELLS STW PARK LANE | AN0357501 |  | SE | South East | R Ithon - conf Camddwr Bk to conf R Wye |  |  | 0.5 | 2 | 2 | 99.65
71217 | ELISABETH CLOSE CSO PENTRE RCT | AN0357801 |  | SE | Central | Rhondda R - source to conf Afon Rhondda Fach |  |  | 3 | 6 | 6 | 99.99
71217 | LEWIS STREET CSO & PUMPING STATION | AN0357901 |  | SE | Central | Rhondda R - source to conf Afon Rhondda Fach |  |  | 3 | 6 | 6 | 99.99
72167 | WVTS - NEWBRIDGE SSO CAERPHILLY | AN0360201 |  | SE | Valleys | Ebbw R - conf Ebbw Fach R to Maes-glas |  |  | 6.25 | 8 | 8 | 90.14
32095 | OLD SOUTH GRIFFIN COLLIERY CSO | AN0360301 |  | SE | South East | Ebbw Fach R - source to conf Ebbw R |  |  | 1 | 2 | 1 | 99.32
72166 | CASTLE STREET RAILWAY LINE | AN0360601 |  | SE | Valleys | Ebbw Fach R - source to conf Ebbw R |  |  | 0 | 0 | 0 | 99.61
72141 | COMMERCIAL STREET (NEXT TO BANK) | AN0360701 |  | SE | Valleys | Ebbw Fach R - source to conf Ebbw R |  |  | 0 | 0 | 0 | 99.9
72173 | LIBRARY ON HIGH STREET BLAINA | AN0360801 |  | SE | Valleys | Ebbw Fach R - source to conf Ebbw R |  |  | 550 | 77 | 77 | 99.93
72091 | CROSS STREET YNYSHIR R-C-T | AN0361001 |  | SE | Valleys | Afon Rhondda Fach - source to conf Rhondda R |  |  | 79 | 54 | 54 | 99.99
72325 | CRUMLIN SWFFRYD SSO CAERPHILLY | AN0361101 |  | SE | Valleys | Ebbw R - conf Ebbw Fach R to Maes-glas |  |  | 134 | 47 | 47 | 82.25 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
71852 | DOLGWILYM ST NO 2 PONTYGWAITH | AN0361301 |  | SE | Cardiff | Afon Rhondda Fach - source to conf Rhondda R |  |  | 5.5 | 5 | 5 | 99.51
71980 | CSO 65 BEAUFORT TERRACE EBBW VALE | AN0361401 |  | SE | Valleys | Ebbw R - source to conf Ebbw Fach R |  |  | 4.75 | 13 | 13 | 99.59
33374 | CSO O/S BEAUFORT ARMS EBBW VALE | AN0361601 |  | SE | Cardiff | Ebbw R - source to conf Ebbw Fach R |  |  | 0.25 | 1 | 0 | 98.92
33366 | QUEENS SQUARE CSO EBBW VALE | AN0361701 |  | SE | Valleys | Ebbw R - source to conf Ebbw Fach R |  |  | 0 | 0 | 0 | 99.89
33341 | WINDOSR HOUSE CSO EBBW VALE | AN0361801 |  | SE | Gwent | Ebbw R - source to conf Ebbw Fach R |  |  | 0.5 | 2 | 0 | 99.62
72278 | JAMES TERRACE YNYSHIR R-C-T | AN0362301 |  | SE | Valleys | Afon Rhondda Fach - source to conf Rhondda R |  |  | 1.75 | 3 | 3 | 99.86
72169 | OPP NO 11 BRYNHYFRYD TERR EBBW VALE | AN0362501 |  | SE | Cardiff | Ebbw R - source to conf Ebbw Fach R |  |  | 10.75 | 18 | 18 | 99.93
71981 | GOSPEL HALL CSO BEAUFOR RD EBBW VA | AN0362601 |  | SE | Valleys | Ebbw R - source to conf Ebbw Fach R |  |  | 67 | 19 | 19 | 99.93
72135 | R/O ST MICHAELS CHURCH ABERTILLERY | AN0362801 |  | SE | Valleys | Ebbw Fach R - source to conf Ebbw R |  |  | 19.25 | 22 | 22 | 99.93
72327 | Malvern Terrace CSO | AN0362901 |  | SE | Gwent | Ebbw R - conf Ebbw Fach R to Maes-glas |  |  | 1 | 4 | 0 | 99.61
72110 | TYNYBRYN ROAD TONYREFAIL R-C-T | AN0363001 |  | SE | Valleys | Ely R - source to conf Nant Mychydd |  |  | 9.75 | 7 | 5 | 99.49
31402 | ABERLLYNFI/THREE COCKS SPS POWYS | AN0364001 |  | SE | Bridgend Hereford & Mid | Afon Llynfi - conf Dulas Bk to conf R Wye |  |  | 89.5 | 27 | 25 | 99.75
33758 | YSTRAD OWEN PS VALE OF GLAMORGAN | AN0364101 |  | SE | Central | Ely R - conf Nant Clun to Allot Gardens, Ely |  |  | 381.25 | 28 | 26 | 99.94
71787 | A COMBINED SEWER OVERFLOW CSO R/O W | AN0368101 |  | SE | Gwent | Rhymney R - conf Nant Cylla to Chapel Wood |  |  | 226.25 | 23 | 23 | 99.36
31098 | TALGARTH STW | AN0373401 |  | SE | South East | Afon Llynfi - conf Dulas Bk to conf R Wye |  |  | 117.75 | 22 | 20 | 99.76
71582 | A COMBINED SEWER OVERFLOW PONTYPRID | AN0373501 |  | SE | Central | Barry Brook |  | Cold Knap | 0 | 0 | 0 | 99.11 | BW | 5 in Bathing Season
32325 | REAR OF RICHARDS TERRACE FOUL PUMPI | AN0373601 |  | SE | Central | Rhondda R - source to conf Afon Rhondda Fach |  |  | 306 | 34 | 34 | 98.92
71609 | A COMBINED SEWER OVERFLOW TREHAFOD | AN0374601 |  | SE | Valleys | Rhondda R - conf Afon Rhondda Fach to conf R Ta |  |  | 379.25 | 30 | 30 | 99.15
71698 | A COMBINED SEWER OVERFLOW GYFEILLON | AN0374701 |  | SE | Valleys | Rhondda R - conf Afon Rhondda Fach to conf R Ta |  |  | 1 | 2 | 2 | 99.93
71605 | CS0 68 REAR OF LILLIAN GROVE EBBW V | AN0377001 |  | SE | Valleys | Ebbw R - source to conf Ebbw Fach R |  |  | 0 | 0 | 0 | 99.89
33592 | A COMBINED SEWER OVERFLOW CSO 111 W | AN0377101 |  | SE | Gwent | Ebbw R - conf Ebbw Fach R to Maes-glas |  |  | 947 | 80 | 80 | 98.92
71796 | BALL ROAD CSO OFF BALL LANE LLANRUM | AN0377301 |  | SE | Cardiff | Rhymney R - conf Nant Cylla to Chapel Wood |  |  | 1279.75 | 96 | 96 | 99.91
31311 | MALPAS PARK/ROWAN WAY PS,MALPAS,NEW | AN0378401 |  | SE | South East | Pantyreos Bk - source to Barrack Hill |  |  | 96.75 | 30 | 29 | 99.92
33392 | REAR OF 11 ROBERTSONS WAY CSO, MALP | AN0378501 |  | SE | Gwent | Pantyreos Bk - source to Barrack Hill |  |  | 29.75 | 13 | 6 | 93.43
33361 | A COMBINED SEWER OVERFLOW BRYNMAWR | AN0378601 |  | SE | Central | R Clydach - source to conf R Usk |  |  | 95 | 36 | 36 | 86.42 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
30889 | GOYTRE SEWAGE TREATMENT WORKS NANT | AN0379201 |  | SE | South East | R Usk - conf R Gavenny to conf Olway Bk |  |  | 3427.75 | 186 | 182 | 99.91
71736 | SOMERTON ROAD BALMORAL ROAD CSO NEW | AN0379501 |  | SE | Gwent | Great-Spytty Reen - source to conf R Usk |  |  | 26 | 34 | 34 | 99.99
33163 | A COMBINED SEWER OVERFLOW ST JULIAN | AN0379601 |  | SE | Valleys | Llwynau Bk - source to conf R Usk |  |  | 27.25 | 36 | 36 | 99.98
71797 | WESTFIELD WAY/HUXLEY GREEN CSO | AN0379701 |  | SE | Valleys | Pantyreos Bk - source to Barrack Hill |  |  | 290 | 73 | 73 | 99.93
31245 | A SEWAGE PUMPING STATION HAY ON WYE | AN0379801 |  | SE | South East | R Wye - conf R Irfon to Brewardine Br |  |  | 559.5 | 183 | 183 | 99.83
32590 | A COMBINED SEWER OVERFLOW DYFRIG ST | AN0382401 |  | SE | Central | Barry Dock No1 |  | Cold Knap | 0 | 0 | 0 | 99.91
30975 | LLYSWEN STW CHURCH ROAD LLYSWEN | AN0390301 |  | SE | South East | R Wye - conf R Irfon to Brewardine Br |  |  | 37 | 7 | 7 | 89.78 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
30956 | LLANGYBI STW LLANGYBI USK | AN0391001 |  | SE | South East | R Usk - conf Olway Bk to New Br |  |  | 1155.75 | 162 | 142 | 99.93
31029 | PANDY STW PANDY MONMOUTHSHIRE | AN0391101 |  | SE | South East | Afon Honddu - source to conf R Monnow |  |  | 488.25 | 39 | 39 | 99.94
31057 | PRESTEIGNE STW CLATTERBROOM | AN0391701 |  | SE | West | R Lugg - conf Norton Bk to conf R Arrow |  |  | 121.75 | 19 | 19 | 99.92
71972 | BARRY BRIDGE STREET CSO BARRY | AN0392501 |  | SE | Central | Cadoxton - headwaters to tidal limit |  |  | 0 | 0 | 0 | 98.52 | BW | 5 in Bathing Season
71770 | HOLTON ROAD CSO HOLTON ROAD | AN0392601 |  | SE | Central | Barry Dock No. 1 |  | Jacksons | 3 | 7 | 7 | 99.93 | BW | 5 in Bathing Season
72043 | ARGAE LANE CSO ARGAE LANE BARRY | AN0392801 |  | SE | Central | Cadoxton - headwaters to tidal limit |  |  | 0 | 0 | 0 | 99.41 | BW | 5 in Bathing Season
70466 | COLDBROOK RD EAST 2 BARRY | AN0393301 |  | SE | Central | Cadoxton - headwaters to tidal limit |  |  | 117.25 | 11 | 11 | 93.06 | BW | 5 in Bathing Season
33152 | CSO AT BARRACK HILL NEWPORT | AN0394701 |  | SE | Cardiff | USK |  |  | 4.5 | 17 | 17 | 99.61
31236 | GRAIG PENLLYN PUMPING STATION VOG | AN0408301 |  | SE | Central | Thaw - headwaters to confluence with Kenson |  |  | 0 | 0 | 0 | 99.99
32226 | TRELYN LANE CSO FLEUR-DE-LIS | AN0408601 |  | SE | Cardiff | Rhymney R - Nant Bargod Rhymni to conf Nant Cyl |  |  | 229.5 | 51 | 44 | 99.17
72145 | RIVER TERRACE CSO TREORCHY RHONDDA | AN0408701 |  | SE | Cardiff | Rhondda R - source to conf Afon Rhondda Fach |  |  | 9 | 5 | 5 | 64.98 |  |  |  | Communications issue, resolved in May 2021.
72144 | RIVER TERRACE CSO TREORCHY RHONDDA | AN0408801 |  | SE | Cardiff | Rhondda R - source to conf Afon Rhondda Fach |  |  | 82.5 | 36 | 36 | 99.93
72035 | NEW SOUTH GRIFFIN COLLIERY CSO | AN0408901 |  | SE | Cardiff | Ebbw Fach R - source to conf Ebbw R |  |  | 63.5 | 18 | 18 | 99.22
73423 | ABERTHAW WWTW W ABERTHAW BARRY | AN0419401 |  | SE | Central | Bristol Channel Inner North |  |  | 803 | 56 | 56 | 99.91
72094 | CSO REAR COMMERC'L ST SENGHENYDD | AN0420401 |  | SE | Valleys | Nant y Aber - source to conf Rhymney R |  |  | 43 | 32 | 22 | 99.99
33530 | WINDSOR PLACE SENGHENYDD CSO CAE'Y | AN0420501 |  | SE | South East | Nant y Aber - source to conf Rhymney R |  |  | 2.5 | 7 | 1 | 99.61
30950 | LLANGAMMARCH WELLS STW EJECTOR | AW1003302 |  | SE | South East | R Irfon - conf Tirabad Dulas to conf R Wye |  |  | 1085.75 | 73 | 71 | 99.93
30954 | LLANGUNLLO STW PS | AW1003502 |  | SE | South East | Lugg Bk - source to conf Bleddfa Bk |  |  | 2414.25 | 139 | 138 | 99.93
31957 | LLANWRTYD WELLS SSO ON TRUNK SEWER | AW1003902 |  | SE | Bridgend Hereford & Mid | R Irfon - conf Afon Gwesyn to conf Cledan |  |  | 1784.25 | 127 | 127 | 99.97
31958 | ABERNANT SSO LLANWRTYD WELLS TRUNK | AW1003903 |  | SE | Bridgend Hereford & Mid | R Irfon - conf Afon Gwesyn to conf Cledan |  |  | 1805.5 | 139 | 130 | 98.32
71378 | DOLWEN FIELD SSO LLANWRTYD WELLS TR | AW1003904 |  | SW | Bridgend Hereford & Mid | R Irfon - conf Afon Gwesyn to conf Cledan |  |  | 194 | 50 | 50 | 99.83
30970 | LLANYRE STW | AW1004002 |  | SE | South East | R Ithon - conf Camddwr Bk to conf R Wye |  |  | - | - | - | 0 |  |  |  | Further work needed on discharge mechanism, revisit planned for 2022.
31062 | STORM TANKS AT RHAYADER STW | AW1005202 |  | SE | South East | R Wye - conf to conf Afon Marteg to co |  |  | 885.5 | 80 | 75 | 99.97
32937 | HIRWAUN STW STORM TANKS HIRWAUN | BA1002401 |  | SW | Central | Sychryd - headwaters to confluence wit |  |  | 63 | 24 | 18 | 99.92
51069 | P'BONT NEWBRDG FLDS SWO PS | BA2032003 |  | SW | Bridgend Hereford & Mid Wales | Ogmore - confluence with Llynfi to tidal limit |  | Southerndown | 7.75 | 5 | 5 | 99.45
51020 | LLANGYNDEYRN PS INTO R GWENDRAETH FACH | BB3391CY |  | South West |  | Gwendraeth Fach - headwaters to tidal limit |  |  | 7 | 4 | 4 | 71.34 |  |  |  | Communications issue, resolved in April 2021.
52329 | GCG - D/s of Graig Road CSO | BB3391FP |  | SW | West | Garnant - headwaters to confluence with Aman |  |  | 478.5 | 37 | 35 | 17 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
33506 | LLWYDCOED SIDE OF LLWYDCOED MOTORS | BB3391HS |  | SE | South East | Afon Cynon - source to conf Aman R |  |  | 198 | 48 | 43 | 81.51 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
70351 | NEW TREDEGAR BIRCH GROVE | BB3391ZD |  | SE | South East | Rhymney R - source to conf Nant Bargod Rhymni |  |  | 3.5 | 6 | 3 | 63.05 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
2087 | OLD COLWYN BEACH ROAD | BB3392CQ |  | N | North | Nant Y Flynnon |  |  | 15.25 | 44 | 14 | 99.32
33368 | EBBW VALE RASSAU ROAD UNDER FLYOVER | BB3392HM |  | SE | South East | Ebbw R - source to conf Ebbw Fach R |  |  | 91 | 29 | 23 | 98.77
71366 | Bronllys Rear of garage A479 | BB3393FM |  | SE | West | Afon Llynfi - conf Dulas Bk to conf R Wye |  |  | 82.75 | 58 | 37 | 96.01
71354 | Rhayader fields St. Brides Church | BB3393NC |  | SW | West | R Wye - conf to conf Afon Marteg to conf Afon Elan |  |  | 10 | 10 | 5 | 99.45
32491 | ABERAMAN CYNON STREET REAR OF | BB3394FX |  | SE | South East | Aman R - source to conf Afon Cynon |  |  | 2.75 | 7 | 1 | 99.56
72602 | Woodland, B4263/Bryn Siriol, Caerphilly | BB3395CU |  | SE | South East | Nant y Aber - source to conf Rhymney R |  |  | 173.25 | 58 | 58 | 98.69
71695 | O/S R/O 33 CHURCH STREET YSTRAD MYNACH | BB3395FK | [6 empty] | 0.75 | 2 | 1 | 99.58
33513 | DOWLAIS MARKET STREET & HIGH STREET JNCT | BB3396CG |  | SE | South East | Nant Morlais - source to conf R Taff |  |  | 0.25 | 1 | 0 | 99.33
73375 | Excelsior Street (rear lane) Ebbw Vale | BB3494FK |  | SE | South East | Ebbw R - source to conf Ebbw Fach R |  |  | 0.5 | 2 | 0 | 99.62
72640 | 47 SANNAN ST. ABERBARGOED CSO | BB3494HH |  | SE | South East | Rhymney R - Nant Bargod Rhymni to conf Nant Cylla |  |  | 0 | 0 | 0 | 69.77 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
33352 | THE SQUARE STREET, ABERTILLERY | BB3495CG |  | SE | South East | Ebbw Fach R - source to conf Ebbw R |  |  | 365.5 | 71 | 58 | 98.62
32035 | EBBW VALE BEAUFORT LAMBS SQUARE | BB3495FH |  | SE | South East | Ebbw R - source to conf Ebbw Fach R |  |  | 1.25 | 3 | 1 | 99.39
33337 | COMMERCIAL ROAD, ABERTILLERY | BB3495ZX |  | SE | South East | Ebbw R - conf Ebbw Fach R to Maes-glas |  |  | 2.5 | 8 | 8 | 98.27
32032 | Allotment Road CSO Glyncoed | BB3496CT |  | SE | South East | Ebbw R - source to conf Ebbw Fach R |  |  | 60.5 | 9 | 8 | 98.45
31954 | Three Cocks - Gwernyfred Park | BB3496FC |  | SE | West | Afon Llynfi - conf Dulas Bk to conf R Wye |  |  | 6.25 | 2 | 1 | 74.33 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
73323 | Brooklyn Terrace CSO Abertillery | BB3496HN |  | SE | South East | Ebbw R - conf Ebbw Fach R to Maes-glas |  |  | 1 | 4 | 4 | 45.36 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
33353 | ABERTILLERY VICTORIA ROAD SIX BELLS | BB3496ZK |  | SE | South East | Ebbw Fach R - source to conf Ebbw R |  |  | - | - | - | 0 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
31405 | TINTERN SSO | BB3691CL |  | SE | South East | R Wye - conf Walford Bk to Bigsweir Br |  |  | 1246.5 | 268 | 243 | 96.17
33934 | ABERTILLERY SIX BELLS ROAD | BB3693FH |  | SE | South East | Ebbw Fach R - source to conf Ebbw R |  |  | 0.5 | 2 | 0 | 99.34
33327 | BLAENAVON BAND HUT MH 57A SWO 2 | BB3693NA |  | SE | South East | Afon Lwyd - source to conf Dowlais Bk |  |  | 198.25 | 57 | 57 | 98.93
32140 | PONTYPOOL FREEHOLDLAND ROAD | BB3694CT |  | SE | South East | Afon Lwyd - source to conf Dowlais Bk |  |  | 153.25 | 51 | 51 | 98.2
31398 | Presteigne - o/s SPS Tanyard | BB3694FC |  | SE | West | R Lugg - conf Norton Bk to conf R Arrow |  |  | 211 | 33 | 33 | 98.96
72000 | Warren Close SPS Overflow | BB3694ZK |  | South East |  | Wye - Scithwen Bk to Brewardine Br |  |  | 0 | 0 | 0 | 99.94
72478 | Abertillery Six Bells Colliery No. 2 CSO | BB3695CF |  | SE | South East | Ebbw Fach R - source to conf Ebbw R |  |  | 830.5 | 63 | 58 | 79 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
31112 | CSO & EO at Weycock Cross SPS | BB3798HP |  | SE | Central | Waycock - headwaters to confluence with Kenson |  |  | 66 | 8 | 8 | 14.67 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
961 | LLANDANWG SPS | BB3892ZK |  | N | North West | Artro |  |  | 4.75 | 1 | 1 | 100
604 | PORTHMADOG BORTH-Y-GEST SPS | BB3893CF |  | N | North West | Un-named to Glaslyn estuary north |  |  | 71 | 75 | 75 | 99.95
71649 | LLAWR PENTRE (Near Beach Road) | BB3893FN |  | N | North | Nant Y Flynnon |  |  | 3.75 | 10 | 10 | 99.65
74565 | Plas Y Coed CSO, Glyn neath | BB3893NJ |  | SW | West | Neath - conf with Nedd Fechan and Mellte to TL |  |  | 109.75 | 41 | 34 | 99.47
71407 | REAR OF CANAL COTTAGE ABERCRAVE | BB3893ZH |  | SW | West | Tawe - conf with Nant Llech to conf with Giedd |  |  | 938.75 | 94 | 86 | 96.77
73069 | Belle Vue Road Old Cwmbran | BB3894CZ |  | SE | South East | Dowlais Bk - source to conf Afon Lwyd |  |  | 77.75 | 41 | 41 | 98.88
71384 | Trefecca old Railway Maesgwyn | BB3894FV |  | SE | West | Afon Llynfi - source to conf Dulas Bk |  |  | 83.5 | 34 | 23 | 98.5
33369 | EBBW VALE HARCOURT STREET NO 4 REAR OF | BB3894HA |  | SE | South East | Ebbw R - source to conf Ebbw Fach R |  |  | 0 | 0 | 0 | 99.07
71656 | High st, Abercan, o/s Chemist | BB3894ZC |  | SE | South East | Ebbw R - conf Ebbw Fach R to Maes-glas |  |  | 2.25 | 8 | 8 | 97.59
33512 | Cefn Coed High St CSO | BB3895CE |  | SE | South East | Taf Fechan - source to conf Afon Taf Fawr |  |  | 8.25 | 20 | 7 | 99.33
73068 | BLAEN-Y-CWM Terrace CSO | BB3895FA |  | SE | South East | Rhondda R - source to conf Afon Rhondda Fach |  |  | 5.75 | 7 | 2 | 95.74
70711 | Ogmore Vale End of Railway Terrace | BB3895ZN |  | SW | West | Ogwr Fawr - headwaters to confluence with Ogmore |  |  | 0.5 | 2 | 2 | 98.94
73060 | Oakfield Terrace Nantymoel | BB3896CW |  | SW | West | Ogwr Fawr - headwaters to confluence with Ogmore |  |  | 0.25 | 1 | 1 | 99.45
72653 | Heol Y Llwyni CSO | BB3896FD |  | SW | West | Llynfi - headwaters to Lletty Brongu STW |  |  | 2.5 | 6 | 6 | 99.73
72654 | Church Street, Maesteg | BB3896HJ |  | SW | West | Llynfi - headwaters to Lletty Brongu STW |  |  | 17.75 | 19 | 19 | 94.31
72652 | Castle Street CSO | BB3896ZV |  | SW | West | Llynfi - headwaters to Lletty Brongu STW |  |  | 17 | 24 | 24 | 99.38
71436 | REAR OF DAN-Y-BRYN GILFACH GOCH | BB3897CR |  | SE | South East | Ogwr Fach - headwaters to confluence with Ogmore |  |  | 82 | 54 | 34 | 98.11
73317 | YNYSYBWL O/S 2 CLYDACH TERRACE | BB3897FJ |  | SE | South East | Nant Clydach - source to conf R Taff |  |  | 149.75 | 41 | 41 | 99.25
72601 | 64 Commercial Street Senghenydd CSO | BB3897HP |  | SE | South East | Nant y Aber - source to conf Rhymney R |  |  | 16.25 | 18 | 9 | 98.6
72607 | REES STREET 71 CSO PENTRE | BB3897ZA |  | SE | South East | Rhondda R - source to conf Afon Rhondda Fach |  |  | 1.75 | 7 | 0 | 66.71 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
71435 | NR GLANNANT HEOL HEULOG GILFACH GOCH | BB3898CY |  | SW | West | Ogwr Fach - headwaters to confluence with Ogmore |  |  | 0.75 | 3 | 3 | 99.73
73253 | 136 TYNTYLA ROAD CSO, TONYPANDY | BB3898FP |  | SE | Central | Rhondda R - source to conf Afon Rhondda Fach |  |  | 0 | 0 | 0 | 99.6
71767 | Llanbedr CSO | BB3898HS |  | N | North | Artro |  |  | 0 | 0 | 0 | 99.73
72634 | Old Brithweunydd Road CSO Tonypandy | BB3898ZD |  | SE | South East | Rhondda R - source to conf Afon Rhondda Fach |  |  | 23.25 | 28 | 12 | 99.78
33529 | ABERTRIDWR COED CAE ROAD 1 | BB3899CQ |  | SE | South East | Nant y Aber - source to conf Rhymney R |  |  | 1 | 4 | 0 | 89.85 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
70408 | Graig-Y-Fedw CSO | BB3899FS |  | SE | South East | Nant y Aber - source to conf Rhymney R |  |  | 214 | 65 | 57 | 98.4
72416 | Rear of 15 Llwyn Onn CSO Croesyceiliog | BB3992ZH |  | SE | South East | Afon Lwyd - source to conf Dowlais Bk |  |  | 26.5 | 22 | 16 | 98.97
71665 | Rede Rd CSO | BB3993FV |  | SE | South East | Dowlais Bk - source to conf Afon Lwyd |  |  | 123.5 | 28 | 22 | 99.34
72989 | 2 Llangorse Road CSO Llanyravon | BB3993NP |  | SE | South East | Afon Lwyd - source to conf Dowlais Bk |  |  | 0 | 0 | 0 | 98.8
72586 | 103 Beaumaris Drive Cwmbran CSO | BB3994HD |  | SE | South East | Afon Lwyd - source to conf Dowlais Bk |  |  | 3.5 | 3 | 2 | 97.31
72988 | 3 Olway close CSO Llanyravon | BB3994ZN |  | SE | South East | Afon Lwyd - source to conf Dowlais Bk |  |  | 0 | 0 | 0 | 23.44 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
73335 | 7 Olway Close CSO, Llanyravon | BB3995CW |  | SE | South East | Afon Lwyd - source to conf Dowlais Bk |  |  | 1 | 4 | 0 | 98.72
51414 | CSO 104 NEWBRIDGE ROAD PUMPING STATION | BB4025501 |  | SW | Central | River Afan | Swans E | Aberfan | 305.5 | 50 | 50 | 99.95 | BW | 5 in Bathing Season | YES
50586 | CROSSHANDS WWTW SSO CROSSHANDS CARM | BC0001501 |  | SW | South West | Gwili - headwaters to tidal limit |  |  | 0 | 0 | 0 | 100
50628 | GOWERTON WWTW VICTORIA ROAD GOWER | BC0003001 |  | SW | Central | LOUGHOR |  |  | 254.25 | 39 | 39 | 99.95 | SFW | 26 in the Year | YES
50685 | LLANSAINT WWTW LLANSAINT FERRYSIDE | BC0006102 |  | SW | Central | Llansaint Stream | Gwendrae |  | 192.5 | 26 | 19 | 100 | BW | 5 in Bathing Season
72320 | 250M DOWN STREAM OF GLAN-YR-AFON | BC0006503 |  | SW | West | Morlais - headwaters to tidal limit |  |  | 169 | 42 | 42 | 99.99
72321 | REAR OF TRIO ENGINEER'G LLANGENNECH | BC0006504 |  | SW | Swansea | Morlais - headwaters to tidal limit |  |  | 123.75 | 46 | 46 | 76.84 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
72337 | LLANGENNECH P.STN.SSO LLANELLI | BC0006505 |  | SW | West | Morlais - headwaters to tidal limit |  |  | 0 | 0 | 0 | 99.7
72475 | BENSON ROAD CSO BENSON RD PENCLAWDD | BC0013903 |  | SW | Swansea | Burry Estuary via surface water sewer | Burry S |  | 8 | 8 | 5 | 99.95 | SFW | 14 in the Year
50795 | TREBANOS STW (SETTLED STORM) TREBA | BC0016601 |  | SW | Central | Tawe |  |  | 3231.25 | 182 | 182 | 99.23
51937 | PONTARDAWE 2 TO R TAWE CSO SWANSEA | BC0016801 |  | SW | Swansea | Tawe -confluence with Twrch to tidal limit |  |  | 67.5 | 14 | 14 | 100
71703 | MYNNYDD CERRIG PUMPING STATION | BD0025101 |  | South West |  | Gwendraeth Fach - headwaters to tidal limit |  |  | 1371.5 | 96 | 96 | 100
50875 | LLANMADOC PS NO. 1 EMERGEN | BE0006401 |  | SW | Central | Burry Pill | Burry S |  | 0.25 | 1 | 0 | 98.51
50902 | LLANMADOC SPS NO. 2 EMERGENCY DISCHARGE | BE0006402 |  | SW | Central | Burry Pill | Burry S |  | 0 | 0 | 0 | 100 | BW | 5 in Bathing Season
50834 | BALDWINS CRESCENT SPS | BE0010501 |  | SW | Central | COASTAL WATERS | Swans E |  | 619.5 | 55 | 54 | 99.98
50918 | TEMPORARY INCREASED DIS. FROM | BE0010502 |  | SW | Central | SEA OUTFALL | Swans E |  | 188.75 | 32 | 32 | 99.98
50868 | CASWELL BAY CAR PARK SPS CASWELL | BE0022301 |  | SW | Central | Caswell Bay | Swans S | Caswell | 9.5 | 4 | 4 | 99.99
50673 | LLANGYNDEYRN STW | BE0039502 |  | SW | South West | Gwendraeth Fach - headwaters to tidal limit |  |  | 0 | 0 | 0 | 100
73484 | CUCKOO MILL PS . . | BE0075602 |  | SW | Central | Clyne River - headwaters to tidal limit |  |  | 922 | 66 | 66 | 96.3
73365 | PENYGROES WWTW SSO PONTLASH | BF0083302 |  | South West |  | The Lash |  |  | 2050 | 139 | 137 | 99.96
51955 | CAMBRIAN STREET P.S. SSO | BF0083605 |  | SW | Central | Loughor Outer | Burry N |  | 9 | 7 | 7 | 100 | SFW | 14 in the Year
51173 | SSO AT STATION ROAD P.S. KIDWELLY | BF0147004 |  | SW | Central | Gwendraeth Fach Estuary | Gwendrae |  | 1 | 3 | 3 | 18.12 |  |  |  | Communications issue, resolved in October 2021.
51426 | CWM CAPEL PS BURRY PORT | BF0177707 |  | SW | Central | right bank of nant dyfatty | Burry N |  | 25.75 | 3 | 2 | 100
51427 | SHORELINE PS BURRY PORT | BF0177708 |  | SW | Swansea | right bank of an unnamed stream flowing to outer harbour | Burry N |  | 0 | 0 | 0 | 99.73
51754 | MAENCLOCHOG STW | BG0000402 |  | SW | South West | E. Cleddau - conf with Wern to conf with Syfynw |  |  | 2356.5 | 167 | 164 | 100
50547 | BONCATH STW | BG0001202 |  | SW | South West | Morgenau - headwaters to confluence with Teifi |  |  | 2652.5 | 160 | 156 | 98.88
51095 | PENCADER STW EO PENCADER CARMARTHEN | BG0007802 |  | SW | South West | Talog - headwaters to confluence with Tyweli |  |  | 211.75 | 25 | 23 | 99.67
50736 | PENCADER STW STORM TANKS | BG0007805 |  | SW | South West | Tyweli - headwaters to confluence with Teifi |  |  | 1576.75 | 103 | 102 | 99.68
51667 | ST ISHMAELS WORKS INLET . . | BG0011502 |  | SW | South West | St Ishmaels Stream - HW to tidal limit, Monk Ha |  |  | 1980.25 | 110 | 110 | 98.56
50811 | WOLFSCASTLE STW . . | BG0011602 |  | SW | South West | Anghof - headwaters to conf with Western Cledda |  |  | 126 | 25 | 21 | 95.88
50650 | LANGDON STW STORM LANGDON PEMBS | BG0012002 |  | SW | South West | Cresswell - headwaters to conf with Waddock Lak |  |  | 2036.25 | 163 | 163 | 73.0223 |  |  |  | Data unreliable from 01/01 to 17/02/21 and from 04/03 to 22/04/2021. Due to static telemetry signal. Instrumentation task escalated through business as usual for instrumentation defect.
51679 | LLANDDEWI VELFREY STW NARBERTH PEMB | BG0013202 |  | SW | South West | Longford Brook - HW to conf with E. Cleddau |  |  | 1099.5 | 62 | 62 | 99.93
50575 | CLARBESTON STW HAVERFORDWEST PEMBS | BG0014502 |  | SW | South West | Cartlett Brook - HW to conf with W. Cleddau |  |  | 1178.75 | 193 | 152 | 100
52650 | CLARBESTON ROAD PS | BG0014503 |  | SW | South West | Deepford Brook - headwaters to conf with Syfynw |  |  | 3011.5 | 150 | 150 | 99.99
50636 | HERBRANDSTON WWTW HERBRANDSTON | BG0016702 |  | SW | South West | Estuarial waters East of Sandy Haven |  | Sandy Haven | 0 | 0 | 0 | 100
50778 | SPITTAL WWTW SPITTAL PEMBS | BG0016902 |  | SW | South West | Rudbaxton Water - HW to conf with W. Cleddau |  |  | 2709.75 | 323 | 269 | 100
50754 | PUNCHESTON WORKS INLET . . | BG0017602 |  | SW | South West | Anghof - headwaters to conf with Western Cleddau |  |  | 2784.75 | 175 | 169 | 99.74
50583 | CROESGOCH WORKS INLET . . | BG0019002 |  | SW | South West | Unnamed - headwaters to tidal limit, Porthgain |  |  | 0 | 0 | 0 | 100
73036 | DINAS (2) SEW'GE SCH EO DINAS CROSS | BG0021902 |  | SW | South West | Clun - HW to tidal limit, Aberbach, Dinas Cross |  |  | 1346 | 90 | 88 | 96.01
51689 | ST NICHOLAS STW . . | BG0022202 |  | SW | South West | Unnamed - HW to tidal limit, Aberbach, nr Aberm |  |  | 6662 | 366 | 364 | 99.89
50702 | MARLOES WORKS INLET . . | BG0022702 |  | SW | South West | Winterton Marsh - HW to TL, Nr Pickleridge Lago |  |  | 381.5 | 29 | 29 | 100
50582 | CRIBYN STW | BG0027002 |  | SW | South West | Grannell - headwaters to confluence with Teifi |  |  | 1599.5 | 219 | 219 | 99.88
70729 | LLWYNCELYN STW | BG0027302 |  | SW | South West | Drywi - headwaters to tidal limit |  |  | 10.5 | 3 | 3 | 100
53022 | MILFORD HAVEN STW | BG0033102 |  | South West |  | Huberston Pill - headwaters to tidal limit |  |  | 279.25 | 23 | 23 | 75.7 |  |  |  | Communications issue, resolved in March 2021.
53022 | MILFORD HAVEN STW | BG0033103 |  | South West |  | Huberston Pill - headwaters to tidal limit |  |  | 132.75 | 40 | 40 | 75.7 |  |  |  | EDM installed in March 2021
70780 | CASTLEMORRIS WASTEWATER TREATMENT | BG0034602 |  | SW | South West | W. Cleddau - headwaters to conf with Cleddau No |  |  | 243.75 | 58 | 42 | 100
50693 | LLANYCHAER STW . . | BG0036802 |  | SW | South West | Gwaun - headwaters to tidal limit |  |  | 1884.25 | 106 | 106 | 99.94
70847 | LLANGADOG STW | BG0040002 |  | SW | South West | Bran - confluence with Ydw to confluence with T |  |  | 2357.75 | 166 | 163 | 99.99
50580 | COSHESTON STW . . | BG0046402 |  | SW | West | Cosheston Pill | Cleddau |  | 2922 | 251 | 223 | 94.33
51691 | TREVINE STW . . | BH0052402 |  | SW | South West | Unnamed - HW to tidal limit, Aberfelin, Trefin |  |  | 1462.25 | 209 | 209 | 100
72067 | CRAIGWEN PS TENBY ROAD ST CLEARS | BH0053403 |  | SW | South West | Taf - headwaters to confluence with Cynin |  |  | 724.5 | 65 | 64 | 100
50846 | BRICKYARD LANE PS BRICKYARD LANE C | BH0053404 |  | SW | South West | Tawelon - headwaters to tidal limit |  |  | 1167 | 109 | 109 | 99.98
52904 | OLD PRIORY ROW CSO PARC HINDS PS C | BH0053405 |  | SW | West | Tawelan Brook |  |  | 297.25 | 193 | 193 | 99.9
51989 | MORFA LN SWO DRAINA | BH0053406 |  | SW | West | Tawelon - headwaters to tidal limit |  |  | 667 | 150 | 150 | 99.8
51126 | SSO POTHOUSE WHARF P.S. | BH0053407 |  | SW | South West | Tawelon - headwaters to tidal limit |  |  | 238.25 | 66 | 62 | 100
51991 | CASTLE HILL DRAINAGE AREA | BH0053408 |  | SW | West | Tywi - Bishop's Pond to conf with Gwili and TL |  |  | 137 | 80 | 58 | 99.63
73098 | CARMARTHEN - STATION ROAD PUMP | BH0053409 |  | SW | West | Tawelan Brook |  |  | 64 | 82 | 82 | 92.25
50789 | TAVERNSPITE STW | BH0056202 |  | SW | South West | Taf - headwaters to confluence with Cynin |  |  | 2301 | 132 | 130 | 100
51108 | PENYCWM PS | BH0057004 |  | SW | South West | Trib of Cwm Mawr stream |  | Newgale | 28.25 | 7 | 6 | 99.84
51658 | TREGARON WWTW TREGARON CEREDIGION | BH0057901 |  | SW | South West | Teifi - Camddwr conf to Nant Wern-macwydd conf |  |  | 2520 | 137 | 137 | 99.97
51656 | TREGARON PS HIGH ST TREGARON CEREDI | BH0058001 |  | SW | South West | Teifi - Camddwr conf to Nant Wern-macwydd conf |  |  | 640.75 | 112 | 112 | 100
51419 | LAUGHARNE SEWERAGE SYSTEM | BH0060003 |  | SW | West | River Coran | Taf |  | 21.25 | 31 | 31 | 99.24
51419 | LAUGHARNE SEWERAGE SYSTEM | BH0060004 |  | SW | West | River Coran | Taf |  | 21.25 | 31 | 31 | 99.24
50914 | Llysnewydd SPS | BH0060501 |  | SW | South West | Bargod - headwaters to confluence with Teifi |  |  | 1955.75 | 117 | 117 | 100
51142 | RHYDFACH PS | BH0060502 |  | SW | South West | Teifi - conf with Nant Wern-Macwydd to tidal limit |  |  | 181.25 | 11 | 11 | 72.07 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
71310 | PENPARC CSO PENPARC CARDIGAN CEREDN | BH0065101 |  | SW | West | Mwidan - headwaters to confluence with Teifi |  |  | 0 | 0 | 0 | 99.45
52005 | PENPARCAU S.S. SSO , , | BH0069401 |  | SW | West | Afon Rheidol |  | Aberystwyth S | 2.5 | 5 | 5 | 99.54 | BW | 5 in Bathing Season
52007 | CSO 7 UNION HILL HAVERFORDWEST | BH0069801 |  | SW | West | MILFORD HAVEN INNER |  |  | 94.25 | 73 | 59 | 100
52014 | NORTHGATE/FRED REES CSO HVRFORDWEST | BH0070601 |  | SW | West | W. Cleddau - Anghof conf to Cartlett Brook conf |  |  | 56 | 32 | 32 | 100
50654 | LETTERSTON WEST WORKS . . | BH0071102 |  | SW | South West | W. Cleddau - Cleddau N conf to Stonehall stm. C |  |  | 1331 | 152 | 139 | 99.24
50804 | VERWIG STW VERWIG NR CARDIGAN DYFED | BH0073802 |  | SW | South West | Mwidan - headwaters to confluence with Teifi |  |  | 2526.25 | 117 | 117 | 100
51028 | WATERSTON WORKS INLET . . | BH0073902 |  | SW | South West | Castle Pill - headwaters to tidal limit |  |  | 819 | 283 | 202 | 100
51725 | PS 1 NR PRIORY C'DIGAN SWO | BH0074203 |  | SW | West | Mwidan - headwaters to confluence with Teifi |  |  | 145.25 | 54 | 44 | 94.94
52022 | SSO GLOCESTER RW OFLOW | BH0074301 |  | SW | South West | Mwidan - headwaters to confluence with Teifi |  |  | 20 | 8 | 8 | 97.18
71356 | PS NO.2 GLOUCESTER RW CARDIG | BH0074303 |  | South West |  | TEIFI |  |  | 416.75 | 91 | 91 | 94.41
71733 | CARDIGAN BRIDGE PS CARDIGAN CERE'N | BH0074403 |  | SW | South West | TEIFI |  |  | 137.25 | 19 | 19 | 100
50863 | CARDIGAN PS NO4 CARDIGAN CEREDIGION | BH0074501 |  | SW | West | TEIFI |  | Poppit West | 8.25 | 3 | 3 | 38.99 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
52016 | CARDIGAN PUMPING STATION NO 5 | BH0074503 |  | SW | South West | Piliau - headwaters to confluence with Teifi |  | Poppit West | 73 | 9 | 9 | 99.86 | BW | 5 in Bathing Season
51168 | ST.DOGMAELS JEWSONS CSO MAIN CSO EO | BH0074507 |  | SW | South West | Unnamed - HW to TL, Teifi estuary, St Dogmaels S. |  | Poppit West | 139 | 15 | 15 | 100
71503 | ST DOGMAELS SSO 2A CSO CARDIGAN | BH0074508 |  | SW | West | TEIFI |  | Poppit West | 565.25 | 45 | 35 | 98.97
70788 | ST DOGMAELS NO4 CSO CARDIGAN | BH0074511 |  | SW | West | TEIFI |  |  | 0.5 | 2 | 0 | 93.59
51062 | MYDDFAI VILLAGE SEWERAGE SCHEME | BH0074901 |  | SW | South West | Bran - headwaters to confluence with Ydw |  |  | 370.5 | 172 | 157 | 99.99
51747 | PENDINE STW . . | BJ0084202 |  | SW | West |  |  | Pendine | 3264.75 | 161 | 161 | 43.85 |  |  |  | Further work needed on discharge mechanism, revisit planned for 2022.
50706 | MERLINS BRIDGE STW/INLET SPS | BJ0087402 |  | SW | South West | Merlin's Brook - headwaters to conf with h Cled |  |  | 847.25 | 115 | 113 | 99.59
51034 | LLANYBYDDER TPS LAMPETER CEREDIGION | BJ0091402 |  | SW | South West | Teifi - Camddwr conf to Nant Wern-macwydd conf |  |  | 1155 | 79 | 78 | 99.97
70928 | TREVAUGHAN SWO | BJ0096401 |  | SW | West | Tawelan Brook |  |  | 0.5 | 2 | 2 | 99.73
51014 | PENCOED FARM SPS LLANGAIN NO 1 CARM | BK0114501 |  | SW | South West | Nant Pwntan - headwaters to tidal limit |  |  | 482 | 49 | 49 | 100
50809 | WHITLAND WWTW WHITLAND CARMS | BL0138501 |  | SW | South West | Taf - headwaters to confluence with Cynin |  |  | 1755.5 | 106 | 105 | 99.97
52168 | CSO NO 102 100M D/S FOOTBRIDGE | BM0003201 |  | SW | Swansea | Afon Afan |  | Aberafan | 92 | 44 | 44 | 99.35
52045 | CSO 101 THE WAUN 200M U/S FOOTBRIDE | BM0003204 |  | SW | Swansea | Afon Afan |  | Aberafan | 191 | 64 | 64 | 99.34
50921 | EWENNI NO2 PUMPING STATION CORTOWN | BM0004402 |  | SW | Central | Ewenny - conf with Ewenny Fach to conf with Alun |  |  | 3693 | 169 | 169 | 99.59
50638 | HOOK STW | BN0000402 |  | SW | South West | Sprinkle Pill - HW to TL, Cleddau Es | Cleddau |  | 287 | 44 | 44 | 93.03
52050 | CWRTNEWYDD SPS DOLWENFACH CERED'N | BN0005603 |  | SW | South West | Cledlyn - headwaters to confluence with Teifi |  |  | 504.25 | 37 | 34 | 99.99
72334 | LLANBYTHER (MANHOLE 7 )EMERGEN | BN0012401 |  | SW | West | Gwendraeth Fawr - Afan Goch to tidal limit |  |  | 473.25 | 32 | 32 | 99.95
50735 | PENNANT STW . . | BN0015602 |  | SW | South West | Arth - headwaters to tidal limit |  |  | 4074.5 | 316 | 250 | 100
50757 | RED ROSES STW | BN0072502 |  | South West |  | New Inn Stream - headwaters to tidal limit |  |  | 973.75 | 86 | 86 | 99.97
50665 | Llanfynydd STW overflow | BN0077601 |  | SW | South West | Sannan - headwaters to confluence with Dulas |  |  | 2527.75 | 201 | 187 | 99.9
70827 | PEMBROKE RIVER PS CATSHOLE QUARRIES | BN0084703 |  | SW | South West | MILFORD HAVEN INNER |  |  | 0 | 0 | 0 | 99.99
51225 | LLANRHYSTUD WWTW CEREDIGION | BN0160302 |  | SW | South West | Afon Wyre |  | Llanrhysted | 53.75 | 23 | 14 | 100
50790 | Templeton WwTW Storm | BN0166702 |  | SW | South West | Right bank of Ford's Lake |  | Wisemans Bridge | 1120.75 | 140 | 120 | 99.91
51734 | CLARACH STW . . | BN0168802 |  | SW | South West | Gorlech - headwaters to confluence with Cothi |  |  | 0 | 0 | 0 | 99.99
50612 | FERRYSIDE STW FERRYSIDE CARMS | BN0169301 |  | SW | Central | Ferryside Stream | Tywi |  | 311.5 | 45 | 41 | 91.5 | BW | 5 in Bathing Season
50613 | FFAIRFACH WWTW FFAIRFACH CARMS | BN0194103 |  | SW | South West | Tywi (Llandovery Bran to Cothi confl) |  |  | 1954.75 | 146 | 146 | 99.74
51718 | SAWMILLS Y'D CSO LLANDEILO CARMARTH | BN0194104 |  | SW | West | Cennen - headwaters to confluence with Tywi |  |  | 0 | 0 | 0 | 99.62
50659 | LLANDOVERY WASTEWATER TREATMENT | BN0202702 |  | SW | South West |  |  |  | 3641.5 | 213 | 211 | 100
51017 | EMERGENCY DISCHARGE FROM LLANGWM SPS | BN0266801 |  | SW | West | Llangwm Pill | Cleddau |  | 982 | 53 | 53 | 91.04
50541 | BANCYFELIN STW BANCYFELIN NEAR ST | BN0269702 |  | SW | South West | Cywyn - conf with Nant Coedcae to tidal limit |  |  | 0 | 0 | 0 | 100
50880 | COLBREN PS 1 EMERG , , | BO5088001 |  | SW | Central | Nant Llech - headwaters to confluence with Tawe |  |  | 530 | 83 | 72 | 99.97
50923 | CSO27 FARMERS ROAD PUMPING STATION | BO5092301 |  | SW | Central | Clydach - headwaters to conf with River Neath |  |  | 203.25 | 46 | 46 | 100
50958 | GROVESEND PS , , | BO5095801 |  | SW | Central | Nant y Garreg - headwaters to tidal limit |  |  | 163.75 | 44 | 44 | 99.59
50989 | LALESTON SPS LALESTON BRIDGEND | BO5098901 |  | SW | Central | Ogmore - confluence with Llynfi to tid |  |  | 17.75 | 9 | 8 | 100
50997 | LINKS PEMBREY PS EMERG , , | BO5099701 |  | SW | Central | Swan Pool Drain | Burry N |  | 15.5 | 4 | 4 | 100
51024 | LLANRHIDIAN PS EMERG , , | BO5102401 |  | SW | Swansea | Estuary | Burry S |  | 160.5 | 92 | 48 | 99.13
51040 | LLWYNUHILWG PS EMERG , , | BO5104001 |  | SW | Central | Trib of River Dafen | Burry N |  | 100.75 | 9 | 9 | 100
72084 | NEW PENCLAWDD SEWAGE PS PENCLAWDD | BO5109601 |  | SW | Swansea | Burry Estuary | Burry S |  | 314.75 | 31 | 30 | 99.39 | SFW | 26 in the Year | Yes
51115 | PONTARDULAIS PS EMERG , , | BO5111601 |  | SW | Central | Dulais - headwaters to confluence with Loughor |  |  | 229.5 | 24 | 23 | 99.98
51638 | RHYDLEWIS STW | BP0013502 |  | SW | South West | Nant Coll |  |  | 824.75 | 50 | 48 | 100
51639 | RHYDLEWIS PS NO 1 | BP0013503 |  | SW | South West | Ceri - headwaters to confluence with Teifi |  |  | 56 | 13 | 13 | 100
52090 | LLANFARIAN WWTW LLANFARIAN CERED'N | BP0015202 |  | SW | South West | Ystwyth - conf with Cwmnewydion to tidal limit |  | Aberystwyth South | 165.75 | 20 | 20 | 98.79
50663 | LLANFARIAN WWTW LLANFARIAN CERED'N | BP0015203 |  | SW | South West | Ystwyth - conf with Cwmnewydion to tidal limit |  | Aberystwyth South | 367.25 | 41 | 40 | 98.79
50663 | LLANFARIAN WWTW LLANFARIAN CERED'N | BP0015204 |  | SW | South West | Ystwyth - conf with Cwmnewydion to tidal limit |  | Aberystwyth South | 1470.75 | 142 | 130 | 98.79
71334 | LLANDEILO (TEMPORARY STORM WATER OV | BP0018401 |  | SW | West | Cennen - headwaters to confluence with Tywi |  |  | 278.25 | 100 | 100 | 99.39
51646 | ABERGREGAN PUMPING STATION AFAN | BP0028601 |  | SW | Central | Afan - conf with Corrwg to confluence |  |  | 1589.25 | 84 | 83 | 100
52157 | BLAENGWNFI STORMWATER OVERFLOW CHAM | BP0028604 |  | SW | Swansea | Afan - headwaters to confluence with C |  |  | 0 | 0 | 0 | 99.91
71264 | CSO 107 BELOW ALDER TERRACE AFAN | BP0028605 |  | SW | Swansea | Afan - headwaters to confluence with C |  |  | 101.5 | 56 | 40 | 99.43
52104 | CSO 108 REAR 16 MARGAM ST CYMMER | BP0028607 |  | SW | Swansea | Afan - conf with Corrwg to confluence |  |  | - | - | - | 0 |  |  |  | Data unreliable from 01/01/2021 to 31/12/2021. Due to static telemetry signal. New cello installed at the end of 2021, data avilable from January 2021.
52105 | DUFFRYN STORMWATER OVERFLOW CHAMBER | BP0028608 |  | SW | Swansea | Afan - conf with Corrwg to confluence |  |  | 3 | 6 | 2 | 85.51 |  |  |  | Communications issue, resolved in April 2021.
51806 | AMROTH AND SUMMERHILL SCHEME PS | BP0034002 |  | SW | South West | COLBY STREAM |  | Wisemans Bridge | 3.25 | 3 | 3 | 100
51805 | AMROTH AND SUMMERHILL SCHEME PS 2 | BP0034003 |  | SW | South West | Trelissey |  | Amroth | 142 | 23 | 21 | 99.97
72131 | SWO.HEATHFIELD AVENUE GLYNNEAT | BP0038901 |  | SW | Swansea | Neath - conf with Nedd Fechan and Mellte to TL |  |  | 582.75 | 170 | 170 | 96.3
50588 | Crymych SWK | BP0044402 | [6 empty] | 469.25 | 73 | 73 | 100
51714 | LLANBOIDY STW | BP0044502 |  | SW | South West | Gronw - headwaters to confluence with Taf |  |  | 100.75 | 17 | 16 | 100
50647 | LAMPETER STW LAMPETER | BP0045002 |  | SW | South West | Teifi - Camddwr conf to Nant Wern-macwydd conf |  |  | 758.75 | 77 | 77 | 99.95
52163 | CSO 122 18 DUKE STREET AFAN | BP0046201 |  | SW | Swansea | Croeserw Brook | Swans E |  | - | - | - | 0 | BW | 5 in Bathing Season |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
51809 | CSO 123 MARGAM PS NR BROMBILL ST | BP0046202 |  | SW | Central | Arnallt Brook | Swans E |  | 0 | 0 | 0 | 99.91
50620 | FRESHWATER OUTFALL PUMPING STATION | BP0060302 |  | SW | South West | Land Adjacent To Freshwater East Stream |  | Freshwater E | 0 | 0 | 0 | 100
71886 | ROCK STREET PS NEW QUAY | BP0061001 |  | SW | South West | New Quay Bay |  | New Quay North | 25.25 | 4 | 4 | 100 | BW | 5 in Bathing Season
52117 | WELLINGTON ST.SWO.ABERA AB | BP0061201 |  | SW | West | Aeron - confluence with Gwili to tidal |  |  | 162 | 41 | 33 | 99.05
52118 | WATER ST.SWO.ABERAERON ABERAE | BP0061301 |  | SW | West | Aberystwyth Harbour |  |  | 145.75 | 37 | 23 | 99.18
52121 | CSO PONT ABERYSTWYTH ABERYSTWYTH | BP0061601 |  | SW | West | River Rheidol |  | Aberystwyth S | 14.75 | 12 | 9 | 100
50779 | ST DAVID'S WWTW ST DAVID'S PEMBS | BP0062702 |  | SW | South West | Coastal Waters at Porth Clais |  | Caerfai | 1573.75 | 97 | 94 | 100
50603 | DINAS STW . . | BP0063202 |  | SW | South West | Cardigan Bay South |  |  | 1256.75 | 64 | 64 | 99.94
53048 | CRANE SPS FISHGUARD HARBOUR FISHGU | BP0063401 |  | SW | South West | Cardigan Bay South |  |  | 0 | 0 | 0 | 100
81437 | THE LLANDARCY 36" OUTFALL, PEN-YR-HEOL, NEATH | BP0064319 |  | SW | West | Clydach - headwaters to conf with River Neath |  |  | 33 | 16 | 16 | 99.71
51851 | IRONGATE PS PORTCAWL BRIDGEND | BP0064401 |  | SW | Central | Bristol Channel | Porthcawl |  | 372 | 20 | 20 | 100 | BW & SFW | 5 in Bathing Season OR 14 in the Year | YES
51810 | BEACH ROAD PUMPING STATION NEWTON | BP0064403 |  | SW | Central | Bristol Channel | Porthcawl |  | 9.75 | 8 | 8 | 100 | BW & SFW | 5 in Bathing Season OR 14 in the Year
52134 | M.HAVEN/CASTLE PILL SWO PEMBS | BP0065501 |  | SW | West | Castle Pill |  |  | 0 | 0 | 0 | 9.7 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
52135 | MILFORD HAVEN SWO | BP0065601 |  | SW | West | Huberston Pill - headwaters to tidal limit |  |  | 125.75 | 68 | 68 | 99.48
52136 | M'FORD HAVEN RATH SWO MILFORD HAVEN | BP0065701 |  | SW | West | Castle Pill - headwaters to tidal limit |  |  | 182.5 | 82 | 82 | 100
71349 | CSO AT 3/4 ST NICHOLAS CRES PBROKE | BP0065801 |  | SW | West | Pembroke - headwaters to tidal limit |  |  | 9.25 | 14 | 8 | 87.63 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
51770 | PENNAR(W).SWO.PEMB.DOCK | BP0066001 |  | SW | West | Cocheston Pill - headwaters to tidal limit |  |  | 8.75 | 13 | 13 | 99.93
51771 | LWR PENNAR(E).SWO.PEMBR PEMB | BP0066101 |  | SW | West | MILFORD HAVEN INNER |  |  | 193 | 34 | 25 | 98.86
51177 | TAN Y CAE PUMPING STATION ABERYSTY | BP0067601 |  | SW | South West | River Rheidol |  | Aberystwyth S | 7.75 | 13 | 13 | 100 | BW | 5 in Bathing Season | YES
51177 | TAN Y CAE PUMPING STAION ABERYSTWYT | BP0067701 |  | SW | South West | River Rheidol |  | Aberystwyth S | 229 | 16 | 16 | 90.63 | BW | 5 in Bathing Season
50818 | ABERGWILI PS NEAR RUGBY FIELD | BP0072101 |  | SW | South West | Gwili - Duad conf to conf with Tywi at spring |  |  | 312 | 77 | 77 | 99.73
50644 | Keeston Works Inlet CSO | BP0087902 |  | South West |  | Camrose Brook - headwaters to conf with W. Cleddau |  |  | 1076.5 | 116 | 116 | 99.98
51583 | CENARTH WWTTW CENARTH CEREDIGION | BP0101203 |  | SW | South West | Teifi - conf with Nant Wern-Macwydd to |  |  | 332.75 | 39 | 37 | 97.75
52772 | TRESAITH . . | BP0110301 |  | SW | South West | Sea |  | Tresaith | 0 | 0 | 0 | 99.99
51660 | FELINDRE FARCHOG P.S. . . | BP0110501 |  | SW | South West | Nyfer - Confluence with Nant Duad to tidal limi |  |  | 990 | 55 | 54 | 100
51000 | LLANBADARN PUMPING STATION | BP0110701 |  | SW | South West | Plas Crug Ditch |  | Aberystwyth S | 36.5 | 5 | 5 | 99.99 | BW | 5 in Bathing Season
51685 | LLANFYRNACH SEWAGE PUMPING STATION | BP0110801 |  | SW | South West | Taf - headwaters to confluence with Cynin |  |  | 1047.5 | 65 | 64 | 96.9
71227 | LLANGRANOG WWTW LLANGRANOG | BP0110901 |  | SW | South West | Cardigan Bay |  | Llangrannog | 0 | 0 | 0 | 100
50847 | BROADHAVEN NORTH PUMPING STATION | BP0111201 |  | SW | West | Swanswell Brook |  | Broadhaven | 10.75 | 11 | 8 | 99.28
51418 | NEYLAND P.S. . . | BP0111601 |  | SW | South West | Milford Haven | Cleddau |  | 82.5 | 21 | 21 | 100 | BW | 5 in Bathing Season
51159 | SOLVA P.S. . . | BP0111701 |  | SW | South West | Solva - headwaters to tidal limit |  |  | 667.75 | 41 | 37 | 99.98
51211 | WOLFSCASTLE P.S. . . | BP0111801 |  | SW | South West | Anghof - headwaters to conf with Western Cledda |  |  | 418.5 | 38 | 38 | 99.97
50828 | ANGLE VILLAGE PS . . | BP0111901 |  | SW | West | Milford Haven |  | West Angle | 1589.75 | 105 | 101 | 95.01
51702 | IRON DUKE CLYNDERWEN SPS | BP0112001 |  | SW | South West | Longford Brook - HW to conf with E. Cleddau |  |  | 887.75 | 47 | 47 | 100
51048 | LYDSTEP PS . . | BP0112101 |  | SW | South West | Un-named Stream |  | Lydstep | 57 | 13 | 12 | 99.94
51094 | PENALLY SEWAGE PUMPING STATION | BP0112201 |  | SW | South West | Un-named watercourse |  | Tenby S | 19 | 9 | 8 | 100
51152 | BROOKLANDS PLACE PS (NO 3) SAUDERSF | BP0112301 |  | SW | South West | Saundersfoot Stream |  | Wisemans Bridge | 3.25 | 1 | 1 | 99.99
51151 | MILFORD ST P S'S (1 & 1A) SAUNDERSF | BP0112401 |  | SW | South West | Saundersfoot Stream |  | Wisemans Bridge | 0.25 | 1 | 1 | 100
52758 | MILFORD STREET PUMPING STATION (NO. 1 & 1A) COMMON OVERFLOW | BP0112402 |  | South West |  | Carmarthen Bay |  |  | 1.25 | 1 | 1 | 99.45
51179 | THE GLEN SAUNDERSFOOT PS | BP0112501 |  | SW | South West | Stream above Beach |  | Wisemans Bridge | 0 | 0 | 0 | 100 | BW | 5 in Bathing Season
51200 | VALLEY RD P S'S (4 & 4A) COMMON OVERFLOW SAUNDERSFOOT, DYFED | BP0112601 |  | SW | South West | Saundersfoot Stream |  | Saundersfoot | 1 | 1 | 1 | 99.84 | BW | 5 in Bathing Season
51200 | VALLEY RD P S'S (4 & 4A) COMMON OVERFLOW SAUNDERSFOOT, DYFED | BP0112602 |  | SW | South West | Saundersfoot Stream |  | Saundersfoot | 1 | 1 | 1 | 99.84 | BW | 5 in Bathing Season
51208 | WHITLAND PS TREVAUGHAN WHITLAND | BP0113001 |  | SW | South West | Taf - headwaters to confluence with Cynin |  |  | 338.75 | 67 | 60 | 100
50927 | FERRYSIDE PS . . | BP0113101 |  | SW | Central | Ferryside Stream | Tywi |  | 163 | 46 | 38 | 99.99 | BW | 5 in Bathing Season
51140 | RHOSMAEN PS , , | BP0113301 |  | South West |  | Tywi (Llandovery Bran to Cothi confl) |  |  | 43.25 | 31 | 31 | 93.39
51721 | ALBION PUMPING STATION CARMS | BP0113501 |  | SW | South West | Bran - confluence with Ydw to confluence with T |  |  | 334 | 96 | 92 | 99.98
51013 | PWNTAN SPS LLANGAIN CARMARTHENSHIRE | BP0113601 |  | SW | South West | Nant Pwntan - headwaters to tidal limit |  |  | 79.5 | 15 | 15 | 99.99
51420 | ABERCYCH PS , , | BP0113701 |  | SW | South West | Teifi - conf with Nant Wern-Macwydd to |  |  | 166.25 | 53 | 46 | 100
50874 | CENARTH PS , , | BP0113801 |  | SW | South West | Teifi - conf with Nant Wern-Macwydd to tidal limit |  |  | 252.5 | 25 | 24 | 100
50906 | CILGERRAN FLYGHT PS . . | BP0114501 |  | SW | South West | Teifi - conf with Nant Wern-Macwydd to tidal limit |  |  | 11.5 | 16 | 11 | 88.43 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
51422 | PEN Y BRYN PS . . | BP0114601 |  | SW | South West | Piliau - headwaters to confluence with Teifi |  |  | 626.75 | 76 | 76 | 99.97
51022 | LLANILAR PS . . | BP0114701 |  | SW | South West | Ystwyth - conf with Cwmnewydion to tidal limit |  |  | 64 | 11 | 10 | 99.96
51107 | PENTRELLYN PS . . | BP0114801 |  | SW | South West | Ystwyth - conf with Cwmnewydion to tidal limit |  |  | 16 | 5 | 3 | 99.97
51743 | LLECHRYD MAIN . . | BP0115001 |  | SW | South West | Arberth - headwaters to confluence with Teifi |  |  | 288.25 | 22 | 22 | 99.96
70731 | PONTRHYDFENDIGAID PS . . | BP0115101 |  | SW | South West | Teifi - headwaters to confluence with Meurig |  |  | 631.5 | 120 | 120 | 100
72039 | PRIMARY SCHOOL CSO FFAIRFACH CERE | BP0115401 |  | SW | West | Cennen - headwaters to confluence with Tywi |  |  | 218.75 | 50 | 50 | 100
51759 | LLANGADOG . . | BP0115501 |  | SW | West | Sawdde - conf with Clydach to confluence with T |  |  | 6.25 | 20 | 5 | 94.1
51761 | LLANDEILO . . | BP0115701 |  | South West |  | Tywi (Llandovery Bran to Cothi confl) |  |  | 267 | 93 | 93 | 98.3
51762 | LLANSAWEL . . | BP0115801 |  | SW | West | Marlais - headwaters to confluence with Melindd |  |  | 22.25 | 3 | 3 | 96.72
51764 | LLANDOVERY No 1 SPS | BP0116001 |  | SW | South West | Gwydderig - conf with Bran to confluence with T |  |  | 305.5 | 106 | 106 | 100
51766 | WATER ST P'BROKE DK SWO | BP0116201 |  | SW | West | MILFORD HAVEN INNER | Cleddau |  | 23.25 | 26 | 26 | 99.33
53130 | TENBY LIFEBOAT CSO CASTLE SQ TENBY | BP0116901 |  | SW | South West | Coastal Waters |  | Tenby S | 2 | 3 | 3 | 100
52581 | CSO WOODBINE CLOSE PEMBROKE | BP0117301 |  | SW | West | Pembroke - headwaters to tidal limit |  |  | 1 | 4 | 0 | 99.72
51779 | HOLYLAND ROAD CSO TWOPENNY HAY CLSE | BP0117501 |  | SW | West | Pembroke - headwaters to tidal limit |  |  | 399.75 | 32 | 31 | 98.45
72333 | NARBERTH BRIDGE SWO NARBERTH PEMBS | BP0117701 |  | SW | West | Narbeth Brook - headwaters to conf with E. Cled |  |  | 220 | 67 | 67 | 100
52657 | DYFFRYN CELLWEN | BP0135001 |  | SW | Central | Pyrddin - headwaters to conf with Nedd Fechan |  |  | 1130.25 | 104 | 104 | 99.99
53068 | SLADE PS SLADE WAY FISHGUARD | BP0151701 |  | SW | South West | GWAUN |  |  | 850.25 | 73 | 73 | 100
51417 | FISHGUARD LOWER TOWN PS | BP0151801 |  | SW | South West | Gwaun - headwaters to tidal limit |  |  | 171.75 | 63 | 59 | 100
50821 | ABERPORTH P.S. SSO NO.1 | BP0167301 |  | SW | South West | Nant Howni |  | Aberporth | 1 | 1 | 1 | 99.99 | BW | 5 in Bathing Season
50822 | ABERPORTH P.S. SSO | BP0167401 |  | SW | South West | Nant Gilddu |  | Aberporth | 0.25 | 1 | 0 | 100 | BW | 5 in Bathing Season
52818 | CAPEL IWAN STW | BP0167801 |  | SW | South West | Cych - headwaters to confluence with Cneifa |  |  | 763 | 47 | 47 | 100
51054 | MARLAS STORM TANKS N CORNELLY BRIDG | BP0169901 |  | SW | Central | Kenfig - headwaters to conf with Nant Cwm Philip |  | Rest Bay Porthcawl | 181 | 22 | 22 | 100
52907 | SHOWFIELD DITCH CSO | BP0208001 |  | SW | West | Creuddyn - headwaters to confluence with Teifi |  |  | 33 | 32 | 32 | 100
52890 | PIT ST ST. DAVIDS SWO | BP0208101 |  | SW | West | River Alun |  | Whitesand | 36.5 | 36 | 17 | 96.24
52889 | PEBBLES ST. DAVIDS SWO | BP0208201 |  | SW | West | River Alun |  | Caerfai | - | - | - | 0 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
52888 | VIC'GE RD ST.DAVIDS.SWO | BP0208301 |  | SW | West | River Alun |  | Whitesand | 46 | 28 | 15 | 99.44
52886 | THE PARROG NEWPORT SWO | BP0208401 |  | SW | West | An unnamed Ditch |  | Newport N | - | - | - | 0 | BW | 5 in Bathing Season |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
52891 | PROMENADE NEYLAND SWO | BP0208601 |  | SW | West | Milford Haven | Cleddau |  | 29.5 | 33 | 16 | 99.75 | BW | 5 in Bathing Season
73367 | BEGELLY CS0 BEGELLY KILGETTY | BP0208701 |  | SW | South West | Cresswell - headwaters to conf with Waddock Lak |  |  | 82 | 17 | 17 | 100
51767 | (B)MEYRICK ST SWO PEMBROKE DO | BP0209401 |  | SW | West | Milford Haven | Cleddau |  | 333.25 | 37 | 37 | 99.12
72426 | M'TON BRDGE P'BROKE SWO | BP0209501 |  | SW | West | Pembroke - headwaters to tidal limit |  |  | 0 | 0 | 0 | 93.42
70852 | WOGAN MEWS CSO LAUGHARNE CARMS | BP0209601 |  | SW | West | Culverted section of mackerel lake stream | Taf |  | 127.25 | 60 | 60 | 98.26 | BW | 5 in Bathing Season | YES
52905 | JEWSONS CSO TANERDY CARMARTHEN | BP0209801 |  | SW | West | Tywi - Bishop's Pond to conf with Gwili and TL |  |  | 166.25 | 35 | 35 | 100
71329 | JOHNSTOWN C'MARTHEN SWO | BP0209901 |  | SW | West | Tawelan Brook |  |  | 260.75 | 83 | 83 | 98.22
70285 | HERMON STW STORM OVERFLOW HERMON | BP0210101 |  | SW | South West | Taf - headwaters to confluence with Cynin |  |  | 2522.75 | 175 | 165 | 100
72398 | PT 28 BRYNMOR\WESTBURY , , | BP0212501 |  | SW | Swansea | Sea | Swans W | Swansea | 0.25 | 1 | 0 | 99.7
70938 | CSO NO 21 DERWEN FAWR ROAD SKETTY S | BP0212801 |  | SW | Swansea | Un-named Tributary of the River Clyne | Swans W | Swansea Bay | 116.5 | 29 | 24 | 99.44 | BW | 5 in Bathing Season
71422 | CSO NO 33 GLAN YR AFON ROAD SKETTY | BP0212901 |  | SW | Swansea | Un-named Tributary of the River Clyne | Swans W | Swansea Bay | 50.25 | 13 | 12 | 100
51866 | CAREW WWTW CAREW PEMBROKESHIRE | BP0215001 |  | SW | South West | Carew - HW to conf with Carew Tidal Mill Pond |  |  | 2966.5 | 179 | 172 | 99.98
50785 | STACKPOLE STW STACKPOLE (Settled Storm Sewage) | BP0217702 |  | SW | South West | Coastal Waters near Stackpole Quay |  | Barafundle | 391 | 37 | 37 | 100
51730 | CILGERRAN STW | BP0217802 |  | SW | South West | Teifi - conf with Nant Wern-Macwydd to |  |  | 1514.25 | 119 | 114 | 99.99
51025 | LLANSADWRN PS | BP0218201 |  | SW | South West | Tywi (Llandovery Bran to Cothi confl) |  |  | 978.5 | 62 | 61 | 100
70223 | TREOES PUMPING STATION BRIDGEND | BP0218301 |  | SW | Swansea | Ewenny - conf with Ewenny Fach to conf |  |  | 472 | 31 | 29 | 95.85
70737 | CROSS INN / NEBO STW , , | BP0218501 |  | SW | South West | Cledan - headwaters to tidal limit |  |  | 15 | 4 | 4 | 100
50770 | SALEM STW | BP0219001 |  | SW | South West |  |  |  | 1532.25 | 117 | 117 | 99.98
70147 | LLANFYRNACH STW STORM OVERFLOW | BP0219201 |  | SW | South West | Taf - headwaters to confluence with Cynin |  |  | 4560 | 221 | 221 | 100
52760 | CLYNE SPS CLYNE NEATH NEATH PORT T | BP0219301 |  | SW | Swansea | Neath - conf with Nedd Fechan and Mellte to TL |  |  | 150.75 | 27 | 25 | 88.72 |  |  |  | Communications issue, resolved in February 2021.
50798 | TRELECH STW TRELECH CARMARTHEN , | BP0219401 |  | SW | South West | Cynin - headwaters to tidal limit |  |  | 359.25 | 61 | 53 | 99.93
50722 | NEWCHAPEL STW | BP0219502 |  | SW | South West | Dulas - headwaters to confluence with Cych |  |  | 269.25 | 32 | 23 | 99.47
70283 | NARBERTH WEST STW | BP0219601 |  | SW | South West | Narbeth Brook - headwaters to conf with E. Cled |  |  | 227.5 | 47 | 42 | 99.99
53065 | P.S.FORMER SITE NARBERTH E STW | BP0219701 |  | SW | South West | Marlais - headwaters to confluence with Taf |  |  | 165.75 | 22 | 22 | 98.74
53042 | LLANWNEN PS SITE OF LLANWNEN (LOWER | BP0220601 |  | SW | South West | Grannell - headwaters to confluence with Teifi |  |  | 2 | 3 | 2 | 99.97
70145 | LLANDDAROG WWTW LLANDDAROG CARMARTH | BP0220701 |  | SW | South West | Gwendraeth Fach - headwaters to tidal limit |  |  | 2879.5 | 143 | 143 | 99.42
33761 | LLANGAN PUMPING STATION LLANGAN | BP0223701 |  | SW | Central | Ewenny - conf with Ewenny Fach to conf |  |  | 10.25 | 4 | 3 | 100
71381 | NEYLAND PROMENADE CSO , , | BP0223901 |  | SW | West | Milford Haven Estaury | Cleddau |  | 3 | 4 | 3 | 99.99 | BW | 5 in Bathing Season
52661 | NEATH ABBEY PS SKEWEN NEATH PORT T | BP0224301 |  | SW | Central | Clydach - headwaters to conf with Rive |  |  | 185.75 | 42 | 42 | 100
52792 | ABBEY PS. | BP0224802 |  | SW | Central | Neath - conf with Nedd Fechan and Mellte to TL |  |  | 246.5 | 67 | 67 | 99.95
50761 | REYNOLDSON WWTW REYNOLDSTON GOWER | BP0232001 |  | SW | Central | Burry Pill - headwaters to tidal limit |  |  | 2393.75 | 145 | 145 | 99.98
70804 | OGOF MARTHA PS MARINE WALK PENYRABE | BP0232401 |  | SW | South West | Cardigan Bay South |  |  | 75.5 | 44 | 38 | 100
70676 | HEARTS OF OAK COTTAGES (STORM) MA | BP0234901 |  | SW | West |  |  |  | 0.5 | 2 | 0 | 99.73
71451 | CSO STH OF GREENFIELD TERRACE PONT | BP0235301 |  | SW | Bridgend Hereford & Mid Wales | Llynfi - headwaters to Lletty Brongu S |  |  | 359.25 | 81 | 81 | 57.53 |  |  |  | Data unreliable from 01/01 to 04/06/2021. Due to erratic telemetry signal, resolved.
71345 | ST GEORGE COTTAGES CSO COEDCAE | BP0236001 |  | SW | West | Afon Dafen, via surface water system | Burry N |  | 0 | 0 | 0 | 75.6 | BW | 16 in Bathing Season |  | Communications issue - escalated through business as usual process for communications failures.
53100 | SWANSEA STW FABIAN WAY SWANSEA , | BP0236601 |  | SW | Swansea | Estuarial Waters in Swansea Bay | Swans E |  | 205.75 | 18 | 18 | 28.76 | BW | 5 in Bathing Season |  | Data unreliable from 01/01 to 16/04/2021. Due to static telemetry signal. Instrumentation task escalated through business as usual for instrumentation defect.
53153 | MUMBLES SPS KNAB ROCK MUMBLES SWANS | BP0236603 |  | SW | Central | Estuarial Waters in Swansea Bay | Swans S | Limeslade | 655.75 | 70 | 70 | 100 | BW | 5 in Bathing Season | YES
52124 | OUTFALL A (CSO 201) JUN OF MUMBLES | BP0237401 |  | SW | Swansea | Swansea Bay | Swans W | Limeslade | 0 | 0 | 0 | 99.71 | BW | 5 in Bathing Season
52126 | OUTFALL B (CSO 301) JUN OF MUMBLES | BP0237402 |  | SW | Swansea | Swansea Bay | Swans W | Limeslade | 11.25 | 20 | 20 | 99.08 | BW | 5 in Bathing Season | YES
52902 | OUTFALL D1 (CSO 10) JUN OF MUMBLES | BP0237404 |  | SW | Swansea | Swansea Bay | Swans W | Limeslade | 9 | 20 | 11 | 99.91 | BW | 5 in Bathing Season
52520 | SWO. NEAR NORTON AVENUE (POINT | BP0237405 |  | SW | Swansea | Swansea Bay | Swans W | Limeslade | 102.25 | 66 | 66 | 72.19 | BW | 5 in Bathing Season | YES | Deterioration of 4G network coverage. Alternative solutions are being considered.
52519 | OUTFALL E (CSO 14) JUN OF MUMBLES R | BP0237406 |  | SW | Swansea | The Washinghouse Brook | Swans W |  | 0 | 0 | 0 | 98.84 | BW | 5 in Bathing Season
70977 | OFF LLIPUT LANE POINT 130 CSO SWAN | BP0237407 |  | SW | Swansea | Swansea Bay | Swans W |  | 0 | 0 | 0 | 99.73 | BW | 5 in Bathing Season
52518 | CSO 16, OUTFALL G, ADJACENT TO JUNCTION OF MUMBLES RD & MAYALS ROAD, SWANSEA | BP0237408 |  | SW | Swansea | Swansea Bay |  |  | 0 | 0 | 0 | 46.5 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
52514 | OUTFALL J (CSO 24) JUN OF MUMBLES R | BP0237410 |  | SW | Swansea | Brynmill Stream | Swansea Bay (S),(W),(E) | Swansea Bay | 9.75 | 15 | 15 | 100
52483 | OUTFALL K (CSO 264) JUN OF MUMBLES | BP0237411 |  | SW | Swansea | Swansea Bay | Swans W | Swansea Bay | 0 | 0 | 0 | 98.81 | BW | 5 in Bathing Season
51148 | SWO. NEAR H.M. PRISON (POINT 6 | BP0237412 |  | SW | Central | Estuarial Waters in Swansea Bay | Swansea Bay (S),(W),(E) | Swansea Bay | 46.75 | 18 | 18 | 100 | BW | 5 in Bathing Season
52487 | OUTFALL 'M' THE TAWE BARRAGE SWANS | BP0237413 |  | SW | Swansea | Estuarial Waters in Swansea Bay | Swans W |  | 234.5 | 25 | 25 | 99.99 | BW | 5 in Bathing Season
70994 | SWO. QUEENS DOCK (POINT 95) | BP0237414 |  | SW | Swansea | Estuarial Waters of Swansea Bay | Swans E |  | 3.75 | 6 | 6 | 99.44 | BW | 5 in Bathing Season
51065 | NEW HEDGES PS ROWSTON HOLIDAY PARK | BP0237701 |  | SW | South West | an unnamed stream |  | Tenby N | 0 | 0 | 0 | 99.99
52769 | ABERPORTH STW ABERPORTH , | BP0238001 |  | SW | South West | Aberporth Coastal Waters |  | Aberporth | 483.5 | 46 | 46 | 99.97 | BW | 5 in Bathing Season | YES
70043 | ABERPORTH HEADLAND PS ABERPORTH , | BP0238301 |  | SW | South West | Aberporth Coastal Waters |  | Aberporth | 0 | 0 | 0 | 97.47 | BW | 5 in Bathing Season
70857 | CWM IFOR STW (STORM TANKS) MANORDEI | BP0239802 |  | SW | South West | Tywi (Llandovery Bran to Cothi confl) |  |  | 1515.75 | 95 | 95 | 99.98
71429 | CSO NO 126 MOORS ST CULVERT AFAN | BP0240201 |  | SW | Swansea | Afon Afan | Swans E |  | 25.75 | 14 | 14 | 99.36
71090 | CSO 9 CIMLA COMMON, CIMILA, NEATH | BP0240601 |  | SW | Swansea | Hollins Clough Ditch |  | Aberafan | 0 | 0 | 0 | 93.56
70951 | CSO 60 GORS AVENUE SWANSEA | BP0241601 |  | SW | Swansea | Tawe - conf with Nant Cwmgelli to tida |  |  | 0.75 | 3 | 0 | 93.56
70968 | CSO 119 CWM ROAD HAFOD SWANSEA | BP0242101 |  | SW | Swansea | A Culvert of the Burlais Brook | Swans W |  | 24.5 | 31 | 31 | 100
74683 | CSO 64A PENLANFACH BRYNHYFRYD | BP0242501 | [6 empty] | 0.75 | 1 | 1 | 94.81
71059 | PENLAN CRESENT (POINT 52A) SWANSEA | BP0242701 |  | SW | Swansea | Tawe - conf with Nant Cwmgelli to tida |  |  | 55.25 | 54 | 35 | 97.82
70955 | CSO 69 TRWYDDFA ROAD SWANSEA | BP0242801 |  | SW | Swansea | Tawe - conf with Nant Cwmgelli to tida |  |  | 4.5 | 5 | 5 | 49.22 |  |  |  | Communications issue - access issue
70956 | CSO 69A HEOL NANT GELLI SWANSEA | BP0242901 |  | SW | Swansea | Tawe - conf with Nant Cwmgelli to tida |  |  | 1 | 3 | 3 | 99.73
70231 | WAUNARLWYDD CARAVAN SITE CSO | BP0243001 |  | SW | Swansea | Gors-Fawr Brook |  |  | 30.25 | 16 | 16 | 51.57 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
70228 | SKOMER PLACE CSO BLAEN Y MAES | BP0243201 |  | SW | Swansea | Llan - headwaters to tidal limit |  | Swansea Bay | 47.75 | 15 | 15 | 95.96
70948 | CADLEWOOD ROAD (POINT 48) SWANSEA | BP0243401 |  | SW | Swansea | Llan - headwaters to tidal limit |  |  | 6.5 | 15 | 4 | 77.98 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
72365 | BLAENYMAES DRIVE (POINT 49) SWANSE | BP0243501 |  | SW | Swansea | Llan - headwaters to tidal limit |  |  | 1.25 | 3 | 3 | 99.45
70950 | MYNYDD NEWYDD ROAD (POINT 50) SWAN | BP0243601 |  | SW | Swansea | Llan - headwaters to tidal limit |  |  | 4 | 6 | 6 | 99.97
70957 | CSO 72 SLATE ST MORRISTON SWANSEA | BP0243701 |  | SW | Swansea | Tawe -confluence with Twrch to tidal l |  |  | 0.25 | 1 | 1 | 99.87
72289 | CSO 73 CROWN ST MORRISTON SWANSEA | BP0243801 |  | SW | Swansea | Tawe -confluence with Twrch to tidal l |  |  | 36 | 23 | 23 | 83.62 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
70959 | CSO 80 PENTRPOETH RD MORRISTON | BP0244001 |  | SW | Swansea | Tawe -confluence with Twrch to tidal l |  |  | 1.75 | 7 | 7 | 91.9
70960 | CSO 81 CWM BATH ROAD MORRISTON | BP0244101 |  | SW | West | Tawe -confluence with Twrch to tidal limit |  |  | 0 | 0 | 0 | 99.32
73040 | (BONYMAEN RD NR DARTFORD RD) SWANSE | BP0244401 |  | SW | Swansea | Nant y Fendrod - headwaters to conf with Tawe |  |  | 46.5 | 21 | 21 | 55.15 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
70964 | SWANSEA (BONYMAEN RD) PT 101A , , | BP0244501 |  | SW | Swansea | Nant y Fendrod - headwaters to conf with Tawe |  |  | 53.25 | 36 | 36 | 93.31
70965 | CSO OFF HEOL LAS LLANSAMLET | BP0244701 |  | SW | Swansea | Nant y Fendrod - headwaters to conf with Tawe |  | Swansea Bay | 0.75 | 3 | 0 | 99.73
71420 | SWANSEA - BIRCHGROVE ROAD/ ST. JOHNS CHURCH (POINT 109) CSO | BP0244801 |  | SW | Swansea | Nant Bran |  | Swansea Bay | 6.25 | 8 | 6 | 99.38
73381 | QUARRY ROAD CLYDACH (POINT 125) S | BP0245001 |  | SW | Swansea | Lower Clydach - headwaters to confluen |  |  | - | - | - | 0 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
70975 | HEOL Y NANT/SYBIL STREET CLYDACH (P | BP0245201 |  | SW | Swansea | Tawe -confluence with Twrch to tidal l |  |  | - | - | - | 0 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
71032 | FAIRWOOD RD/LYNDEN TREE P H SWANSEA | BP0245401 |  | SW | Swansea | Swansea Bay | Swans W |  | 1.5 | 5 | 1 | 99.28
50944 | STORM KING NEAR GLAIS PS CSO | BP0246001 |  | SW | Central | Baglan Brook - headwaters to conf with River Ne |  |  | 87.5 | 23 | 23 | 99.98
70805 | 15 METRES D/S WHITLAND BRIDGE , , | BP0246101 |  | SW | West | Gronw - headwaters to confluence with Taf |  |  | 47.5 | 33 | 24 | 99.24
50891 | HOLYTHORNE CROFTY B SEWAGE PS CROFT | BP0246301 |  | SW | Swansea | Burry Estuary | Burry S |  | 7.5 | 5 | 4 | 99.69
52068 | EMERGENT CULVERT GOODWICK , | BP0246801 |  | SW | West | Goodwick Brook - headwaters to tidal |  |  | 422.75 | 79 | 64 | 98.88
52780 | PEMBROKE DOCK STW (EMERGENCY) FORT | BP0250802 |  | SW | South West | MILFORD HAVEN INNER |  |  | 94.75 | 32 | 32 | 99.98
51036 | LLECHRYD NO 1 SPS NEAR CARDIGAN , | BP0251301 |  | SW | South West | Teifi - conf with Nant Wern-Macwydd to |  |  | 867.75 | 62 | 62 | 99.45
53049 | SAUNDERSFOOT STW/PS SAUNDERSFOOT | BP0251801 |  | SW | South West | Saundersfoot Stream |  | Saundersfoot | 51.25 | 30 | 30 | 99.99 | BW | 5 in Bathing Season
53049 | SAUNDERSFOOT STW/PS SAUNDERSFOOT | BP0251803 |  | SW | South West | Coastal Waters at Saundersfoot |  | Saundersfoot | 1294.75 | 79 | 76 | 99.99
53131 | STORM TANKS AT TENBY HEADWORKS TE | BP0251902 |  | SW | South West | River Ritec |  | Tenby S | 687.75 | 54 | 54 | 99.75
53131 | STORM TANKS AT TENBY HEADWORKS TE | BP0251903 |  | SW | South West | River Ritec |  | Tenby S | 693 | 54 | 54 | 99.75
71351 | PEN Y BANC CSO 40 ON HENDRE SEWER | BP0252001 |  | SW | West | Loughor - conf with Marlais to conf with Aman |  |  | 239.75 | 64 | 41 | 50.08 |  |  |  | Data unreliable from 01/04/21 - 26/09/21. Due to erratic telemetry signal.
53021 | LLANELLI STW BERRWICK RD BYNEA | BP0252601 |  | SW | Central | The Loughor Estuary | Burry N |  | 290.5 | 33 | 33 | 99.95 | SFW | 26 in the Year | YES
53047 | CSO AT BURY PORT SPS BURY PORT CARM | BP0252702 |  | SW | Swansea | Nant Dyfatty | Burry N |  | 15.75 | 9 | 9 | 100 | SFW | 14 in the Year
52703 | PWLL SEWAGE PUMPING STATION CARMS | BP0252801 |  | SW | Central | Afon Dulais | Burry N |  | 23 | 2 | 2 | 100 | BW & SFW | 5 in Bathing Season OR 14 in the Year
52703 | PWLL PS (STORM/EMERGENCY) PWLL LLA | BP0252802 |  | SW | Central | Loughor Estuary | Burry N |  | 0 | 0 | 0 | 100 | SFW | 14 in the Year
53040 | SSO. NORTHUMBERLAND OUTFALL | BP0252901 |  | SW | Central | Loughor Estuary | Burry N |  | 42.75 | 19 | 19 | 99.98 | SFW | 14 in the Year | YES
53040 | NORTHUMBERLAND PS (STORM/EMER) | BP0252902 |  | SW | Swansea | Loughor Outer | Burry N |  | 0 | 0 | 0 | 99.45 | SFW | 14 in the Year
53040 | NORTHUMBERLAND PS (STORM/EMER) | BP0252903 |  | SW | West | Loughor Outer | Burry N |  | 0.5 | 2 | 2 | 99.73
52700 | BYNEA PS (EMERGENCY) BYNEA LLANELL | BP0253002 |  | SW | Swansea | Tidal Pill of Loughor Estuary | Burry N |  | 153.25 | 16 | 16 | 99.97 | SFW | 26 in the Year
50785 | STACKPOLE STW (EMERGENCY) STACKPOLE | BP0253601 |  | SW | South West | Un-named of tributary of Bosheston Lakes, Eastern Arm |  | Barafundle | 175.75 | 27 | 26 | 100
53014 | PS AT CLARACH BAY HOL VILLAGE CLARA | BP0254201 |  | SW | South West | The Afon Clarach |  | Aberystwyth N | 204.5 | 22 | 22 | 99.94
53035 | DYNEVOR PS CSO EO LLANDARCY NPT | BP0255601 |  | SW | Central | NEATH |  |  | 1406.5 | 139 | 139 | 99.99
53088 | FARFIELD PS PRINCE OF WALES DRIVE | BP0255701 |  | SW | Central | Neath - conf with Nedd Fechan and Mellte to TL |  |  | 473.75 | 102 | 102 | 100
53034 | LLANTWIT PS LLANTWIT CHURCH NEATH | BP0255801 |  | SW | Central | Neath - conf with Nedd Fechan and Mellte to TL |  |  | 22.25 | 10 | 8 | 99.99
53039 | MELINCRYDDAN PS MILLAND ROAD IND ES | BP0255901 |  | SW | Central | Crythan Brook - headwaters to conf with Neath |  |  | 572.75 | 78 | 78 | 99.93
51104 | PENRHIWTYN SPS NEATH | BP0256001 |  | SW | Central | Baglan Brook - headwaters to conf with River Neath |  | Aberafan | 3 | 5 | 5 | 99.93
53036 | PENTREFFYNNON PS NEATH ABBEY IND ES | BP0256101 |  | SW | Central | NEATH |  |  | 113 | 32 | 26 | 100
52654 | QUAY ROAD PS TOWN CENTRE NEATH , | BP0256201 |  | SW | Central | Neath - conf with Nedd Fechan and Mellte to TL |  |  | 69 | 41 | 41 | 99.94
53085 | GREEN ACRES PS SOUTH CLOVELLY | BP0257501 |  | SW | Central | Ogmore - confluence with Llynfi to tid |  |  | 0 | 0 | 0 | 100
53066 | MOOR (PARROG) PS FISHGUARD HARBOUR | BP0261101 |  | SW | South West | Goodwick Brook - headwaters to tidal |  |  | 271.5 | 31 | 31 | 100
53058 | ASHFIELD ROW P.S ASHFIELD LLANGADO | BP0263301 |  | SW | South West | Tywi (Llandovery Bran to Cothi confl) |  |  | 1103 | 66 | 65 | 99.98
50586 | CROSSHANDS WWTW | BP0265701 |  | SW | South West | Gwili - headwaters to tidal limit |  |  | 566.75 | 91 | 91 | 100
53063 | MANORBIER TRANSFER PS MANORBIER TE | BP0266601 |  | SW | South West | Coastal Waters, Manorbier |  | Manorbier | 162.25 | 15 | 15 | 99.6
71474 | LAMACK VALE PS LAMACK VALE TENBY , | BP0267401 |  | SW | South West | Knightston Brook |  | Tenby S | 22.5 | 14 | 8 | 99.66
50848 | BROADHAVEN SOUTH PS BROADHAVEN , | BP0268701 |  | SW | West | Broadhaven Stream |  | Broadhaven | 18.75 | 9 | 7 | 98.63
53152 | CSO SKETTY PARK DRIVE SWANSEA , | BP0268801 |  | SW | Swansea | Un-nmaed tributary of the River Clyne | Swans W | Swansea Bay | 1 | 3 | 3 | 100 | BW | 5 in Bathing Season
50589 | CRYNANT STW CRYNANT NEATH | BP0269101 |  | SW | Central | Dulais - headwaters to confluence with River Ne |  |  | 5245.25 | 244 | 244 | 99.96
52586 | CSO AT BEDFORD ROAD CEFN CRIBWR , | BP0269201 |  | SW | Swansea | Afan - conf with Corrwg to confluence |  |  | 437.75 | 93 | 84 | 99.9
50652 | LAUGHARNE WWTW (STW) LAUGHARNE | BP0270701 |  | SW | South West | Taf Estuary at confluence of River Coran and Railsgate Pill | Taf |  | 1390.25 | 118 | 118 | 91.3
53119 | LLANTWIT MAJOR WWTW (STW) WICK ROAD | BP0270901 |  | SW | Central | Bristol Channel Inner North |  |  | 324.25 | 42 | 42 | 100
52538 | LLANTWIT MAJOR PS | BP0270902 |  | SW | Central | COLHUW |  |  | 51 | 12 | 12 | 100
50699 | LLETTY BRONGU WWTW LLANGYNWYD MAES | BP0271001 |  | SW | Central | Llynfi - headwaters to Lletty Brongu S |  |  | 1741.25 | 150 | 150 | 99.64
53103 | FABIAN WAY SPS FABIAN WAY SWANSEA | BP0271501 |  | SW | Central | The Neath Estuary | Swans E |  | 781.25 | 48 | 48 | 99.91 | BW | 5 in Bathing Season
50545 | BISHOPSTON STW BRANDY COVE LANE | BP0271801 |  | SW | Central | Coastal Waters Of Brandy Cove | Swans S |  | 161 | 19 | 18 | 100
50557 | BURTON FERRY WWTW NEYLAND PEMBS | BP0272401 |  | SW | South West | Milford Haven Waterway | Cleddau |  | 586 | 44 | 41 | 99.98 | BW | 5 in Bathing Season
70820 | LITTLE HAVEN SPS HEAD OF BEACH LIT | BP0273801 |  | SW | West | Little Haven Stream |  | Broadhaven | 216.25 | 19 | 19 | 99.02
50966 | HEOL DDU PS TRIMSARAN LLANELLI | BP0274101 |  | SW | South West | Nant Dyfatty - headwaters to tidal limit |  |  | 50.25 | 12 | 12 | 99.45
50728 | OVERTON STW PORT EYNON | BP0274701 |  | SW | Central | Coastal Waters of Overton Mere |  | Porth Eynon | 30.5 | 4 | 4 | 100
50564 | CARDIGAN WWTW(STW) CARDIGAN | BP0275401 |  | SW | South West | TEIFI |  |  | 2097.75 | 296 | 284 | 99.97
53158 | BRIDGE STREET CSO LAMPETER | BP0277901 |  | SW | West | Teifi - Camddwr conf to Nant Wern-macwydd conf |  |  | 2 | 7 | 7 | 100
53156 | STATION TERRACE CSO LAMPETER | BP0278001 |  | SW | West | Dulas - headwaters to confluence with Teifi |  |  | 73.75 | 40 | 40 | 100
71460 | BRYNHYFRYD CSO LLANGYFELACH ROAD | BP0280601 |  | SW | Swansea | Tawe - conf with Nant Cwmgelli to tida |  |  | 35.25 | 31 | 31 | 95.52
72480 | MYNYDDGARNLLWYD CSO SWANSEA | BP0280701 |  | SW | Swansea | Tawe - conf with Nant Cwmgelli to tida |  |  | 6 | 12 | 6 | 99.99
71421 | CWMBWRLA CSO CWMBWRLA RBOUT SWANSEA | BP0280801 |  | SW | Swansea | Tawe - conf with Nant Cwmgelli to tida |  |  | 1445.25 | 130 | 130 | 100
72401 | WYCHTREE STREET CSO MORRISTON | BP0280901 |  | SW | Swansea | Tawe -confluence with Twrch to tidal l |  |  | 420.75 | 61 | 61 | 100
53173 | MILL BRIDGE CSO | BP0281401 |  | SW | West | Pembroke - headwaters to tidal limit |  |  | 73.25 | 43 | 43 | 94.54
71450 | MAESTEG SOUTH CSO ASSET 95015 | BP0281601 |  | SW | Bridgend Hereford & Mid Wales | Llynfi - headwaters to Lletty Brongu S |  |  | 4720.25 | 312 | 312 | 97.74
52010 | PICTON PS & PICTON FIELDS CSO | BP0282301 |  | SW | West | MILFORD HAVEN INNER |  |  | 298.75 | 89 | 89 | 99.97
71333 | NEW QUAY CSO NEW QUAY HAVERFORDWEST | BP0282701 |  | SW | West | MILFORD HAVEN INNER |  |  | 61 | 41 | 41 | 100
71480 | GEORGES ROW SPS GEORGES ROW NEATH | BP0283101 |  | SW | Central | Neath Estuary | Swans E |  | 5.25 | 4 | 4 | 99.96 | SFW | 14 in the Year
71702 | BRITON FERRY SPS INNER DOCK NEATH | BP0283201 |  | SW | Central | Neath Estuary | Swans E |  | 8.75 | 5 | 5 | 99.83 | SFW | 14 in the Year
71479 | GIANTS GRAVE SPS PILL TERRACE | BP0283301 |  | SW | Central | Neath Estuary | Swans E |  | 7.75 | 12 | 12 | 99.91 | BW & SFW | 5 in Bathing Season OR 14 in the Year
70764 | BOW STREET SPS BOW STREET | BP0283401 |  | SW | South West | Bow Street Brook - headwaters to conf with Clarach |  | Clarach South | 1129.5 | 76 | 71 | 100
52394 | TY YR AFON CSO TY YR AFON PANTARWEL | BP0283801 |  | SW | Bridgend Hereford & Mid Wales | Ogwr Fawr - headwaters to confluence w |  |  | 3264.75 | 219 | 219 | 100
52440 | CORBETT STREET CSO OGMORE VALE | BP0284001 |  | SW | Bridgend Hereford & Mid Wales | Ogwr Fawr - headwaters to confluence w |  |  | 7 | 5 | 5 | 100
53175 | ABERAERON SPS FORESHORE CAR PARK | BP0284101 |  | SW | South West | Cardigan Bay Central |  |  | 715.25 | 57 | 57 | 100
52384 | HENDRE ROAD CSO PENCOED | BP0286001 |  | SW | Bridgend Hereford & Mid Wales | Ewenny - conf with Ewenny Fach to conf |  |  | 90.5 | 28 | 26 | 100
70291 | CRUNDALE SPS CRUNDALE HAVERFORDWEST | BP0287301 |  | SW | West | MILFORD HAVEN INNER |  |  | 0 | 0 | 0 | 97.63
53154 | AFAN WWTW PHOENIX WHARF HARBOUR RD | BP0287601 |  | SW | Central | Swansea Bay | Swansea Bay (S),(W),(E) | Swansea Bay | 1409.75 | 152 | 152 | 99.97
51222 | BAGLAN SPS BRITON FERRY NEATH | BP0287801 |  | SW | Central | Swansea Bay | Swans E |  | 1651 | 173 | 173 | 99.96 | SFW | 14 in the Year | YES
51222 | BAGLAN SPS BRITON FERRY NEATH | BP0287901 |  | SW | Central | Tidal River Neath | Swans E |  | 0.75 | 2 | 2 | 99.96 | BW & SFW | 5 in Bathing Season OR 14 in the Year
71932 | CSO ADJ 97 CRAIG RD GELLINUDD | BP0288501 |  | SW | Swansea | Tawe -confluence with Twrch to tidal l |  |  | 374 | 65 | 49 | 98.77
71404 | KILLAY SPS OFF GOWER RD KILLAY | BP0289501 |  | SW | Central | Clyne River - headwaters to tidal limit |  |  | 58.25 | 12 | 12 | 100
71280 | CSO SOUTH OF RAILWAY LLANHAREN | BP0289801 |  | SW | South | Ewenny Fach - headwaters to confluence with Ewe |  |  | 645.75 | 87 | 87 | 100
50855 | BRYNMEILLION SPS LLANPUMSAINT | BP0292601 |  | SW | South West | Gwili - headwaters to confluence with Alltwalis |  |  | 269.25 | 43 | 38 | 100
71434 | CSO AT FARMLAND NR ELM STREET | BP0292901 |  | SW | Valleys | Ogwr Fach - headwaters to confluence w |  |  | 424.25 | 67 | 67 | 99.85
52439 | CSO BLANDY TERRACE ADJ ST JOHN ST | BP0293001 |  | SW | Bridgend Hereford & Mid Wales | Ogwr Fawr - headwaters to confluence w |  |  | 280.5 | 66 | 66 | 100
70163 | CSO 24 REAR GARDEN - 40 GER YR AFON | BP0293701 |  | SW | West | Garnant - headwaters to confluence with Aman |  |  | 283.25 | 60 | 60 | 99.64
70904 | CSO 8 SARON ROAD SARON AMMANFORD | BP0293801 |  | SW | West | Loughor - conf with Marlais to conf with Aman |  |  | 32.5 | 17 | 12 | 99.3
71200 | CSO 7 OUTSIDE 29 ABERLASH RD | BP0293901 |  | SW | West | Marlais - headwaters to confluence with Loughor |  |  | 764.75 | 56 | 53 | 99.78
70915 | CSO 5 1 METRE UPSTREAM OF ROAD BRGE | BP0294001 |  | SW | West | Marlais - headwaters to confluence with Loughor |  |  | 1045.25 | 88 | 84 | 99.16
52545 | CSO 26 QUARRY PLACE AMMONFORD | BP0295301 |  | SW | West | Garnant - headwaters to confluence with Aman |  |  | 362.25 | 52 | 52 | 100
70226 | CSO BELOW CEMETERY RD OGMORE VALE | BP0295401 |  | SW | Bridgend Hereford & Mid Wales | Ogwr Fawr - headwaters to confluence w |  |  | 1862.5 | 143 | 143 | 100
71500 | COMBINED SEWER OVERFLOW NO 6 | BP0295801 |  | SW | West | W. Cleddau - Anghof conf to Cartlett Brook conf |  |  | 89.5 | 61 | 61 | 83.55 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
52013 | COMBINED SEWER OVERFLOW NO 10 | BP0295901 |  | SW | West | W. Cleddau - Anghof conf to Cartlett Brook conf |  |  | 0 | 0 | 0 | 100
52441 | NANT Y MOEL JUNIOR SCHOOL CSO | BP0296001 |  | SW | Bridgend Hereford & Mid Wales | Ogwr Fawr - headwaters to confluence w |  |  | 417.75 | 100 | 100 | 100
50806 | WALTON WEST STW BALANCING TANK | BP0296201 |  | SW | South West | Swanswell Brook |  | Broadhaven | 275.75 | 28 | 28 | 99.76
71125 | CWM SEWAGE PUMPING STATION | BP0296401 |  | SW | South West | Newport Bay |  | Newport N | 2423.25 | 136 | 135 | 100
52499 | LLIWITHA ROAD CSO | BP0296601 |  | SW | Swansea | Afon Llan |  | Swansea Bay | 0 | 0 | 0 | 99.42
71896 | BROADMOOR SEAGE PUMPING STATION | BP0296701 |  | SW | South West | Cresswell - headwaters to conf with Waddock Lak |  |  | 85 | 20 | 18 | 99.99
71221 | PUMPING STATION ADJ TO NANT HAWEN | BP0298001 |  | SW | West | Nant Hawen |  | Llangrannog | 133.75 | 14 | 14 | 99.71
32830 | LLANDOW PUMPING STATION LLANDOW | BP0298801 |  | SW | Central | Alun - headwaters to confluence with Ewenny |  |  | 1075 | 60 | 57 | 99.45
70258 | LLYSWORNEY PUMPING STATION | BP0298901 |  | SW | Central | Alun - headwaters to confluence with Ewenny |  |  | 129 | 7 | 7 | 16.76 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
32831 | SO & EO at Colwinston Pumping Station | BP0299201 |  | SE | Central | Alun - headwaters to confluence with Ewenny |  |  | 101.25 | 12 | 10 | 100
71368 | PARC Y DAI NO1 CSO DREFACH | BP0301001 |  | SW | West | Gwendraeth Fawr - headwaters Afan Goch |  |  | 148.25 | 27 | 25 | 16.32 |  |  |  | Communications issue - access issue
71303 | DDOLL LAS TEMPORARY CSO LLANELLI | BP0301801 |  | SW | West | Gwendraeth Fawr - headwaters Afan Goch |  |  | 123.75 | 25 | 24 | 99.95
71447 | CSO AT LON Y CARIADON NORTH CORNELL | BP0303101 |  | SW | Swansea | Afon Fach |  | Rest Bay Porthcawl | 0.25 | 1 | 0 | 99.45
52733 | SOUTH CORNELLY PUMPING STATION | BP0303201 |  | SW | Central | Ogmore - confluence with Llynfi to tid |  |  | 0 | 0 | 0 | 100
53081 | HAZEL GROVE PUMPING STATION PYLE | BP0303301 |  | SW | Swansea | Kenfig - headwaters to conf with Nant Cwm Phili |  |  | 4.25 | 2 | 2 | 99.46
70705 | HEOL FACH CSO NORTH CORNELLY | BP0303401 |  | SW | Swansea | Coastal Waters |  | Rest Bay Porthcawl | 0 | 0 | 0 | 92.24
70200 | CSO NO 31 OPP NEW ROAD SKEWEN | BP0303801 |  | SW | Swansea | Clydach - headwaters to conf with River Neath |  |  | 1.5 | 5 | 5 | 95.9
71417 | CSO NO 38 O/S PUBLIC HEALTH OFFICE | BP0303901 |  | SW | Swansea | Neath - conf with Nedd Fechan and Mellte to TL |  | Aberafan | 2 | 7 | 1 | 99.62
71472 | CSO CAR PARK NEW OGMORE VALE SCHOOL | BP0304001 |  | SW | Bridgend Hereford & Mid Wales | Ogwr Fawr - headwaters to confluence w |  |  | 813.5 | 74 | 74 | 77.25 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
71428 | CSO 136, Afan St. Velindre, Afan | BP0304101 |  | SW | Swansea | Afon Afan |  | Aberafan | 2 | 6 | 2 | 99.98
70173 | CSO NO 134 GOYTRE BRYN AFAN | BP0304201 |  | SW | Swansea | Ffrwd Wyllt |  | Aberafan | 248.25 | 86 | 64 | 99.01
52343 | CSO NO 116 100M U/S CONF PELENNA | BP0304301 |  | SW | Swansea | Afon Afan |  | Aberafan | 9.25 | 20 | 7 | 93.13
52428 | MILTON DRIVE CSO BRIDGEND | BP0304501 |  | SW | Swansea | Ogmore - confluence with Llynfi to tid |  |  | 23.25 | 11 | 8 | 99.44
52883 | PONTYBEREM WASTE WATER TREATMENT WK | BP0304601 |  | SW | South West | Gwendraeth Fawr - Afan Goch to tidal limit |  |  | 1042.5 | 62 | 62 | 99.9
71036 | BLAEN Y MAES POINT66 CSO | BP0304901 |  | SW | Swansea | Llan - headwaters to tidal limit |  |  | 3 | 4 | 4 | 98.69
52333 | GORSEINON 1 (S123) 3M'S CSO | BP0305001 |  | SW | Swansea | Lliw - headwaters to confluence with Llan |  |  | 78.5 | 17 | 17 | 97.99
71401 | KINGSWAY COMBINED SEWER OVERFLOW | BP0305101 |  | SW | Swansea | Llan - headwaters to tidal limit |  |  | 0 | 0 | 0 | 80 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
70232 | CWMBACH ROAD CSO COCKETT SWANSEA | BP0305201 |  | SW | Swansea | Llan - headwaters to tidal limit |  |  | 181.5 | 66 | 66 | 99.99
52302 | KINGSBRIDGE CSO GORSEINON SWANSEA | BP0305301 |  | SW | Swansea | Lliw - headwaters to confluence with Llan |  |  | 186 | 44 | 44 | 100
71699 | CSO at rear of Ynys Y Wern, Cwmafan | BP0305601 |  | SW | Swansea | Nant Cwm-Clais |  | Aberafan | 214.25 | 75 | 75 | 97.86
50993 | LANGLAND SPS LANGLAND SWANSEA | BP0305901 |  | SW | Swansea | Langland Bay | Swans S | Langland | 2 | 4 | 2 | 93.56
71574 | RHOSNEWYDD MAESYGWERN CSO TUMBLE | BP0307301 |  | SW | West | Gwendraeth Fawr - Afan Goch to tidal limit |  |  | 43.5 | 26 | 26 | 99.63
51647 | CSO NO 109 CYMMER CSO AFAN | BP0307901 |  | SW | Central | Afan - conf with Corrwg to confluence |  |  | 887.5 | 115 | 115 | 99.97
50598 | CWRT NEWYDD STW STORM OVERFLOW | BP0308501 |  | SW | South West | Cledlyn - headwaters to confluence with Teifi |  |  | 4400 | 366 | 366 | 100
70687 | WINDSOR RAOD CSO PORTCAWL | BP0308601 |  | SW | Swansea | Bristol Channel | Porthcawl | Rest Bay | - | - | - | 0 | BW | 5 in Bathing Season |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
52461 | PENIEL GREEN CSO PENIEL GREEN ROAD | BP0309801 |  | SW | Swansea | Culvert of trib of Nant-Bran |  | Swansea Bay | 120.25 | 24 | 24 | 99.96
71292 | FELIN FRAN CSO WALTERS RD LLANSAMLE | BP0311401 |  | SW | Swansea | Nant-Bran |  |  | 237 | 33 | 33 | 88.9 |  |  |  | Communications issue, resolved in August 2021.
50625 | GOLDEN GROVE WWTW INLET CSO LLANDIE | BP0312601 |  | SW | South West | Tywi (Llandovery Bran to Cothi confl) |  |  | 876.5 | 142 | 142 | 100
50539 | ANGLE WWTW PEMBROKE PEMBROKESHIRE | BP0312801 |  | SW | South West | Milford Haven Outer |  |  | 695.75 | 46 | 44 | 100
51889 | LLANEDI WWTW | BP0312901 |  | SW | South West | Gwili - headwaters to tidal limit |  |  | 1652.5 | 275 | 208 | 100
50605 | EGLWYSWRW WWTW EGLWYSWRW NR NWPRT | BP0314101 |  | SW | South West | Nant Duad - headwaters to confluence with Nyfer |  |  | 359 | 19 | 19 | 100
71359 | CSO AT UPPER CROSS ROADS NR COEDCAE | BP0314701 |  | SW | West | Dafen - headwaters to tidal limit |  |  | 0 | 0 | 0 | 99.44 | SFW | 14 in the Year
71505 | KILGETTY EAST PS KILGETTY EAST WWTW | BP0314901 |  | SW | South West | Ford's Lake Stream |  | Wisemans Bridge | 795 | 46 | 46 | 100
52307 | BEN HUGHES FOUNDRY CSO OPP REV JAMES PUBLIC HOUSE, LOUGHOR | BP0315201 |  | SW | Swansea | LOUGHOR |  | Swansea Bay | 17.25 | 9 | 9 | 6.95 | BW | 5 in Bathing Season |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
50792 | TIERS CROSS WWTW INLET CSO PEMBRK | BP0315301 |  | SW | South West | Rickeston Pill - headwaters to tidal limit |  |  | 4666.75 | 263 | 252 | 99.99
50801 | TRIMSARAN WWTW SPUDDER BRIDGE RD | BP0315501 |  | SW | South West | Gwendraeth Fawr - Afan Goch to tidal limit |  |  | 1167 | 84 | 84 | 94.16
50801 | TRIMSARAN WWTW SPUDDER BRIDGE RD | BP0315601 |  | SW | South West | Gwendraeth Fawr - Afan Goch to tidal limit |  |  | 137.5 | 101 | 101 | 99.97
52337 | CSO 17 UNDER OLD RD BRDGE ABRDULAIS | BP0316401 |  | SW | Swansea | Dulais - headwaters to confluence with River Ne |  |  | 45 | 12 | 12 | 99.69
70181 | CSO 34 REAR OF 38 CAENANT TERRACE, NEATH | BP0316501 |  | SW | Swansea | Tennant Canal |  | Aberafan | 6 | 5 | 4 | 95.8
71701 | CSO 48 NEATH RIVER BRIDGE ADJ CALOR | BP0316601 |  | SW | Swansea | Neath - conf with Nedd Fechan and Mellte to TL |  |  | 166.75 | 53 | 36 | 100
50597 | CWRT HENRI WWTW INLET STORM OVERFLW | BP0316701 |  | SW | South West | Dulas - conf with Sannan to confluence with Tyw |  |  | 156.5 | 51 | 34 | 99.42
71778 | HEOL PENTRE BACH CSO GORSEINON | BP0316901 |  | SW | Swansea | Llannant Pill - headwaters to tidal limit |  |  | 0 | 0 | 0 | 1.92 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
74549 | BOROUGH ROAD CSO GORSEINON SWANSEA | BP0317001 |  | SW | Swansea | Llannant Pill - headwaters to tidal limit |  |  | 0 | 0 | 0 | 98.75
50657 | LLANDEWI BREFI WWTW LLANDEWI BREFI | BP0317101 |  | SW | South West | Brefi - headwaters to confluence with Teifi |  |  | 422.75 | 30 | 30 | 99.98
50703 | MATHRY SPS NR FISHGUARD PEMBROKSHRE | BP0317201 |  | SW | South West | W. Cleddau - headwaters to conf with Cleddau No |  |  | 91.25 | 13 | 11 | 100
50578 | CYNWYL ELFED WWTW CYNWYL ELFED CARM | BP0317301 |  | SW | South West | Duad - conf with Gochen to confluence with Gwil |  |  | 325.75 | 36 | 35 | 48.6 |  |  |  | Discharge mechanism revised. Reliable data from 08/07/2021.
71602 | CSO NO 117 PLAYGROUND, REAR OF 3 MORGAN TERRACE, EFAIL FACH | BP0317501 |  | SW | Swansea | River Pelenna |  | Aberafan | 0 | 0 | 0 | 96.68
52100 | CSO 129 GLYNCORRWG CSO GLYNCORRWG | BP0317601 |  | SW | Central | Corrwg - headwaters to confluence with Afan |  |  | 113.75 | 26 | 26 | 99.9
50593 | CWMGWILI WWTW CWMGWILI NR AMMANFORD | BP0318001 |  | SW | South West | Gwili - headwaters to tidal limit |  |  | 0 | 0 | 0 | 99.98
51169 | ST DOGMAELS NORTH END PS CSO AND EO | BP0318101 |  | SW | South West | Unnamed - HW to TL, Teifi estuary, St Dogmaels N. |  | Poppit West | 1518.5 | 79 | 79 | 100 | BW | 5 in Bathing Season | YES
72041 | GILFACHREDA CSO NEWQUAY CEREDIGION | BP0319101 |  | SW | West | Afon Lethi |  | New Quay | 908 | 68 | 68 | 100 | BW | 5 in Bathing Season | YES
72036 | LLANARTH BRIDGE CSO LLANARTH CERE'N | BP0319201 |  | SW | West | Gido - headwaters to tidal limit |  |  | 491.75 | 79 | 71 | 75.89 |  |  |  | Data unreliable from 14/06 to 09/09/2021. Due to erratic telemetry signal, resolved.
72090 | REAR GODFREY AVENUE GLYNNEATH NPT | BP0319301 |  | SW | Swansea | Neath - conf with Nedd Fechan and Mellte to TL |  |  | 183.5 | 50 | 47 | 100
71338 | HEOL GOFFA ROAD CSO LLANELLI CARMS | BP0319601 |  | SW | West | Afon Lliedi | Burry N |  | 1 | 3 | 1 | 99.7 | BW | 5 in Bathing Season
72389 | HEOL HEN CSO LLWYNHENDY LLANELLI | BP0319901 |  | SW | West | Un-named Tributary | Burry N |  | 0 | 0 | 0 | 99.21 | BW | 5 in Bathing Season
70256 | CSO 12 B4599 ROAD BRIDGE | BP0320001 |  | SW | Swansea | Tawe - conf with Nant Llech to conf wi |  |  | 202 | 49 | 41 | 100
52383 | COYCHURCH ROAD CSO BRIDGEND | BP0320501 |  | SW | Swansea | Ewenny - conf with Ewenny Fach to conf |  |  | - | - | - | 0 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
72414 | DENVER R'D INTO CULVERT SWANSEA | BP0320801 |  | SW | Swansea | Afan Llan |  | Swansea Bay | 14.25 | 27 | 27 | 100
72263 | DIMBATH AVE BLACKMILL BRIDGEND | BP0321001 |  | SW | Bridgend Hereford & Mid Wales | Ogwr Fach - headwaters to confluence w |  |  | 901.25 | 103 | 101 | 99.53
52029 | GREENFIELD SQUARE CSO CARDIGAN CERE | BP0321201 |  | SW | West | Mwidan - headwaters to confluence with Teifi |  | Poppit West | 28 | 20 | 15 | 100 | BW | 5 in Bathing Season
71327 | CHURCH ROAD CSO BURRY PORT LLANELLI | BP0321901 |  | SW | West | Nant Dyfatty | Burry N |  | 0.5 | 2 | 0 | 95.09 | BW | 5 in Bathing Season
72083 | O/S 54 YNYS STREET | BP0322001 |  | SW | Bridgend Hereford & Mid Wales | Afan - confluence with Pelenna to tidal limit |  |  | 25.25 | 14 | 6 | 99.19
53095 | PRIORY | BP0322201 |  | SW | South West | Huberston Pill - headwaters to tidal limit |  |  | 11.5 | 7 | 7 | 100
72170 | STEYNTON SPS | BP0322501 |  | SW | South West | Castle Pill - headwaters to tidal limit |  |  | 509.25 | 59 | 52 | 99.72
52553 | PONTNEDDFECHAN STW SWANSEA | BP0322901 |  | SW | Central | Neath - conf with Nedd Fechan and Mellte to TL |  |  | 1525 | 171 | 155 | 99.97
51915 | 270M D/S ROAD | BP0323001 |  | SW | Swansea | LOUGHOR |  |  | 25.25 | 13 | 13 | 99.63
72101 | PENRHIWLLAN P S | BP0323301 |  | SW | South West | Teifi - conf with Nant Wern-Macwydd to |  |  | 439.5 | 30 | 29 | 100
51155 | SILIAN PS LAMPETER CEREDIGION | BP0323401 |  | SW | South West | Dulas - headwaters to confluence with Teifi |  |  | 1895.75 | 94 | 94 | 100
51136 | TY HEN RHOS P S | BP0323501 |  | SW | South West | Siedi - headwaters to confluence with Teifi |  |  | 512.5 | 45 | 38 | 100
50723 | NEWGALE SEWAGE TREATMENT WORKS | BP0324301 |  | SW | South West | Brandy Brook |  | Newgale | 451.25 | 38 | 35 | 99.99
50576 | CLYNDERWEN WWTW INLET CSO | BP0324401 |  | SW | South West | Longford Brook - HW to conf with E. Cleddau |  |  | - | - | - | 0 |  |  |  | Further work needed on discharge mechanism, revisit planned for 2021. Modified inlet channel impacting discharge mechanism.
50653 | LETTERSTON EAST WWTW INLET CSO | BP0324501 |  | SW | South West | Anghof - headwaters to conf with Western Cledda |  |  | 1537 | 89 | 88 | 100
50671 | LLANGWM WWTW LLANGWM PEMBROKESH | BP0324601 |  | SW | South West | MILFORD HAVEN INNER | Cleddau |  | 900 | 43 | 43 | 100
50599 | CYNGHORDY WWTW INLET STORM OVERFLOW | BP0328201 |  | SW | South West | Bran - headwaters to confluence with Crychan |  |  | 795.5 | 102 | 102 | 99.95
50611 | FELINGWM WASTEWATER TREATMENT WORKS | BP0328301 |  | SW | South West | Cloidach - headwaters to confluence with Cothi |  |  | 323 | 89 | 70 | 100
50639 | HUNDLETON WWTW INLET STORM OVERFLOW | BP0328401 |  | SW | South West | Goldborough Pill East - headwaters to tidal limit |  |  | 515 | 110 | 92 | 100
50734 | PEMBREY WWTW PEMBREY CARMARTHENSH | BP0328501 |  | SW | Central | unnamed trib of Loughor Estuary |  | Pembrey | 1354.25 | 100 | 100 | 100
71963 | MONASTERY ROAD CSO (CSO 35) NEATH | BP0336901 |  | SW | West | Clydach - headwaters to conf with River Neath |  |  | 20.5 | 14 | 14 | 99.56
71885 | CSO 790/CSO 800/CHIP SHOP CSO | BP0337301 |  | SW | West | New Quay Bay via surface water sewer |  | New Quay North | - | - | - | 0 | BW | 5 in Bathing Season |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
71887 | CSO SOUTH JOHN STREET NEW QUAY | BP0337401 |  | SW | West | New Quay Bay via surface water sewer |  | New Quay | 0 | 0 | 0 | 99.42 | BW | 5 in Bathing Season
72907 | CSO 790/CSO 800/CHIP SHOP CSO | BP0337501 |  | SW | West | New Quay Bay |  | New Quay North | 0.25 | 1 | 1 | 98.91 | BW | 5 in Bathing Season
52765 | LLANINA WWTW PS LLANINA NEW QUAY | BP0338701 |  | SW | South West | Coastal Waters off Llanina Point |  | New Quay | 263.5 | 20 | 20 | 100
52765 | LLANINA WWTW/LL OLD H'DWATERS PS | BP0338801 |  | SW | South West | Coastal Waters off Llanina Point |  | New Quay | 242 | 27 | 27 | 100
50649 | LAMPHEY WWTW LAMPHEY NEAR PEMBROKE | BP0339101 |  | SW | South West | Pembroke - headwaters to tidal limit |  |  | 6 | 3 | 2 | 99.94
71827 | CSO SOUTH OF MAESTIR FELINFOEL LLAN | BP0339801 |  | SW | Swansea | Lliedi - headwaters to tidal limit |  |  | 0 | 0 | 0 | 99.45 | SFW | 14 in the Year
50716 | PONT-AR-GOTHI & NANTGAREDIG WWTW | BP0340501 |  | SW | South West | Cothi - headwaters to confluence with Tywi |  |  | 0 | 0 | 0 | 100
50686 | LLANSAWEL WWTW | BP0340601 |  | SW | South West | Marlais - conf with Melinddwr to conf with Cothi |  |  | 5.5 | 9 | 5 | 99.97
70244 | CHAINBRIDGE CSO GLYN-NEATH | BP0341101 |  | SW | West | Neath - conf with Nedd Fechan and Mellte to TL |  |  | 695.5 | 74 | 74 | 86.74 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
71110 | PENRALLTDRAW COMBINED SEWER | BP0341301 |  | SW | West | Teifi - conf with Nant Wern-Macwydd to |  |  | 12 | 6 | 5 | 99.35
50759 | RESOLVEN STW STORM TANKS NEATH | BP0341401 |  | SW | Central | Neath - conf with Nedd Fechan and Mellte to TL |  |  | 391.5 | 64 | 64 | 100
50679 | LLANNANT WWTW LLANNANT ROAD SWANSEA | BP0341501 |  | SW | Central | Llannant Pill - headwaters to tidal limit |  |  | 2383.75 | 173 | 173 | 99.97
71848 | GEORGE IV CSO 23 UPPER CWMTWRCH | BP0341601 |  | SW | Swansea | Twrch - conf with Llynfell to confluen |  |  | 688.25 | 57 | 57 | 100
72250 | DILWYN ARMS PONTARDAWE CROSS NPT | BP0343601 |  | SW | Swansea | Upper Clydach - headwaters to confluen |  |  | 556.25 | 105 | 105 | 99.98
71780 | CAREW/MILTON WWTWS PEMBROKESHIRE | BP0345601 |  | SW | South West | Radford Pill | Carew |  | 3710.75 | 172 | 172 | 100
50596 | CWMTAWEL WWTW OFF A48 S CROSS HANDS | BP0345701 |  | SW | South West | Gwili - headwaters to tidal limit |  |  | 0 | 0 | 0 | 99.96
72998 | DALE WWTW DALE MILFORD HAVEN PEMBS | BP0345801 |  | SW | South West | Milford Haven Waterway |  | Dale | 15 | 24 | 15 | 99.99
50726 | NEYLAND WWTW NEYLAND PEMBROKESH | BP0347501 |  | SW | South West | MILFORD HAVEN INNER | Cleddau |  | 38.75 | 32 | 24 | 100
73567 | GLOGUE STW | BP0348601 |  | SW | South West | Taf - headwaters to confluence with Cynin |  |  | 1874.5 | 127 | 124 | 99.72
71740 | HENDY SEWAGE PUMPING STATION | BP0349601 |  | SW | Swansea | LOUGHOR |  |  | 18.5 | 2 | 2 | 99.66
50573 | CILYCWM WWTW | BP0349901 |  | SW | South West | Gwenlais - headwaters to confluence with Tywi |  |  | 1677.25 | 238 | 177 | 99.7
52806 | ABERARTH WWTW ABERARTH CEREDIGION | BP0350101 |  | SW | South West | Arth - headwaters to tidal limit |  |  | 457.25 | 33 | 29 | 100
71779 | GWBERT SEWAGE PUMPING STATION | BP0350201 |  | SW | South West | Cardigan Bay |  | Poppit | 154.75 | 20 | 18 | 100
50786 | TALGARREG WWTW TALGARREG CEREDIGION | BP0350501 |  | SW | South West | Clettwr - headwaters to confluence with Teifi |  |  | 314 | 58 | 54 | 95.66
50533 | ADPAR WWTW ADPAR CEREDIGION | BP0350601 |  | SW | South West | Teifi - conf with Nant Wern-Macwydd to |  |  | 408 | 24 | 24 | 99.98
51665 | LLANSAINTFFRAID SPS CEREDIGION | BP0351101 |  | SW | South West | Cardigan Bay Central |  |  | 494.25 | 48 | 42 | 100
72004 | CANAL CSO. TOWPATH OFF HEBRON ROAD, CLYDACH | BP0353201 |  | SW | Swansea | Tawe -confluence with Twrch to tidal l |  |  | 156.25 | 50 | 50 | 99.63
51113 | PONT-YR-HAFOD SEWAGE PUMPING STATION | BP0353301 |  | SW | West | Stonehall Stream - HW to conf with W. Cleddau |  |  | 1802.5 | 94 | 94 | 77.73 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
71853 | CHURCH ROAD CSO CHURCH ROAD NEATH | BP0353501 |  | SW | Swansea | Neath - conf with Nedd Fechan and Mellte to TL |  |  | 22.5 | 7 | 7 | 99.99
70184 | CADOXTON ROAD CSO, NEATH | BP0353601 |  | SW | Swansea | River Neath |  | Aberafan | 3 | 3 | 3 | 96.83
71958 | OLD ROAD CSO OLD ROAD SKEWEN NEATH | BP0353701 |  | SW | Swansea | Clydach - headwaters to conf with River Neath |  | Aberafan | 293.25 | 77 | 77 | 99.98
52356 | GNOLL PARK ROAD CSO, NEATH | BP0353801 |  | SW | Swansea | River Neath |  | Aberafan | 62.5 | 63 | 63 | 99.73
71414 | PARK STREET CSO PARK STREET TONNA | BP0353901 |  | SW | North | Neath - conf with Nedd Fechan and Mellte to TL |  |  | 5.25 | 13 | 13 | 99.69
50858 | CEI BACH SPS NEWQUAY CEREDIGION | BP0354501 |  | SW | South West | unnamed drainage ditch |  | New Quay | 0 | 0 | 0 | 99.98 | BW | 5 in Bathing Season
71934 | WILKES HEAD CSO LLANDYSUL CERED'N | BP0356201 |  | SW | South West | Teifi - conf with Nant Wern-Macwydd to |  |  | 267 | 50 | 43 | 100
71328 | SPS HEOL VAUGHAN BURRY PORT CARMS | BP0359101 |  | SW | West | Old Canal | Burry N |  | 3.25 | 2 | 2 | 91.77 | SFW | 26 in the Year
71937 | GLANDYFFRYN CLOSE CSO, PORT TALBOT | BP0359301 |  | SW | Swansea | Ffrwd Wyllt - headwaters to tidal limi |  |  | 13.5 | 10 | 10 | 100
52801 | HAVARD ROAD CSO LLANELLI CARMS | BP0359401 |  | SW | West | Dafen - headwaters to tidal limit |  |  | 4.75 | 12 | 12 | 100 | SFW | 26 in the Year
50544 | BEULAH WWTW INLET SO BEULAH CERED'N | BP0361401 |  | South West |  | Ceri - Dulas to conf Teifi |  |  | 1746.5 | 214 | 214 | 99.99
50567 | CARWAY WWTW CARWAY CARMS | BP0361501 |  | SW | South West | Gwendraeth Fawr - Afan Goch to tidal limit |  |  | 3184 | 192 | 190 | 99
73428 | CARMEL WWTW CARMEL | BP0361601 |  | SW | South West | Marlais - headwaters to confluence with Loughor |  |  | 3667.75 | 187 | 186 | 100
71961 | HEOL ILLTYD CSO BRYNCOCH NPT | BP0362001 |  | SW | Swansea | Neath - conf with Nedd Fechan and Mellte to TL |  |  | 0.25 | 1 | 1 | 99.98
71446 | STATION ROW CSO PONTYRHYL BRIDGEND | BP0370801 |  | SW | Swansea | Garw - headwaters to confluence with O |  |  | 1875.25 | 158 | 155 | 93.23
72075 | CAERBRYN R'D CSO PENYGROES CARMS | BP0371201 |  | SW | South West | Loughor - conf with Marlais to conf with Aman |  |  | 439.75 | 73 | 65 | 100
50903 | CWMANN SPS CWMANN LAMPETER CERED'N | BP0371301 |  | SW | South West | Teifi - Camddwr conf to Nant Wern-macw |  |  | 240.5 | 102 | 102 | 100
52151 | CSO No 115, Scott's Yard, Cwmafan | BW0200101 |  | SW | Swansea | Afon Afan |  | Aberafan | 764.5 | 97 | 97 | 99.42
52153 | CSO NO 125 CWMAFAN RFC CWMAFAN | BW0200301 |  | SW | Swansea | Afan - confluence with Pelenna to tidal limit |  |  | 116.25 | 21 | 19 | 97.99
50814 | ABBEY SPS BRITISH STEEL SITE | BW0202801 |  | SW | Central | Swansea Bay | Swans E |  | 0.5 | 2 | 2 | 99.8 | BW | 5 in Bathing Season
52170 | SWO.M'HOLE148 GOUGH ARM YSTRADGYN | BW0600101 |  | SW | Swansea | Tawe - conf with Giedd to confluence with Twrch |  |  | 135.5 | 33 | 33 | 92.24
52172 | CSO 13 RUGBY CLUB | BW0600301 |  | SW | Swansea | Tawe - conf with Giedd to confluence with Twrch |  |  | 100.75 | 16 | 16 | 99.59
52173 | MASON'S ARMS SWO YSTRADG | BW0600401 |  | SW | Bridgend Hereford & Mid Wales | Tawe - conf with Giedd to confluence with Twrch |  |  | 121 | 21 | 21 | 99.47
73374 | CSO 10 REAR OF WAUN GYRLAIS PENRHOS | BW0600501 |  | SW | Swansea | Tawe - conf with Nant Llech to conf wi |  |  | 108.25 | 30 | 27 | 100
52175 | SWO.M'HOLE12 CWMTAWE FM PENRHOS | BW0600601 |  | SW | Swansea | Tawe - conf with Nant Llech to conf wi |  |  | 122 | 17 | 16 | 98.13
71849 | CSO 4 OPPOSITE LAMB & FLAG COTTAGES | BW0600701 |  | SW | Swansea | Tawe - conf with Nant Llech to conf wi |  |  | 1239.25 | 130 | 130 | 99.99
52177 | SWO.M'HOLE 14 ABERCRAVE ST.DAVIDS C | BW0600801 |  | SW | Swansea | Tawe - conf with Nant Llech to conf wi |  |  | 117 | 19 | 18 | 40.76 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
50813 | YSTRADGYNLAIS WWTW OFF WIND ROAD | BW0600901 |  | SW | Central | Tawe - conf with Giedd to confluence with Twrch |  |  | 2546.5 | 137 | 137 | 100
52180 | CWMTWRCH SWO YSTRADGYNLAIS YSTRADGY | BW0601101 |  | SW | Swansea | Twrch - conf with Nant Gwys to conf wi |  |  | 1468.25 | 116 | 116 | 98.8
71369 | PARC Y DAI NO.2 CSO DREFACH | BW0800101 |  | SW | West | Gwendraeth Fawr - headwaters Afan Goch |  |  | 163.75 | 55 | 46 | 97.56
52182 | BLAENHIRWAUN CSO CEFNEITHIN | BW0800201 |  | SW | West | Gwendraeth Fawr - headwaters Afan Goch |  |  | 744.25 | 100 | 94 | 96.16
51942 | HEOL NAZARETH CSO | BW0800601 |  | SW | West | Gwendraeth Fawr - Afan Goch to tidal limit |  |  | 7.5 | 8 | 8 | 99.45
52186 | HEOL MEINCIAU CSO | BW0800701 |  | South West |  | Gwendraeth Fawr - Afan Goch to tidal limit |  |  | 105.75 | 20 | 20 | 100
71332 | TOM JONES NURSERY CSO | BW0800901 |  | SW | West | Gwendraeth Fawr - Afan Goch to tidal limit |  |  | 217.25 | 48 | 48 | 100
71578 | CLOS ISAF CSO DREFACH | BW0801001 |  | SW | West | Gwendraeth Fawr - headwaters Afan Goch |  |  | 173 | 49 | 44 | 81.55 |  |  |  | Communications issue from 01/01 to 4/3/2021, resolved.
71575 | NEW LODGE INN CSO PONTYBEREM CARM | BW0801101 |  | SW | West | Gwendraeth Fawr - Afan Goch to tidal limit |  |  | 140 | 30 | 30 | 100
70156 | NEW PONTYBEREM PS CSO PONTYBEREM | BW0801201 |  | SW | South West | Gwendraeth Fawr - Afan Goch to tidal limit |  |  | 334.5 | 48 | 48 | 99.98
51968 | SWO. FELINFACH RD. YSTRADOWEN. | BW1400101 |  | SW | West | Twrch - headwaters to confluence with |  |  | 452.25 | 36 | 34 | 15.44 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
52194 | SWO.M'HOLE 154A GEORGE IV PH UPPER | BW1400201 |  | SW | Swansea | Twrch - conf with Llynfell to confluen |  |  | 134.25 | 32 | 24 | 99.8
52196 | CSO 38 500M UP/STRM CONF LOUGHER | BW1400401 |  | SW | West | Aman - conf with Garnant to conf with Loughor |  |  | 42 | 41 | 41 | 100
71319 | CSO 37 MANHOLE 24B BETWS RD BRIDGE | BW1400501 |  | SW | West | Aman - conf with Garnant to conf with Loughor |  |  | 346.25 | 73 | 54 | 99.12
52198 | CSO 36 MANHOLE 31C OPP BETTWS PK | BW1400601 |  | SW | West | Aman - conf with Garnant to conf with Loughor |  |  | 204.25 | 67 | 50 | 99.37
71968 | CS0 34 100M DOWNSTREAM OF BRIDGE | BW1400701 |  | SW | West | Aman - conf with Garnant to conf with Loughor |  |  | 222.75 | 34 | 34 | 99.97
71889 | CSO 33 5M DOWNSTREAM OF PIPE BRIDGE | BW1400801 |  | SW | West | Aman - conf with Garnant to conf with Loughor |  |  | 2023 | 139 | 139 | 99.98
52201 | CSO 31 MANHOLE 72C MAESGRENIG | BW1400901 |  | SW | West | Aman - conf with Garnant to conf with Loughor |  |  | 11.5 | 9 | 6 | 21.67 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
52202 | CSO 30 MANHOLE 72F MAESGRENIG | BW1401001 |  | SW | West | Aman - conf with Garnant to conf with Loughor |  |  | 72.75 | 12 | 12 | 25.57 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
70894 | CSO 32 30M D/STRM A474 ROADBRIDGE | BW1401101 |  | SW | West | Aman - conf with Garnant to conf with Loughor |  |  | 39.5 | 14 | 9 | 68.53 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
71202 | CSO 29 AT MANHOLE 76C NR HOSPITAL | BW1401201 |  | SW | West | Aman - conf with Garnant to conf with Loughor |  |  | 0.25 | 1 | 0 | 99.8
71208 | CSO 28 AT MANHOLE 89 NR AMMAN RFC | BW1401301 |  | SW | West | Aman - conf with Garnant to conf with Loughor |  |  | 888.5 | 102 | 102 | 100
71379 | CSO 22 SW CORNER OF DISUSED TIP | BW1401401 |  | SW | West | Garnant - headwaters to confluence with Aman |  |  | 328.75 | 42 | 42 | 100
70914 | CSO 23 MANHOLE 125B NR BRYNBACH FM | BW1401501 |  | SW | West | Aman - headwaters to confluence with Garnant |  |  | - | - | - | 0 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
71203 | CSO 20 MANHOLE 135B WAR MEMORIAL | BW1401601 |  | SW | West | Garnant - headwaters to confluence with Aman |  |  | 75.75 | 55 | 55 | 95.41
52209 | CSO 21 NR FORGE WASHERY BRYNAMMAN | BW1401701 |  | SW | Bridgend Hereford & Mid | Aman - headwaters to confluence with Garnant |  |  | 163.5 | 122 | 77 | 99.84
52210 | CSO 16 PANTYFFYNON RAILWAY BRIDGE | BW1401801 |  | SW | West | Loughor - conf with Marlais to conf with Aman |  |  | 730.5 | 84 | 79 | 99.89
52213 | CSO 13/42 PONT Y CLERC RD BRIDGE | BW1401901 |  | SW | West | Loughor - conf with Marlais to conf with Aman |  |  | 499 | 83 | 71 | 89.59 |  |  |  | Data unreliable from 04/10 to 7/11/2021. Due to erratic telemetry signal, resolved.
52212 | CSO 12 MANHOLE 172K AMMANFORD | BW1402001 |  | SW | West | Loughor - conf with Marlais to conf with Aman |  |  | 3 | 5 | 4 | 99.59
71382 | CSO 14/43 PONT Y CLERC RD AMMANFORD | BW1402101 |  | SW | West | Loughor - conf with Marlais to conf with Aman |  |  | 2235.5 | 134 | 134 | 85.76 |  |  |  | Communications issue from 07/02 to 07/03/2021 and from 30/04 to 24/05/2021, resolved.
71201 | CSO 9 10 METRES DOWNSTREAM - BRIDGE | BW1402301 |  | SW | West | Loughor - conf with Marlais to conf with Aman |  |  | 475 | 96 | 86 | 99.97
52216 | CSO 6 NR BRYN MARLAIS FARM | BW1402401 |  | SW | West | Marlais - headwaters to confluence with Loughor |  |  | 4248.25 | 227 | 227 | 99.45
71372 | CSO 3 MANHOLE 222D WITHIN HIGHWAY | BW1402501 |  | SW | West | Marlais - headwaters to confluence with Loughor |  |  | 177.75 | 35 | 28 | 99.44
52218 | CSO 4 MANHOLE 225A ADJ 3 RAWLINGS | BW1402601 |  | South West |  | Marlais - headwaters to confluence with Loughor |  |  | 73 | 7 | 7 | 69.63 |  |  |  | New cello installed in April 2021.
52219 | CSO 19 HALL STREET BRYNAMMAN | BW1402701 |  | SW | West | Garnant - headwaters to confluence with Aman |  |  | 8 | 8 | 8 | 99.35
72317 | 50M D/S FROM CULVERT MEADOWS R'D | BW1402801 |  | SW | West | Gwili - headwaters to tidal limit |  |  | 354.5 | 57 | 52 | 97.76
52251 | 100M D/S R'DBR CWMGWILI (SWO) CARMS | BW1402901 |  | SW | West | Gwili - headwaters to tidal limit |  |  | 827.75 | 94 | 90 | 100
52225 | CAPEL HENDRE SEWAGE SCHEME OVERFLOW | BW1403301 |  | SW | West | Loughor - conf with Marlais to conf with Aman |  |  | 0 | 0 | 0 | 89.01 |  |  |  | Data unreliable from 16/09 to to 25/10/21. Due to static telemetry signal, resolved
71584 | PENYGROES (SWO 4) WATERLO | BW1403401 |  | SW | West | Loughor - conf with Marlais to conf with Aman |  |  | 193.25 | 36 | 36 | 96.89
71309 | CAE BRYN WOODS CSO | BW1403601 |  | SW | West | Loughor - conf with Marlais to conf with Aman |  |  | 273.5 | 67 | 54 | 99.94
52232 | SWO NO 11 NR GLANYRAFON CWMLLY | BW1404001 |  | SW | Swansea | Llynfell - headwaters to confluence wi |  |  | 186 | 63 | 52 | 99.46
72129 | PEN-Y-GROES PS GATE ROAD GORSLAS | BW1404101 |  | SW | South West | Loughor - conf with Marlais to conf with Aman |  |  | 244.25 | 40 | 37 | 100
50621 | GARNSWLLT STW LONGELIN AMMANFORD | BW1404301 |  | SW | South West | Loughor - confluence with Aman to tidal limit |  |  | 5631 | 264 | 264 | 99.99
51149 | Sandy SPS Llanelli | BW2200201 |  | SW | West | Afon Dulais | Burry N |  | 20.5 | 5 | 5 | 24.61 | SFW | 14 in the Year |  | Communications issue - escalated through business as usual process for communications failures. Data unreliable from 10/12/2021 to 14/12/2021 and from 24/12/2021 to 31/12/2021. Due to erratic telemetry signal.
50960 | HALFWAY PS DAFEN LLANELLI CARMS | BW2200401 |  | SW | Central | Dafen - headwaters to tidal limit |  |  | 21.5 | 6 | 6 | 99.96
72281 | YNYS TOMENLLE CSO ISCOED R'D HENDY | BW2200501 |  | SW | West | Dulais - headwaters to confluence with Loughor |  |  | 0.5 | 1 | 1 | 100
52242 | SWO AT HENDY ON LEFT BANK OF R | BW2200701 |  | SW | West | LOUGHOR |  |  | 33.75 | 44 | 20 | 99.23
52243 | YARD BRIDGE CSO SANDY RD PWLL LLAN | BW2200801 |  | SW | West | Afon Dulais, via surface water system | Burry N |  | 1.25 | 2 | 2 | 76.18 |  |  |  | Communications issue, resolved in October 2021.
71832 | HALFWAY AREA CSO Y LLWYN COEDCAE | BW2200901 |  | SW | West | Afon Dafen, via surface water system | Burry N |  | 0 | 0 | 0 | 100 | SFW | 26 in the Year
71716 | St Michael's Church CSO Llanelli Carmarthenshire | BW2201101 |  | SW | Swansea | Dafen - headwaters to tidal limit |  |  | 190.25 | 22 | 22 | 97.57 | SFW | 14 in the Year | YES
52247 | CSO 49 TIR EINON LLWYHENDY LLANELI | BW2201201 |  | SW | West | Afon Dafen | Burry N |  | 31.75 | 24 | 16 | 97.41 | BW & SFW | 5 in Bathing Season OR 14 in the Year | YES
52250 | CSO 15 15M UPSTREAM OF CONFLUENCE | BW2201501 |  | SW | West | Loughor - conf with Marlais to conf with Aman |  |  | 390 | 80 | 77 | 95.45
52253 | CWM MAWR RB NO1 GWENDREATH CATCHMEN | BW2201801 |  | SW | West | Gwendraeth Fawr - headwaters Afan Goch |  |  | 115.75 | 24 | 24 | 92.95
71502 | HEOL WAUN Y CLUN CSO TRIMSARAN | BW2201901 |  | SW | Swansea | Gwendraeth Fawr - Afan Goch to tidal limit |  |  | 0 | 0 | 0 | 100
71580 | ACCESS ROAD TO PONTYBEREM STW | BW2202401 |  | SW | Central | Gwendraeth Fawr - Afan Goch to tidal limit |  |  | 2 | 3 | 2 | 99.9
71205 | PONT HENRI INCLINE INN CSO | BW2202501 |  | SW | West | Gwendraeth Fawr - Afan Goch to tidal limit |  |  | 69.5 | 15 | 15 | 100
51943 | SOC4 PONTYATES AREA CSO | BW2202601 |  | SW | West | Gwendraeth Fawr - Afan Goch to tidal limit |  |  | 362 | 48 | 40 | 99.44
71875 | GARREG SPS LLANGADOG KIDWELLY | BW2202801 |  | SW | Central | Gwendraeth Fach | Gwendrae |  | 221 | 28 | 28 | 100
51173 | SSO AT STATION ROAD P.S. KIDWELLY | BW2202901 |  | SW | Central | Gwendraeth Fach Estuary | Gwendrae |  | 1 | 3 | 3 | 18.12 |  |  |  | Communications issue, resolved in October 2021.
51406 | TYCOCH SEWAGE PUMPING STATION KIDW | BW2203001 |  | SW | Central | Unnamed tributary of Gwendraeth Fawr | Gwendrae |  | 505.5 | 77 | 77 | 99.91
50831 | SSO AT ASHBURNHAM P.S. BURRY PORT | BW2203101 |  | SW | Central | Burry Port Harbour via drain | Burry N |  | 29.75 | 13 | 13 | 100 | SFW | 14 in the Year
71376 | CSO Behind 8 Pwll Road, Pwll | BW2203201 |  | SW | West | Barnaby Pil - headwaters to tidal limit |  |  | 182.5 | 16 | 15 | 99.45 | SFW | 14 in the Year | YES
71326 | SWO. BURRY PORT AREA BURRY PORT | BW2203301 |  | SW | West | Canal | Burry N |  | 2.5 | 4 | 4 | 99.73
52271 | SWO. BURRY PORT AREA - INTO O | BW2203601 |  | SW | West | Canal | Burry N |  | 480.5 | 82 | 82 | 99.99 | BW | 5 in Bathing Season | YES
52280 | SWO.BELOW PENYFAN QUARRY(S158) LLAN | BW2204501 |  | SW | West | River Lliedi | Burry N |  | 3.25 | 9 | 3 | 94.13 | BW | 5 in Bathing Season
71831 | CSO BELOW ANDREW STREET BRIDGE LLAN | BW2204701 |  | SW | West | Afon Lliedi | Burry N |  | 12.75 | 3 | 3 | 99.72 | SFW | 14 in the Year
71339 | BUCKLEYS CELLAR CSO LLANELLI | BW2204801 |  | SW | West | Afon Lliedi | Burry N |  | 0 | 0 | 0 | 97.86 | SFW | 14 in the Year
50680 | LLANON STW | BW2205001 |  | SW | South West | Morlais - headwaters to tidal limit |  |  | 2445.25 | 162 | 162 | 99.96
51016 | SSO LLANGENNECH PS CARMS | BW2205101 |  | SW | Central | Morlais - headwaters to tidal limit |  |  | 103.25 | 63 | 63 | 99.98
50872 | SSO. CEFN STYLLE P.S. GOWERTON | BW2300101 |  | SW | Central | Nant Cafngolau - headwaters to tidal limit |  |  | 0 | 0 | 0 | 99.94
52505 | SWO.APX 70YDS U/S R'WAY B'GE U | BW2300201 |  | SW | Swansea | LOUGHOR |  |  | 59 | 24 | 24 | 93.24
51141 | SSO. RHOSOG P.S. (OVERF | BW2300301 |  | SW | Central | LOUGHOR |  |  | 172.75 | 28 | 28 | 99.95
51919 | SWO. 165 YDS DOWNSTREAM OF ISL | BW2300501 |  | SW | Swansea | LOUGHOR |  |  | 596.75 | 112 | 112 | 83.18 |  |  |  | Communications issue from 07/07/ to 03/09/2021, resolved.
52300 | SWO.BACH Y GWREIDDYN FARM PONTLLIW. | BW2300701 |  | SW | Swansea | Lliw - headwaters to confluence with Llan |  |  | 1356.75 | 130 | 130 | 82.7 |  |  |  | Communications issue from 29/09 to 10/11/2021, resolved.
52301 | Gorseinon 2 (S121) Bako CSO | BW2300801 |  | SW | Swansea | Un-named tributary of Afon Lliw |  | Swansea Bay | 10.5 | 3 | 3 | 99.66
52310 | CSO BRYNAFON ROAD GORSEINON SWANSEA | BW2301701 |  | SW | Swansea | Llannant Pill - headwaters to tidal limit |  | Swansea Bay | 37.5 | 11 | 11 | 96.95 | BW | 5 in Bathing Season
71403 | SWO. 60 YARDS U/S CONFLUENCE D | BW2301901 |  | SW | Swansea | Dulais - headwaters to confluence with Loughor |  |  | 14.75 | 2 | 2 | 99.64
51115 | SWO.400 YDS D/S C'LUENCE DULAI | BW2302001 |  | SW | Central | Dulais - headwaters to confluence with Loughor |  |  | 28.75 | 7 | 7 | 98.39
52315 | SWO BRYNMOR RD SOC11 GOWERTON S124 | BW2302201 |  | SW | Swansea | unnamed waterbody at Gowerton |  |  | 29 | 23 | 23 | 90.59
52318 | SWO. YNYSMEUDW WAREHOUSE (SOC | BW2302501 |  | SW | Swansea | Tawe -confluence with Twrch to tidal l |  |  | 408.75 | 65 | 65 | 98.53
72001 | INCO CSO CLYDACH SWANSEA | BW2302601 |  | SW | Swansea | Tawe -confluence with Twrch to tidal l |  |  | 1030 | 128 | 128 | 91.32
72248 | SWO. GODRE'R GRAIG SOC 20. GODRE'R | BW2302801 |  | SW | Swansea | Tawe -confluence with Twrch to tidal l |  |  | 227.5 | 26 | 26 | 99.99
52324 | SWO.CRAIG Y DUKE TREBANOS SOC | BW2303101 |  | SW | Swansea | Tawe -confluence with Twrch to tidal l |  |  | 520.25 | 85 | 62 | 99.14
72249 | OFFICE ROW CAR PARK YSTALYFERA CSO | BW2303401 |  | SW | Swansea | Tawe -confluence with Twrch to tidal l |  |  | 34.5 | 18 | 18 | 99.96
70257 | CSO 21 BRIDGE STREET | BW2303501 |  | SW | Swansea | Twrch - conf with Nant Gwys to conf wi |  |  | 178.25 | 35 | 35 | 100
71206 | CSO 27 BOUNDARY RD BRIDGE GARNANT | BW2303701 |  | SW | West | Garnant - headwaters to confluence with Aman |  |  | 809.75 | 69 | 69 | 69.24 |  |  |  | Communications issue from 25/04/21 to 22/07/21, resolved.
71771 | MOSES ROW CSO RESOLVEN NEATH | BW2900301 |  | SW | Swansea | Neath - conf with Nedd Fechan and Mellte to TL |  |  | 432.5 | 59 | 59 | 99.7
50881 | COMMERCIAL RD PS RESOLVEN NEATH , | BW2900502 |  | South West |  | Neath - conf with Nedd Fechan and Mellte to TL |  |  | 30 | 26 | 26 | 99.97
52341 | CL'ACH BR.RE'VEN SWO 3A RESO | BW2900601 |  | SW | Swansea | Neath - conf with Nedd Fechan and Mellte to TL |  |  | 22 | 32 | 32 | 87.9 |  |  |  | Communications issue, resolved in October 2021.
52342 | YS.MARCH CRYNANT SWO 2C | BW2900701 |  | SW | Swansea | Dulais - headwaters to confluence with River Ne |  |  | 1161.75 | 181 | 181 | 88.78 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
71468 | CSO 103 UNDER R'DBR PONTRHYDYFEN | BW2900801 |  | SW | Swansea | Afon Pelenna |  | Aberafan | 221.75 | 49 | 39 | 99.08
52345 | CSO NO 110 TONMAWR | BW2901001 |  | SW | Swansea | Afon Pelenna |  | Aberafan | 473.25 | 77 | 63 | 92.92
71842 | LONGFORD ROAD CSO LONGFORD ROAD | BW2901101 |  | SW | Swansea | Clydach - headwaters to conf with River Neath |  |  | 47.75 | 12 | 12 | 98.35
52349 | CSO NO 10 30M U/S ROADBRIDGE | BW2901401 |  | SW | West | Clydach - headwaters to conf with River Neath |  |  | 204.25 | 76 | 60 | 99.53
72021 | CSO 8 BRYNCOCH SWO 7B BRYNCOCH | BW2901501 |  | SW | West | Clydach - headwaters to conf with River Neath |  |  | 53.75 | 11 | 10 | 100
70198 | REAR NO 1 DYFFRYN V'W BRYN COCH | BW2901601 |  | SW | Cardiff | Clydach - headwaters to conf with River Neath |  |  | 247.75 | 53 | 42 | 100
52359 | GUNSIGHT OVERFLOW (SWO 11)-NEATH VALLEY | BW2902401 |  | SW | Swansea | RIVER NEATH |  | Aberafan | 23.25 | 21 | 14 | 96.75
51044 | SKEWEN SPS PARK AVENUE LONLAS NEATH | BW2902601 |  | SW | Central | Crymlyn Brook - HW to conf with Tennant Canal |  |  | 309.25 | 106 | 84 | 94.79
71413 | CSO 49 LLANGATWG SCHOOL ABERDULIAS | BW2902801 |  | SW | Swansea | tributary of the Tennant Canal |  | Aberafan | 148.5 | 28 | 24 | 100
52364 | BRYNDULAIS (SWO 2A) | BW2902901 |  | SW | Swansea | Dulais - headwaters to confluence with River Ne |  |  | 1025 | 53 | 53 | 16.85 |  |  |  | Communications issue - access issue
52368 | CSO 32 NR ST JOESEPHS CHURCH | BW2903601 |  | SW | Swansea | Eastland Brook |  | Aberafan | 7.75 | 15 | 7 | 98.63
52369 | CSO 33 CIMLA ROAD CIMLA NEATH | BW2903701 |  | SW | Swansea | Nant Cae'r-bryn - headwaters to conf with Neath |  | Aberafan | 21.5 | 7 | 7 | 99.15
52372 | NANT Y CAFN SWO DULAIS VALLEY | BW2904001 |  | SW | Swansea | Dulais - headwaters to confluence with River Ne |  |  | 1377.75 | 125 | 125 | 99.83
52374 | CSO AT RIVERSIDE ABERKENFIG | BW3200201 |  | SW | Swansea | Ogmore - confluence with Llynfi to tid |  |  | 43.5 | 17 | 15 | 99.12
52123 | BEACH ROAD CSO PORTHCAWL | BW3200301 |  | SW | Swansea | Bristol Channel | Porthcawl | Trecco Bay | 4 | 3 | 2 | 99.66
72133 | REDLANDS CLOSE CSO PENCOED BRIDGEND | BW3201301 |  | SW | Bridgend Hereford & Mid Wales | Ewenny - conf with Ewenny Fach to conf |  |  | 0 | 0 | 0 | 100
52397 | BETTWS ROAD CSO LLANGEINOR | BW3202501 |  | SW | Bridgend Hereford & Mid Wales | Garw - headwaters to confluence with O |  |  | 4128.25 | 229 | 229 | 100
52399 | SWO. VICTORIA STREET PONTYCYMMER (P | BW3202701 |  | SW | Swansea | Garw - headwaters to confluence with O |  |  | 44.75 | 30 | 30 | 99.61
52400 | SWO.MEADOW STREET PONTYCYMMER (POIN | BW3202801 |  | SW | Bridgend Hereford & Mid Wales | Garw - headwaters to confluence with O |  |  | 0 | 0 | 0 | 82.76 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
52401 | FENTON PLACE CSO PONT Y CYMER | BW3202901 |  | SW | Bridgend Hereford & Mid Wales | Garw - headwaters to confluence with O |  |  | 526.75 | 113 | 104 | 100
72134 | BRID OGWR PT 32 ABERKENFIG CSO BR'D | BW3203201 |  | SW | Bridgend Hereford & Mid Wales | Llynfi - Lletty Brongu STW to conf wit |  |  | 22.75 | 10 | 10 | 100
72553 | SWO. TYNYCOED (POINT 30) | BW3203401 |  | SW | Bridgend Hereford & Mid Wales | Ogmore - conf with Garw to confluence |  |  | 3 | 4 | 2 | 99.92
52410 | SWO. CWMFELIN (POINT 26) | BW3203801 |  | SW | Swansea | Llynfi - headwaters to Lletty Brongu S |  |  | 0 | 0 | 0 | 44.65 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
71449 | SWO. BRIDGEND ROAD GARTH (POINT 23) | BW3204101 |  | SW | Bridgend Hereford & Mid Wales | Llynfi - headwaters to Lletty Brongu S |  |  | 27.5 | 21 | 8 | 99.85
52414 | SWO. HEOL FAEN GARTH (POINT 22) | BW3204201 |  | SW | Bridgend Hereford & Mid Wales | Llynfi - headwaters to Lletty Brongu S |  |  | 395.5 | 117 | 101 | 98.07
71512 | SLAUGHTER HOUSE CSO ASSET 52415 | BW3204301 |  | SW | Bridgend Hereford & Mid Wales | Llynfi - headwaters to Lletty Brongu S |  |  | 359.75 | 50 | 50 | 100
73913 | SWO. GREENFIELD STREET (POINT | BW3204501 |  | SW | Bridgend Hereford & Mid Wales | Llynfi - headwaters to Lletty Brongu S |  |  | 3.75 | 7 | 4 | 99.99
52418 | SWO. MAESTEG MARKET (POINT 18) | BW3204601 |  | SW | Bridgend Hereford & Mid Wales | Llynfi - headwaters to Lletty Brongu S |  |  | 0 | 0 | 0 | 65.33 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
71117 | CAERAU STH CSO ASSET 52420 MAESTEG | BW3204901 |  | SW | Bridgend Hereford & Mid Wales | Llynfi - headwaters to Lletty Brongu S |  |  | 414.25 | 54 | 54 | 100
71448 | SPELTER CSO ASSET 52423 | BW3205101 |  | SW | Bridgend Hereford & Mid Wales | Llynfi - headwaters to Lletty Brongu S |  |  | 518 | 81 | 81 | 99.25
52425 | HERMON ROAD CSO ASSET 52425 MAESTEG | BW3205301 |  | SW | Bridgend Hereford & Mid Wales | Llynfi - headwaters to Lletty Brongu S |  |  | 192.75 | 67 | 67 | 100
52426 | SWO. CAERAU SQUARE(POINT 10) | BW3205401 |  | SW | Swansea | Llynfi - headwaters to Lletty Brongu S |  |  | 178.75 | 85 | 85 | 99.01
52427 | CAERAU ROAD CSO ASSET 52427 MAESTEG | BW3205501 |  | SW | Bridgend Hereford & Mid Wales | Llynfi - headwaters to Lletty Brongu S |  |  | 160 | 56 | 56 | 100
72132 | WILDMILL CSO WILDMILL BRIDGEND | BW3206101 |  | SW | Bridgend Hereford & Mid Wales | Garw - headwaters to confluence with O |  |  | 1 | 1 | 1 | 82.8 |  |  |  | Communications issue, resolved in August 2021.
50743 | PENYBONT WWTW PENYBONT | BW3206201 |  | SW | Central | Ogmore Estuary | Porthcawl | Southerndown | 664.25 | 49 | 49 | 99.98 | BW | 5 in Bathing Season
71440 | SWO. E.BANK OPP SWO N'THERN CO | BW3206501 |  | SW | Bridgend Hereford & Mid Wales | Ogwr Fawr - headwaters to confluence w |  |  | 51 | 18 | 10 | 99.73
52438 | OGWR FAWR CSO OGMORE VALE | BW3206601 |  | SW | Swansea | Ogwr Fawr - headwaters to confluence w |  |  | 0 | 0 | 0 | 99.4
71437 | SWO. EAST BANK BEHIND GILEAD C NANT | BW3207001 |  | SW | Bridgend Hereford & Mid Wales | Ogwr Fawr - headwaters to confluence w |  |  | 202.25 | 76 | 59 | 99.33
51132 | SWO. 50 YARDS BELOW SHELL GARA KNEL | BW4100201 |  | South West |  | Oxwich Marsh Stream - headwaters to tidal limit |  |  | 7.75 | 12 | 12 | 23.39 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
51415 | NEW CROFTY C SEWAGE PS CROFTY GOWER | BW4100301 |  | SW | Swansea | Morlais River | Burry S |  | 52 | 20 | 19 | 77.48 | SFW | 14 in the Year | YES | Communications failure from 01/01 - 09/01/2021 and from 20/02 to 25/03/2021. Data unreliable from 04/10 to 21/10/21. Due to erratic telemetry signal.
50915 | DRUMAU FARM BIRCHGROVE RD P.S. SSO | BW4100401 |  | SW | Central | Nant y Fendrod - headwaters to conf with Tawe |  |  | 1080.25 | 97 | 93 | 99.96
50996 | LIMESLADE PUMPING STATION SWANSEA | BW4100901 |  | SW | Central | Limeslade Bay | Swans S | Limeslade | 0.5 | 2 | 0 | 98.5 | BW | 5 in Bathing Season
50961 | SSO. HALFWAY CRYMLYN ROAD P.S. PENT | BW4101101 |  | SW | Central | Crymlyn Brook - HW to conf with Tennant Canal |  |  | 24.75 | 16 | 13 | 100
50969 | HILLEND LLANGENNITH P.S. SSO | BW4101501 |  | SW | Central | UNNAMED STREAM |  | Rhosilli | 5.5 | 2 | 2 | 100
52484 | Trallwyn Community Centre, Llansamlet CSO106 | BW4101701 |  | SW | Swansea | Nant Bran |  | Swansea Bay | 0 | 0 | 0 | 99.73
52462 | PENTRE CHWYTH SW0. (POINT 100 | BW4101901 |  | SW | Swansea | Nant y Fendrod - headwaters to conf with Tawe |  |  | 59 | 25 | 25 | 98.06
72736 | CSO NO 34 REAR OF FURZELAND DRIVE S | BW4102301 |  | SW | Swansea | An un-named tributary of the River Clyne | Swans W | Swansea Bay | 145 | 30 | 28 | 99.26 | BW | 5 in Bathing Season
50944 | SSO.OUTLET OF GLAIS P.S. | BW4102801 |  | SW | Central | Tawe -confluence with Twrch to tidal l |  |  | 87.5 | 23 | 23 | 99.98
71419 | CSO 103 SAMLET ROAD LLANSAMLET | BW4103101 |  | SW | Swansea | Nant y Fendrod - headwaters to conf with Tawe |  |  | 221.25 | 33 | 33 | 95.68
71453 | CSO 104 BETHEL ROAD LLANSAMLET | BW4104101 |  | SW | Swansea | Nant y Fendrod - headwaters to conf with Tawe |  |  | 0 | 0 | 0 | 6.31 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
52490 | SWO. YNYSTAWE (POINT 86 NEW MA | BW4104701 |  | SW | Swansea | Tawe -confluence with Twrch to tidal l |  |  | 1231.25 | 168 | 150 | 95.25
73413 | SSO YNYSFORGAN ROUNDABOUT | BW4104901 |  | SW | Swansea | An unnamed tributary of the River Tawe |  | Swansea Bay | 0 | 0 | 0 | 100
52493 | SWO.NEAR CHEMICAL RD. MORRISTON (PO | BW4105001 |  | SW | Swansea | Tawe -confluence with Twrch to tidal l |  |  | 0 | 0 | 0 | 99.73
52497 | CSO 70 A4067 NTHBND LANDORE SWANSEA | BW4105401 |  | SW | Swansea | Tawe - conf with Nant Cwmgelli to tida |  |  | 322 | 90 | 90 | 100
71400 | Blaen-Y-Maes (Point 65) CSO, Cranmer Court | BW4105701 |  | SW | Swansea | Un-named tributary of Afon Llan |  | Swansea Bay | 6 | 8 | 7 | 83.25 |  |  |  | Communications issue, resolved in August 2021.
52502 | CADLE MILL POINT 47 CSO | BW4105901 |  | SW | Swansea | Un-named tributary of Afon Llan |  | Swansea Bay | 6 | 7 | 7 | 97.46
70229 | Station Rd CSO, Pen Y Cwm | BW4106601 |  | SW | Swansea | Unnamed tributary of Afon Llan |  | Swansea Bay | 17 | 24 | 24 | 93.42
71023 | ELMGROVE ROAD CSO | BW4108401 |  | SW | Swansea | Washinghouse Brook | Swans W |  | 5 | 4 | 4 | 38.56 | BW | 5 in Bathing Season |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
72535 | SSO. PENCLAWDD SEWERAGE SCHEME | BW4108601 |  | SW | Swansea | LOUGHOR ESTUARY | Burry S |  | 741.25 | 96 | 77 | 96.02
72030 | PONTARDAWE LEIS CENTRE CSO SWANSEA | BW4108701 |  | SW | Swansea | Tawe -confluence with Twrch to tidal l |  |  | 266.25 | 62 | 62 | 99.02
71431 | SWO AT HILLSIDE AVENUE LLANHARAN | BW4200601 |  | SE | South East | Ewenny Fach - headwaters to confluence with Ewenny |  |  | 410.75 | 112 | 112 | 97.71
2364 | BAGILLT VERGE OFF MANOR DRIVE - SSO | CB3090FW |  | N | North |  |  |  | 0.5 | 2 | 2 | 99.93
687 | Rhydymwyn WwTW Storm overflow | CB3191CA |  | N | North East |  |  |  | 11.75 | 1 | 1 | 99.97
74791 | Howe Circle, Ringland, Newport, NP19 9GP | CB3191FY |  | SE | South East | Monks Ditch - source to Wainbridge |  |  | 0 | 0 | 0 | 99.38
71458 | NEAR DELFFORDD PONTARDAWE | CB3191HQ |  | SW | West | Tawe -confluence with Twrch to tidal limit |  |  | 0 | 0 | 0 | 100
32051 | BLACKWOOD OAKDALE RHIW HILL BOTTOM OF RE | CB3191ZW |  | SE | South East | Sirhowy R - Rock Villas to conf Afon Ebwy |  |  | 197.25 | 63 | 63 | 98.91
32053 | BLACKWOOD CWMGELLI | CB3192CD |  | SE | South East | Sirhowy R - Rock Villas to conf Afon Ebwy |  |  | 116.25 | 38 | 27 | 99.26
71406 | REAR OF LONLAS STATION ROAD ABERCRAVE | CB3192FQ |  | SW | West | Tawe - conf with Nant Llech to conf with Giedd |  |  | 45.5 | 25 | 21 | 96.79
50714 | Mydroilyn WwTW Storm Overflow | CB3192HB |  | SW | South West | Mydyr - headwaters to confluence with Aeron |  |  | 45.75 | 3 | 3 | 98.01
51193 | Heol Dulais CSO, Birchgrove | CB3192ZR |  | SW | West |  |  |  | 11 | 8 | 8 | 99.35
72575 | STATION RD GWYNFRYNLEN CSO | CB3193CJ |  | SW | West | Tawe - conf with Nant Llech to conf with Giedd |  |  | 572.25 | 76 | 71 | 96.93
50974 | Houghton SPS | CB3193FB |  | SW | South West |  |  |  | 0 | 0 | 0 | 91.92
71454 | O/S 17 GLANTAWE ROW YSTRADGYNLAIS | CB3193ZY |  | SW | West | Tawe - conf with Giedd to confluence with Twrch |  |  | 275.75 | 59 | 59 | 99.04
72661 | SWN YR AFON CSO, Ystradgynlais | CB3194CP |  | SW | West | Tawe - conf with Nant Llech to conf with Giedd |  |  | 250 | 60 | 53 | 98.96
52419 | 27 Talbot Street CSO, Maesteg | CB3198ZG |  | SW | West | Llynfi - headwaters to Lletty Brongu STW |  |  | 2683 | 271 | 271 | 97.01
72040 | ABERRHONDDA ROAD CSO, PORTH | CB3199CH |  | SE | South East | Afon Rhondda Fach - source to conf Rhondda R |  |  | - | - | - | 0 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
32571 | TALBOT GREEN HEOL MILES REAR OF NO 24 | CB3199FZ |  | SE | South East | Ely R - conf Nant Mychydd to conf Nant Clun |  |  | 6 | 10 | 10 | 66.46 |  |  |  | Communications issue, resolved in August 2021.
71325 | Brecon Supermarket CSO | CB3292CJ |  | SW | West | R Usk - conf Afon Senni to conf Afon Crawnon |  |  | 51.5 | 46 | 46 | 89.38 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
72331 | Ty-Isaf Road CSO | CB3292FB |  | SW | West | Ogmore - confluence with Llynfi to tidal limit |  |  | 7.75 | 7 | 7 | 98.74
795 | DOLGELLAU SEWAGE TREATMENT WORKS | CB3297CK |  | North |  | Wnion - lower |  |  | 3653.5 | 247 | 247 | 99.7
71426 | Rear of Margam Rd Depot | CB3298FZ |  | SW | West | Ffrwd Wyllt - headwaters to tidal limit |  |  | 0 | 0 | 0 | 98.46
70383 | Cynon Terrace CSO, Penrhiwceiber, Mountain Ash, Rhondda Cynon TafF, CF45 3SU | CB3790HT |  | SE | South East | R Cynon - conf Aman R to conf R Taff |  |  | 23.5 | 31 | 18 | 99.63
895 | LLANYSTUMDWY FINAL EFFLUENT | CG0014301 |  | N | North West | Dwyfawr - lower |  |  | 0.25 | 1 | 0 | 99.83
2112 | BRYNCIR STW | CG0014501 |  | N | North West | Dwyfach |  |  | 384.5 | 92 | 80 | 99.9
3167 | TYN Y GROES STW - STORM OVERFL | CG0015501 |  | N | North | River Conway |  |  | 58.25 | 19 | 11 | 99.73
496 | LLANGAFFO STW SSO | CG0019202 |  | N | North West | Braint - lower |  |  | 480 | 138 | 138 | 99.96
70651 | ABERGYNOLWYN STW (SETTLED STORM) | CG0029102 |  | N | North West | Dysynni - upper |  |  | 177.25 | 40 | 37 | 100
470 | EGLWYSBACH STW | CG0030702 |  | N | North West | Hiraethlyn |  |  | 1751 | 85 | 85 | 100
916 | MYNYTHO STW - STORM OVERFLOW | CG0030802 |  | N | North West | Un-named near Soch catchment |  |  | 1341.25 | 127 | 121 | 92.33 |  |  |  | Data unreliable from 24/06 to 21/07/2021 Due to static telemetry signal, resolved
70653 | LLAN LLANBRYNMAIR PS | CG0033301 | [6 empty] | 800.25 | 48 | 48 | 84.41 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
2085 | BETTWYS YN RHOS SPORTS GROUND | CG0035501 |  | N | North | Dulas - un-named tributary |  |  | 2520 | 140 | 128 | 71.34 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
2166 | MACHYNLLETH - POPULAR ROAD SSO | CG0041001 |  | N | North West | Dyfi - tidal limit to Afon Twymyn | Dyfi |  | 22 | 42 | 17 | 95.73
2167 | MACHYNLLETH - DOLL STREET SSO | CG0041101 |  | N | North West | Dyfi - tidal limit to Afon Twymyn | Dyfi |  | 252.5 | 60 | 40 | 99.16
71882 | HEOL PENRALLT CSO | CG0041201 |  | N | North West | Dyfi - tidal limit to Afon Twymyn | Dyfi |  | 0 | 0 | 0 | 100
3058 | PENRHOS CAMP STW - SCREENED ST | CG0041302 |  | N | North West | Penrhos |  |  | 60.75 | 15 | 12 | 100
801 | DYFFRYN ARDUDWY WWTW STORM | CG0043702 |  | N | North West | Ardudwy Marsh Main Drain |  | Dyffryn | 782.75 | 60 | 60 | 99.97
972 | PORTHMADOG STW STORM STORAGE PORT | CG0051702 |  | N | North West | Glaslyn Estuary within Glaslyn Marshes | Glaslyn |  | 4.75 | 4 | 3 | 99.97
2113 | PORTHMADOG - LOMBARD STREET SS | CG0051801 |  | N | North West | unnamed stream | Glaslyn |  | 6.5 | 19 | 19 | 80.57 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
971 | SNOWDON STREET PS PORTHMADOG | CG0051901 |  | N | North West | The "Cyt Bach" surface watercourse adjacent to Snowdon Street | Glaslyn |  | 438.75 | 104 | 104 | 99.98
622 | TREMADOG SSO | CG0052001 |  | N | North West | Cyt Stream | Glaslyn |  | 6.5 | 10 | 6 | 100
1283 | PONT LLANDEGFAN SEWAGE PUMPING STAT | CG0055401 |  | N | North West | Afon Cadnant | Menai E |  | 1312.25 | 90 | 89 | 98.98
877 | LLANFECHELL PUMPING STATION | CG0058201 |  | N | North West | Wygyr |  | Cemaes | 1025.75 | 78 | 76 | 100
3155 | GWALCHMAI STW | CG0058303 |  | N | North West | Ffraw |  |  | 9.5 | 16 | 11 | 99.99
2749 | LLANFFESTINIOG STW | CG0058802 |  | N | North West | Cynfal |  |  | 2590 | 307 | 275 | 99.99
2749 | LLANFFESTINIOG STW | CG0058803 |  | N | North West | Cynfal |  |  | 1081.75 | 116 | 105 | 99.99
541 | LOWER CORRIS STW | CG0061901 |  | North |  | Dulas North |  |  | 1219.25 | 89 | 89 | 100
474 | LLANRWST STW LLANRWST CONWY | CG0062001 |  | N | North West | Conwy - tidal limit to Merddwr | Conwy/Conwy Bridge |  | 887.75 | 85 | 85 | 99.97
560 | TALSARNAU PS | CG0071501 |  | N | North West | Dwyryd estuary south |  |  | 269.25 | 63 | 63 | 99.99
2043 | LLANBERIS SSO NO. 2 | CG0072703 |  | N | North | Nant Peris |  |  | 86.5 | 36 | 21 | 99.26
647 | ESGAIRGEILIOG STW | CG0072801 |  | N | North West | Dulas North |  |  | 388.75 | 35 | 35 | 99.98
521 | LLANRUG WWTW STORM | CG0073902 |  | N | North West | Seiont - lower |  |  | 1631.75 | 120 | 120 | 96.39
888 | PONT RHYTHALLT PUMPING STATION | CG0074001 |  | N | North West | Seiont - lower | Menai Strait (West) |  | 1333.75 | 132 | 132 | 100
2046 | CWMYGLO SSO | CG0074101 |  | N | North West | Nant Peris |  |  | 154.25 | 21 | 20 | 43.42 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
2007 | CAPEL CURIG SD.SCHEME | CG0074201 |  | N | North West | Llugwy - Conwy to Nant gwryd |  |  | 3519.75 | 191 | 187 | 81.89 |  |  |  | Data unreliable from 28/07/2021 to 01/10/2021. Due to static telemetry signal. Instrumentation task escalated through business as usual for instrumentation defect.
527 | PONTLLYFNI STW - SSO PONTLLYFNI , | CG0074602 |  | N | North West | Llyfni |  |  | 731.25 | 52 | 52 | 99.92
3027 | DOLGARROG SSO NO. 2 | CG0075601 |  | N | North West | CONWY |  |  | 1250.75 | 86 | 83 | 99.74
72329 | DOLGARROG SSO | CG0075701 |  | N | North West | CONWY |  |  | 99.75 | 37 | 28 | 99.98
2047 | CAERNARFON - DORLAN GOCH SSO N CARM | CG0076901 |  | N | North West | Llifon |  |  | 629.5 | 114 | 114 | 89.27 |  |  |  | Communications issue from 10/01/ to 06/02/21 and from29/12/21 to 31/12/2021, resolved.
72315 | CAERNARFON - LLWYN GWALCH SSO GROES | CG0076902 |  | N | North West | Llifon |  |  | 172.5 | 26 | 26 | 99.8
2049 | CAERNARFON - RHOSTRYFAN SSO NO | CG0076903 |  | N | North West | Gwyrfai |  |  | 188 | 71 | 71 | 98.59
72260 | CAERNARFON - RHOSTRYFAN SSO NO | CG0076904 |  | N | North West | Carrog |  |  | 314.25 | 71 | 60 | 100
2051 | HEN GASTELL NO.5 - SSO | CG0076905 |  | N | North West | Carrog |  |  | 481.25 | 83 | 83 | 98.65
2052 | CAERNARFON - GLANRHYD SSO NO. | CG0076906 |  | N | North West | Afon Rhyd | Menai F |  | 274.25 | 102 | 85 | 99.01
2053 | CAERNARFON - BONTNEWYDD SSO NO | CG0076907 |  | N | North West | Gwyrfai |  |  | 704 | 111 | 84 | 97.69
2054 | CAERNARFON - BONTNEWYDD SSO NO | CG0076908 |  | N | North West | Gwyrfai |  |  | 118 | 58 | 42 | 98.02
3143 | LLANFAIRFECHAN SSO NO. 1 | CG0077101 |  | N | North West | Afon Llanfairfechan | Menai E | Llanfairfech | 147.25 | 43 | 28 | 94.18 | BW | 5 in Bathing Season | YES
497 | LLANGEFNI WWTW STORM OVERFLOW | CG0078002 |  | N | North West | Cefni - Ceint to Cefni reservoir |  |  | 40.5 | 46 | 46 | 99.9
3161 | LLANFAGLAN WWTW STORM OVERFLOW | CG0078102 |  | N | North West | Gwyrfai | Menai F |  | 582 | 63 | 59 | 99.98
2940 | CAERNARFON WWTW STORM TANKS | CG0078502 |  | N | North West | Afon Seiont | Menai W |  | 30.75 | 42 | 28 | 99.96
511 | CAERNARFON WWTW INLET PUMP ST 6MM | CG0078601 |  | N | North West | Afon Seiont | Menai W |  | 306 | 85 | 85 | 99.96
607 | CAERNARFON BANK QUAY PS | CG0078603 |  | N | North West | Menai Stait | Menai W |  | 0 | 0 | 0 | 99.96
2291 | SSO AT MILL LANE CAERNARFON | CG0078606 |  | N | North West | Afon Seiont | Menai W |  | 254.25 | 93 | 75 | 100
2947 | LLANFAIR PG WWTW | CG0081201 |  | N | North West | Menai Strait | Menai E |  | 698.75 | 111 | 111 | 100
3144 | LLANFAIRPWLL SSO NO. 2 | CG0081202 |  | N | North West | Menai Strait | Menai E |  | 0 | 0 | 0 | 23.66 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
891 | LLANSADWRN PS | CG0082401 |  | N | North West | Cadnant |  |  | 0 | 0 | 0 | 100
2741 | PENMAENPOOL PS | CG0082601 |  | N | North West | Wnion - lower |  |  | 18.75 | 4 | 4 | 100
1005 | LLANELLTYD SSO | CG0082701 |  | N | North West | Mawddach - lower |  |  | 10 | 8 | 8 | 97.64
72657 | PENMAENPOOL PS | CG0082801 |  | N | North West | Wnion - lower |  |  | 701.5 | 107 | 97 | 97.77
2151 | LLANELLTYD PS | CG0082901 |  | N | North West | MAWDDACH |  |  | 1741 | 100 | 100 | 99.18
555 | MACHYNLLETH WWTW (STORM OUTFALL) | CG0083002 |  | N | North West | Dyfi - tidal limit to Afon Twymyn |  | Aberdyfi | 733.25 | 94 | 94 | 100
2816 | MACHYNLLETH STW | CG0083004 |  | North |  | Dyfi - tidal limit to Afon Twymyn |  |  | 0.25 | 1 | 1 | 99.59
555 | MACHYNLLETH - GARSIWN DITCH SS | CG0083101 |  | North |  | Dyfi - tidal limit to Afon Twymyn |  |  | 12.5 | 2 | 2 | 100
70545 | BLAENAU FFESTINIOG WWTW (STORM) | CG0083402 |  | N | North West | Goedol |  |  | 2805 | 166 | 166 | 99.84
3279 | LAND OPP GLANLLYN NR OAKLEY SQUARE | CG0083505 |  | N | North West | Goedol |  |  | 581.5 | 98 | 98 | 100
2999 | TREGARTH WWTW STORM TANKS | CG0083802 |  | N | North West | Ogwen - lower |  |  | 2750 | 140 | 140 | 100
612 | FRON OGWEN PS | CG0083901 |  | N | North West | Ogwen - lower | Menai Strait (East) |  | 1856.25 | 110 | 110 | 99.83
1017 | TREFRIW STW | CG0084101 |  | N | North | CONWY |  |  | 1322 | 94 | 94 | 100
2004 | TREFRIW STW | CG0084102 |  | N | North | CONWY |  |  | 14.5 | 4 | 4 | 100
557 | PENRHYNDEUDRAETH OUTFALL-SCREE | CG0084502 |  | North |  | Glaslyn |  |  | 574.5 | 69 | 69 | 99.96
71654 | BETHEL SEWAGE TRANSFER PS | CG0085702 |  | N | North West | Unnamed tributary of Afon Cadnant | Menai W |  | 3415.5 | 185 | 184 | 98.68
2578 | BETHEL SSO NO. 2 | CG0085703 |  | N | North West | Afon Cadnant | Menai W |  | 0.25 | 1 | 0 | 99.45
3320 | BETHEL SSO NO. 3 | CG0085704 |  | N | North West | Afon Cadnant | Menai W |  | 60.75 | 19 | 19 | 99.95
980 | RHIWLAS STW | CG0086002 |  | N | North West | Cegin |  |  | 463 | 114 | 93 | 99.94
2767 | BRONABER STW | CG0086702 |  | N | North West | Eden - upper |  |  | 339.25 | 35 | 33 | 100
1291 | COMMINS COCH PUMPING STATION CSO | CG0087402 |  | N | North West |  |  |  | 2790.25 | 132 | 130 | 86.57 |  |  |  | Data unreliable from 13/11 to 31/12/2021. Due to static telemetry signal. Instrumentation task escalated through business as usual for instrumentation defect.
519 | LLANLLYFNI STW | CG0087502 |  | N | North West | Llyfni |  |  | 2521.25 | 195 | 188 | 99.77
2303 | CAERNARFON - PENYGROES SSO NO. | CG0087601 |  | N | North West | Llyfni |  |  | 299.75 | 121 | 121 | 98.21
2058 | CAERNARFON - PENYGROES SSO NO. | CG0087602 |  | N | North West | Llyfni |  |  | 166.25 | 67 | 67 | 100
619 | TALYSARN NO 3 - SSO | CG0087603 |  | N | North West | Llyfni |  |  | 0 | 0 | 0 | 93.49
72047 | TALYSARN NO 4 - SSO | CG0087604 |  | N | North | Llyfni |  |  | 437.75 | 81 | 81 | 99.98
2062 | NANTLLE NO 5-SSO | CG0087605 |  | N | North West | Llyfni |  |  | 539.25 | 77 | 57 | 98.62
514 | LLANBERIS STW (STORM) LLANBERIS | CG0089101 | [6 empty] | 1135.75 | 132 | 132 | 99.89
72012 | STAYLITTLE LANE SSO | CG0090401 |  | N | North West | Wnion - lower |  |  | 372.75 | 64 | 64 | 100
760 | PONT Y BRENIN PS | CG0091701 |  | N | North West | Afon y Brenin | Menai E |  | 64.75 | 12 | 10 | 100
896 | LLEINIOG PS | CG0091801 |  | N | North West | Menai Strait | Menai E |  | 278 | 50 | 49 | 99.99
2155 | MARIAN MAWR CSO | CG0092201 |  | N | North West | Wnion - lower | Mawddach |  | 187.75 | 45 | 45 | 100
2244 | HENDRE ROAD SSO CONWY | CG0094301 |  | N | North West | Afon Gyffin | Conwy |  | 3.25 | 7 | 1 | 98.82
1354 | GYFFIN PS MORFA BACH CONWY | CG0094401 |  | N | North West | CONWY | Conwy/Conwy Bridge |  | 0 | 0 | 0 | 99.79
2011 | GOLF CLUB HOUSE PS B BETTWS Y COE | CG0099101 |  | N | North West | Llugwy - Conwy to Nant gwryd |  |  | 1264.25 | 92 | 91 | 100
71995 | WATERLOO PUMPING STATION | CG0099301 |  | N | North West | Conwy - tidal limit to Merddwr |  |  | 209.5 | 30 | 27 | 99.36
1375 | PENMAENMAWR WWTW PENMAENMAWR | CG0099501 |  | N | North West | Afon Gyrach | Conwy | Penmaenmawr | 15.25 | 6 | 6 | 99.96 | BW | 5 in Bathing Season
3116 | IND ESTATE LLANDUDNO JUNCTION GLAN | CG0105301 |  | N | North West | unnamed watercourse | Conwy |  | 0.25 | 1 | 0 | 99.99 | BW | 5 in Bathing Season
71592 | FRIOG SEWAGE PUMPING STATION | CG0107601 |  | N | North West | unnamed watercourse | Mawddach | Fairbourne | 67.25 | 5 | 5 | 99.98
71590 | BRYNCOCH SEWAGE PUMPING STATION | CG0109301 |  | N | North West | unnamed watercourse | Mawddach | Fairbourne | 117.25 | 10 | 9 | 99.03
2158 | LLANFACHRETH STW (STORM) | CG0110902 |  | N | North West | Mawddach - lower |  |  | 48.25 | 14 | 7 | 100
71594 | MAWDDACH CRESCENT PUMPING STATION | CG0112001 |  | N | North West | Mawddach Estuary | Mawddach |  | 59.25 | 6 | 6 | 100
71295 | ABERGWYNGREGYN PUMPING STATION | CG0113902 |  | N | North West | Menai Strait | Menai E |  | 943 | 48 | 48 | 99.8 | BW | 5 in Bathing Season
482 | Bodedern WwTW | CG0114002 |  | North |  | Crigyll/Caradog catchment - Caergeiliog |  |  | 14.75 | 5 | 5 | 100
3169 | GAERWEN WWTW STORM | CG0114102 |  | N | North West | Cefni - tidal limit to Ceint |  |  | 116.25 | 11 | 11 | 99.48
848 | LLANBRYNMAIR STW LLANBRYNMAIR | CG0114202 |  | N | North West | Iaen - lower |  |  | 5413 | 276 | 276 | 99.98
3159 | LLANERCHYMEDD STW | CG0114505 |  | N | North West | Goch Dulas |  |  | 0 | 0 | 0 | 99.87
3276 | LLAN PENMACHNO STW - SCREENED | CG0114602 |  | N | North West | Machno |  |  | 1074 | 82 | 80 | 99.99
499 | MALLTRAETH WWTW - STORM | CG0115102 |  | N | North West | Cefni Estuary | Mawddach |  | 79.5 | 27 | 17 | 99.69
2251 | DEGANWY ROAD DEGANWY | CG0127101 |  | N | North West | Conwy Estuary | Conwy | Llandudno W | 5.5 | 10 | 10 | 99.68 | BW | 5 in Bathing Season
73445 | BARMOUTH WWTW OUTFALL TO MLWS | CG0129901 |  | N | North West | Cardigan Bay North | Mawddach | Barmouth | 25.75 | 16 | 16 | 99.67
1318 | BARMOUTH HARBOUR PUMPING STATION | CG0130001 |  | N | North West | Mawddach Estuary | Mawddach | Barmouth | 24.75 | 15 | 11 | 100 | BW | 5 in Bathing Season
2065 | WAUNFAWR STW (STORM) | CG0134002 |  | N | North West | Gwyrfai |  |  | 1459.5 | 102 | 102 | 100
944 | PENISARWAUN WWTW | CG0134102 |  | N | North West | Seiont - lower |  |  | 827.75 | 126 | 111 | 100
2780 | DEINIOLEN - CLWT Y BONT - SSO | CG0134201 |  | N | North West | Caledffrwd |  |  | 1.75 | 1 | 1 | 99.89
2306 | DEINIOLEN - SSO | CG0134501 |  | N | North East | Caledffrwd |  |  | 820.75 | 130 | 130 | 97.8
71623 | GLAN Y MOR PUMPING STATION | CG0137301 |  | N | North West | Nant Garreg Ddu | Conwy |  | 0.25 | 1 | 0 | 100
2351 | LLYSFAEN | CG0137801 |  | N | North West | Irish Sea | Llanddulas |  | 0.25 | 1 | 0 | 99.45 | BW | 5 in Bathing Season
71273 | LLANBEGROG SPS LLANBEDROG | CG0138501 |  | N | North West | Tremadog Bay |  |  | 645.5 | 37 | 37 | 99.98
71769 | NEFYN PUMPING STATION | CG0138901 |  | N | North West | Caernarfon Bay |  | Morfa Nefyn | 1381 | 148 | 148 | 99.9
3131 | BONTDDU STW | CG0139002 |  | N | North West | Afon Cwmllechen | Mawddach |  | 1503.75 | 123 | 121 | 99.94
2086 | MARINE RD CSO MARINE RD COLWYN BAY | CG0139301 |  | N | North West | Colwyn Bay | Rhos on S | Colwyn Bay | 0 | 0 | 0 | 99.45 | BW | 5 in Bathing Season
3323 | BEACH ROAD CSO BEACH RD COLWYN | CG0139401 |  | N | North West | North Wales |  | Colwyn Bay | 60.75 | 25 | 25 | 85.96 | BW | 5 in Bathing Season | YES | Communications issue, resolved in December 2021.
71873 | TURKEY SHORE PS HOLYHEAD ANGLESEY | CG0139601 |  | N | North West | Holyhead Bay |  |  | 223.5 | 48 | 48 | 99.97
71846 | ANGLESEY ARMS PUMPING STATION | CG0139701 |  | N | North West | Afon Seiont | Menai W |  | 0 | 0 | 0 | 17.74 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
71870 | HIBERNIA ROW PUMPING STATION | CG0140201 |  | North |  | Holyhead Bay |  |  | 3 | 1 | 1 | 85.08 |  |  |  | EDM installed in February 2021.
71871 | WATERSIDE PUMPING STATION | CG0140401 |  | N | North West | Holyhead Bay |  |  | 9.5 | 35 | 35 | 84.87 |  |  |  | Discharge mechanism revised. Reliable data from 25/02/2021
71874 | MORAWELON SEWAGE PUMPING STATION | CG0140901 |  | N | North West | Holyhead Bay |  |  | 365.5 | 38 | 38 | 100
70027 | GLAN CONWY SPS | CG0141201 |  | N | North West | Afon Conwy | Conwy |  | 811 | 50 | 50 | 99.58 | BW | 5 in Bathing Season | YES
3117 | LLANDDULAS PS | CG0141301 |  | N | North East | Liverpool Bay | Llanddulas | Abergele (Pensarn) | 188.5 | 104 | 104 | 100 | BW | 5 in Bathing Season | YES
1377 | PENRHYN BAY PS MORFA RD PENRHYN BAY | CG0141601 |  | N | North West | Coastal Waters of Penrhyn Bay | Rhos on S |  | 237.75 | 34 | 34 | 99.99 | BW | 5 in Bathing Season
3303 | MORFA PS MORFA DRIVE MORFA CONWY | CG0141901 |  | N | North West | Afon Conwy | Conwy |  | 92.25 | 54 | 54 | 99.92 | BW | 5 in Bathing Season | YES
3029 | WEST SHORE PS ABBEY ROAD LLANDU | CG0142301 |  | N | North West | CONWY | Conwy |  | 186.5 | 64 | 64 | 99.98 | BW | 5 in Bathing Season | YES
72165 | LLANEILIAN AMLWCH | CG0143701 |  | N | North West | Anglesey North |  |  | 285.75 | 28 | 28 | 62.81 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
71238 | RHOSNEIGR STW (SETTLED STORM/EMERGE | CG0144402 |  | N | North West | Crigyll |  |  | 159.5 | 22 | 22 | 78.71 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
71888 | GIMBLET ROCK TIDAL TANK PWLLHELI | CG0144701 |  | N | North West | Afon Erch |  | Pwllheli | 0 | 0 | 0 | 99.97
969 | PORTH Y FELIN PUMPING STATION | CG0145701 |  | N | North West | Holyhead Bay |  |  | 783.5 | 56 | 56 | 95.07
2220 | AMLWCH PORT P.S. | CG0145801 |  | N | North | Goch Amlwch |  |  | 103.75 | 20 | 16 | 99.73
743 | BULL BAY P.S. | CG0145901 |  | N | North West | Goch Amlwch |  |  | 513.5 | 72 | 64 | 100
1271 | WEST END PS BEAUMARIS ANGLESEY | CG0146301 |  | N | North West | Menai Strait | Menai E |  | 73.25 | 24 | 24 | 100
976 | RHIANFA PS LLANDEGFAN | CG0146401 |  | N | North West | Menai Strait | Menai E |  | 87.5 | 23 | 18 | 100
1270 | GLYN GARTH PS LLANDEGFAN | CG0146501 |  | N | North West | Menai Strait | Menai E |  | 85.75 | 17 | 17 | 100
73056 | FOUR MILE BRIDGE PUMPING STATION | CG0146801 |  | N | North West | Holyhead Strait |  |  | 901.75 | 60 | 59 | 100
71869 | GORAD PS GORAD NR VALLEY ANGLE | CG0146901 |  | N | North West | Un-named - Crigyll/Caradog catchment |  |  | 91.75 | 30 | 26 | 100
2229 | CEMAES PS/BALANCING TANK CEMAES | CG0147001 |  | N | North West | Anglesey North |  | Cemaes | 637.25 | 42 | 41 | 99.78
639 | WATERLOO PORT SEWAGE PUMPING ST | CG0147101 |  | N | North West | Menai Strait | Menai W |  | 0.25 | 1 | 0 | 98.41
934 | NEWLANDS BEACH PS VALLEY ANGLE | CG0147201 |  | N | North West | Un-named - Crigyll/Caradog catchment |  |  | 0 | 0 | 0 | 100
71867 | PENRHOS BEACH PUMPING STATION | CG0147301 |  | N | North West | Holyhead Bay |  |  | 0.25 | 1 | 0 | 97.19
2234 | COASTGUARD CSO | CG0147701 |  | N | North West | Holyhead Bay |  |  | 195 | 69 | 69 | 99.97
913 | MALLTRAETH VILLAGE PUMPING STATION and CSO | CG0147801 |  | N | North West | Afon Cefni upstream of tidal gates | Malltraeth |  | - | - | - | 0 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
782 | CYNLAI PS LLANGOED ANGLESEY | CG0147901 |  | N | North West | Coastal Waters | Menai E |  | 9.25 | 5 | 5 | 97.97
2015 | PENRHYN HILL PENRHYN BAY | CG0148101 |  | N | North West | Coastal Waters | Rhos on S |  | - | - | - | 0 | BW | 5 in Bathing Season |  | Communications issue - access issue
1822 | PENMAENMAWR PROMENADE PS | CG0148301 |  | N | North West | Coastal Waters |  | Penmaenmawr | 34.5 | 18 | 18 | 100 | BW | 5 in Bathing Season | YES
2150 | MAENTWROG | CG0150101 |  | N | North | Dwyryd - lower |  |  | - | - | - | 0 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
2120 | AMMANDA TERRACE BORTH Y GEST PORTHM | CG0150301 |  | N | North West | Afon Glaslyn Estuary | Glaslyn |  | 0 | 0 | 0 | 66.88 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
729 | BORTH Y GES PS | CG0150401 |  | N | North West | Afon Glaslyn | Glaslyn |  | 59.25 | 26 | 26 | 97.67
645 | BRITANNIA PS | CG0150601 |  | N | North West | Afon Glaslyn | Glaslyn |  | 49.25 | 7 | 7 | 100
609 | ABERDARON PS | CG0150701 |  | N | North West | Afon Daron |  | Aberdaron | 152 | 30 | 30 | 99.98 | BW | 5 in Bathing Season
601 | ABERSOCH HARBOUR PUMPING STATION | CG0150801 |  | N | North West | Afon Soch |  | Abersoch | 0 | 0 | 0 | 99.97 | BW | 5 in Bathing Season
685 | LON COB BACH PS PWLLHELI | CG0151001 |  | N | North West | Afon Rhyd Hir |  | Pwllheli | 303.25 | 46 | 44 | 98.81
2126 | BRIDGE GARAGE PWLLHELI | CG0151101 |  | N | North West | Afon Erch |  | Pwllheli | 0 | 0 | 0 | 99.45
822 | GLAN Y DON PS PWLLHELI | CG0151201 |  | N | North West | Afon Erch |  | Pwllheli | 13.75 | 5 | 4 | 99.48
625 | MORFA GARREG PS PWLLHELI | CG0151301 |  | N | North West | Afon Erch |  | Pwllheli | 0 | 0 | 0 | 99.98
3102 | DALE ROAD STORM PS LLANDUDNO | CG0152501 |  | N | North West | Wydden |  |  | 892 | 204 | 204 | 99.95
71596 | WESLEYAN TERRACE SEWAGE PUMPING ST | CG0155701 |  | N | North West | unnamed watercourse | Mawddach |  | 58.75 | 4 | 4 | 99.97
71595 | ST MARY'S SEWAGE PUMPING STATION | CG0156601 |  | N | North West | unnamed watercourse | Mawddach |  | 89.25 | 27 | 11 | 99.95
2240 | PENRHYN BAY LLANDUNDNO ROAD - | CG0162101 |  | N | North West | Afon Ganol | Rhos on S |  | 72.25 | 50 | 34 | 97.24 | BW | 5 in Bathing Season | YES
2242 | LLANFAIRFECHAN - SSO | CG0162201 |  | N | North West | Afon Llanfairfechan | Menai E | Llanfairfech | 65 | 24 | 24 | 16.66 |  |  |  | Communications issue - access issue
72022 | ST. AGNES ROAD CSO | CG0162501 |  | N | North West | Afon Gyffin | Conwy |  | 3.25 | 7 | 7 | 98.82
566 | MILL ROAD SEWAGE PUMPING STATION | CG0162801 |  | N | North West | Llugwy - Conwy to Nant gwryd |  |  | 1421.75 | 79 | 78 | 100
2247 | BETWYS Y COED- PENTRE DDU-SSO | CG0162901 |  | N | North West | Llugwy - Conwy to Nant gwryd |  |  | 141 | 29 | 23 | 97.21
72403 | CWM PENMACHNO - SSO | CG0163101 |  | N | North | Machno |  |  | 2766.25 | 140 | 135 | 96.96
71751 | MIN-Y-NANT CSO | CG0163501 |  | N | North West | Afon Cadnant | Menai W |  | 11.75 | 19 | 19 | 100
2293 | CAERNARFON MARGARET STREET - S | CG0163601 |  | N | North West | Afon Cadnant | Menai W |  | 83.75 | 82 | 44 | 99.02
71750 | CROSSVILLE CSO | CG0163701 |  | N | North West | Menai Straits | Menai W |  | 102.5 | 60 | 60 | 94.16
636 | CAERNARFON PONT SEIONT PS | CG0163801 |  | N | North West | Afon Seiont | Menai W |  | 157.25 | 18 | 17 | 98.34
606 | BALACLAVA ROAD SEWAGE PUMPING ST | CG0163901 |  | N | North West | Menai Strait | Menai W |  | 0 | 0 | 0 | 99.96
2304 | ROCK TERRACE CSO BETHESDA | CG0164901 |  | N | North West | Ogwen - lower |  |  | 548.75 | 64 | 59 | 94.64
71650 | OLD COLWYN QUEENS ROAD - SSO | CG0166101 |  | N | North East | Beach |  | Colwyn Bay | 118 | 32 | 30 | 99.37 | BW | 5 in Bathing Season | YES
2349 | PENTREFOELAS - SSO | CG0167001 |  | N | North | Merddwr (Conwy) |  |  | 13.75 | 5 | 2 | 98.08
2439 | CORRIS MINFORDD ST - SSO | CG0167401 |  | N | North | Dulas North |  |  | 70 | 11 | 11 | 99.25
2511 | LLANGEFNI MH REAR OF BURGESS - | CG0167901 |  | N | North | Cefni - Ceint to Cefni reservoir |  |  | 36.25 | 23 | 13 | 99.56
2512 | GAERWEN STATION SPS | CG0168101 |  | N | North West | Braint - lower |  |  | 724.25 | 62 | 58 | 99.98
2513 | HERMON MH IN ROAD PREC SPS | CG0168201 |  | N | North | Rhyd-Hir |  |  | 590.75 | 52 | 52 | 84.14 |  |  |  | Data unreliable from 01/01 to 19/02/2021. Due to calibration issue, resolved.
71864 | TREARDDUR BAY PS (PUMPED DISCHARGE) | CG0168401 |  | N | North West | Estuarial waters of the Inland Sea |  | Trearddur | 298.5 | 62 | 62 | 99.91
2518 | RHOSYBOL GORSLWYD PS | CG0168801 |  | N | North | Alaw |  |  | 1710.75 | 140 | 140 | 87.04 |  |  |  | Data unreliable from 03/06 to 20/07/2021. Due to static telemetry signal. Instrumentation task escalated through business as usual for instrumentation defect.
965 | RHOSYBOL PLAS Y FFRWD SPS | CG0168901 |  | N | North West | Alaw |  |  | 113.75 | 29 | 28 | 100
626 | NANTLLE PS | CG0169601 |  | N | North West | Llyfni |  |  | 1318 | 96 | 96 | 99.99
71593 | GLASFRYN TERRACE STW ARTHOG | CG0171601 |  | N | North West | unnamed watercourse | Mawddach | Fairbourne | 63 | 4 | 4 | 99.84
71591 | CASTELL PUMPING STATION | CG0171701 |  | N | North West | unnamed watercourse | Mawddach |  | 86.25 | 9 | 6 | 100
71589 | ARTHOG TERRACE SEWAGE PUMPING ST | CG0171801 |  | N | North West | unnamed watercourse | Mawddach |  | 239.25 | 27 | 27 | 97.2
1147 | LLANGERNYW PS | CG0179701 |  | N | North East | Elwy - Melai to Gallen |  |  | 98.75 | 11 | 11 | 37.67 |  |  |  | Communications issue, resolved in November 2021.
835 | GWALCHMAI ISAF PS | CG0180201 |  | N | North West | Un-named - Crigyll/Caradog catchment |  |  | 51.25 | 10 | 8 | 79.18 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
2521 | BODFFORDD OPP CAPEL SARDIS - S | CG0180301 |  | N | North | Cefni - Cefni reservoir west |  |  | 193.25 | 61 | 45 | 98.88
2522 | DWYRAN BY SCHOOL - SSO | CG0180401 |  | N | North West | Afon Braint | Menai W | Llanddwyn | 1.75 | 5 | 2 | 5.56 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
2523 | DWYRAN RHYDWYN - SSO | CG0180501 |  | N | North West | Afon Braint | Menai W | Llanddwyn | 59 | 24 | 17 | 99.66
682 | ABERGYNOLWYN PS - STORM ABERGYNOL | CG0181601 |  | N | North West | Dysynni - upper |  |  | 20.75 | 4 | 3 | 100
2090 | Towyn Gors Road PS | CG0183601 |  | N | North East | North Wales |  |  | 0 | 0 | 0 | 100
913 | MALLTRAETH VILLAGE PUMPING STATION and CSO | CG0183801 |  | N | North West | Afon Cefni upstream of tidal gates | Malltraeth |  | - | - | - | 0 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
577 | LLANDUDNO LLANRHOS SPS | CG0184201 |  | N | North West | Unnamed Ditch | Conwy |  | 6.25 | 5 | 2 | 100 | BW | 5 in Bathing Season
581 | LLANFAIRFECHAN HOSPITAL SPS | CG0184301 |  | N | North West | Conway Bay | Menai E |  | 0 | 0 | 0 | 100 | BW | 5 in Bathing Season
583 | BETWYS Y COED MURIAU P.S. | CG0184401 |  | N | North West | Conwy - tidal limit to Merddwr |  |  | 30 | 27 | 21 | 100
568 | DEGANWY BEACH SPS | CG0184501 |  | N | North West | Unnamed Ditch | Conwy |  | 4 | 6 | 5 | 100 | BW | 5 in Bathing Season
72002 | GLANWYDDAN PUMPING STATION | CG0184601 |  | N | North West | Afon Wydden | Rhos on S |  | 723.75 | 42 | 42 | 99.99 | BW | 5 in Bathing Season
72268 | BRYNREFAIL MAIN SPS | CG0185101 |  | N | North West | Caledffrwd |  |  | 437 | 63 | 59 | 99.83
621 | GLASINFRYN SPS | CG0185201 |  | N | North West | Cegin |  |  | 639 | 78 | 66 | 99.97
1305 | RHYD Y FOEL | CG0185501 |  | N | North East | Dulas - lower |  |  | 3.25 | 10 | 10 | 98.83
2146 | BLAENAU FFESTINIOG NO2 | CG0185701 |  | N | North West | Goedol |  |  | 4.25 | 17 | 0 | 45.7 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
2570 | LAND OFF PENCEFN ROAD TANYGRISIAU | CG0186001 |  | N | North |  |  |  | 1039.25 | 123 | 110 | 98.51
3280 | LAND OFF A496 MANOD BLAENAU FFESTI | CG0186201 |  | N | North West | Goedol |  |  | 681.75 | 110 | 95 | 99.01
805 | FAIRBOURNE PUMPING STATION | CG0186501 |  | N | North West | Afon Henddol | Mawddach |  | 98 | 17 | 17 | 100
697 | ABERANGELL NO1 PS | CG0186701 |  | N | North West | Angell |  |  | - | - | - | 0 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
3109 | BODELWYDDAN MAIN PS | CG0186801 |  | N | North East | Gele |  |  | 85.5 | 17 | 17 | 99.99
747 | LLANGAFFO CAE BERLLAN SPS | CG0186901 | [6 empty] | 0.25 | 1 | 1 | 99.79
1014 | PENTRAETH TAN Y GRAIG SPS | CG0187001 |  | N | North West | Afon Nodwydd | Red Wharf |  | 0 | 0 | 0 | 99.9
1284 | LLANDDANIEL PONT Y CRUG SPS | CG0187101 |  | N | North West | Afon Briant | Menai W |  | 263.25 | 42 | 38 | 99.99
827 | GORSLLWYD SEWAGE PUMPING STATION | CG0187201 |  | N | North West | Cadnant |  | Llanddona | 837.5 | 106 | 95 | 93.68
891 | LLANSADWRN PS | CG0187301 |  | N | North West | Afon Cadnant | Menai E |  | 7.75 | 3 | 3 | 93.88
2524 | BODEDERN SEWAGE PUMPING STATION | CG0187501 |  | N | North West | Alaw |  |  | 0 | 0 | 0 | 100
591 | BRYN DU SEWAGE PUMPING STATION | CG0187601 |  | N | North West | Llyn Maelog |  | Rhosneigr | 350.5 | 39 | 37 | 99.85
1267 | TREARDDUR BAY HAUL A MOR SPS | CG0187901 |  | N | North West | Adj Ditch |  | Trearddur | 0 | 0 | 0 | 100
593 | LLANGEFNI MAIN PUMPING STATION | CG0188001 |  | N | North West | Cefni - Ceint to Cefni reservoir |  |  | 115 | 14 | 14 | 99.97
1278 | LLANGEFNI RHOSTREHWFA | CG0188101 |  | N | North West | Elwy - Melai to Gallen |  |  | 46.5 | 13 | 10 | 100
72019 | TALWRN SPS | CG0188201 |  | N | North East | Ceint |  |  | 53.5 | 17 | 14 | 99.99
594 | NEWBOROUGH MILLBANK SPS | CG0188301 |  | N | North West | Unnamed Ditch | Malltraeth |  | 0 | 0 | 0 | 6.8 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
999 | LLANFAIR PG SPS | CG0188401 |  | North |  | Braint - upper |  |  | 237.75 | 41 | 41 | 99.92
1015 | DOLGARROG TAN Y FFORDD PS | CG0188601 |  | N | North West | Porth-llwyd |  |  | 338.75 | 58 | 58 | 99.99
70026 | MARL DRIVE CSO LLANDUDNO JUNCTION | CG0190901 |  | N | North West | Afon Wydden | Conwy |  | 66.75 | 9 | 9 | 100 | BW | 5 in Bathing Season
2217 | LLANGEFNI MH FRONT YNYS MON OF | CG0191201 |  | N | North West | Cefni - Ceint to Cefni reservoir |  |  | 60.75 | 42 | 42 | 98.68
592 | FRYARS BAY P.S- SCREENED EMERG | CG0312601 |  | N | North West | Menai Straits | Menai E |  | 0 | 0 | 0 | 99.61
559 | TALYBONT STW | CG0314702 |  | N | North West | Afon Ogwen | Menai E |  | 4.25 | 11 | 5 | 100
1938 | YNYS LAS PS | CG0314801 |  | N | North West | unnamed ditch | Dyfi |  | 408.5 | 30 | 28 | 99.98
2828 | CLYNNOG FAWR PS CLYNNOG FAWR , | CG0315102 |  | N | North West | Desach |  |  | 256 | 53 | 51 | 100
71598 | LLANDUDNO ROAD (PENRHYN BAY) PUMPING STATION | CG0315301 |  | N | North West | Afon Ganol East | Rhos on S |  | 9.25 | 3 | 3 | 100 | BW | 5 in Bathing Season
770 | QUAY PS CONWY QUAY CONWY | CG0315801 |  | N | North West | Afon Conwy | Conwy |  | 12.5 | 10 | 10 | 99.91 | BW | 5 in Bathing Season
2656 | FORYD RD EMERGENCY KINMEL BAY , | CG0316401 |  | N | North East | Kinmel Bay Drain |  | Sandy Cove | 0 | 0 | 0 | 99.17
1230 | TY NEWYDD PUMPING STATION | CG0317001 |  | N | North East | Rhyl Cut |  | Rhyl | 0.25 | 1 | 0 | 100 | BW | 5 in Bathing Season
2849 | BOOT & SHIP PS , , | CG0317101 |  | N | North East | unnamed watercourse discharging to River Dee | Dee W |  | 0 | 0 | 0 | 99.97
2573 | CWM BOWYDD SSO BLAENAU FFESTINIOG | CG0317201 |  | N | North West | Goedol |  |  | 904.75 | 114 | 114 | 99.93
1298 | PRESTATYN NANT HALL PS NANT HALL RO | CG0317701 |  | N | North East | Nant Mill Stream |  | Prestatyn | 0 | 0 | 0 | 99.99 | BW | 5 in Bathing Season
1298 | PRESTATYN NANT HALL PS NANT HALL RO | CG0317702 |  | N | North East | Nant Mill Stream |  | Prestatyn | 0 | 0 | 0 | 99.99
3111 | BUCKLEY (THE WILLOWS) SPS | CG0323501 |  | N | North East | Lead Brook |  |  | 86.25 | 20 | 14 | 99.9
2367 | STORMWATER TANK ADJACENT TO HALLS F | CG0324301 |  | N | North East | Morlas Brook |  |  | 336.5 | 87 | 87 | 98.96
3105 | FLINT STW (THE MEADOWS) , , | CG0324401 |  | N | North East | The Swinchiard Brook | Dee W |  | 0 | 0 | 0 | 100
502 | PENTRAETH STW | CG0325501 |  | N | North West | Afon Nodwydd | Red Wharf |  | 1473.5 | 129 | 125 | 99.96
3278 | BLAENAU FFESTINIOG SSO NO 3 , , | CG0325701 |  | N | North West | Goedol |  |  | 0 | 0 | 0 | 100
500 | NEWBOROUGH STW | CG0326101 |  | N | North West | Afon Braint | Menai W | Llanddwyn | 111.25 | 34 | 20 | 100
70636 | CHIRK PS (SCREENED STROM) , , | CG0329701 |  | N | North East | Dee - Ceiriog to Alwen |  |  | 0 | 0 | 0 | 93.28
70636 | CHIRK PS (SCREENED STROM) , , | CG0329702 |  | N | North East | Dee - Ceiriog to Alwen |  |  | 6.5 | 15 | 5 | 99.99
3128 | BONTNEWYDD SSO YSGOL GYNRADD BONTNE | CG0332501 |  | N | North West | Gwyrfai |  |  | 97.5 | 16 | 16 | 99.99
70514 | Bodffordd STW Settled Storm | CG0337001 |  | N | North | Cefni - Cefni reservoir west |  |  | 241 | 52 | 41 | 99.67
3371 | BRYNSIENCYN STW SETTLED STORM , , | CG0340902 |  | N | North West | The Menai Strait | Menai W |  | 1441 | 99 | 92 | 84.79 |  |  |  | Communications issue from 01/01 to 25/02/2021, resolved.
71820 | BRYNSIENCYN SEWAGE PUMPING STATION | CG0340903 |  | N | North West | The Menai Strait | Menai W |  | 164.25 | 16 | 16 | 100
71820 | BRYNSIENCYN SEWAGE PUMPING STATION | CG0340904 |  | N | North West | The Menai Strait | Menai W |  | 161.75 | 17 | 16 | 100
3211 | CRICCIETH EAST PS , ,Storm and EO | CG0341301 |  | N | North West | Tremadog Bay |  | Criccieth | - | - | - | 0 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
3211 | CRICCIETH EAST PS , ,EO | CG0341302 |  | N | North West | Tremadog Bay |  | Criccieth | 183 | 18 | 17 | 88.64 |  |  |  | Communications issue, resolved in February 2021.
3210 | CRICCIETH WEST PS , ,Storm | CG0341401 |  | N | North West | Tremadog Bay |  | Criccieth | 167.5 | 28 | 26 | 99.17
3210 | CRICCIETH WEST PS , ,EO | CG0341402 |  | N | North West | Tremadog Bay |  | Criccieth | 405.75 | 43 | 42 | 99.31
72562 | CSO ON SEWER (CRICCIETH BEACH) , | CG0341501 |  | N | North West | Culverted stream which crosses Criccieth Beach |  | Criccieth | 9 | 6 | 5 | 99.67
70550 | CRICCIETH STW FINAL | CG0341602 |  | N | North West | Tremadog Bay |  |  | 1969.5 | 126 | 126 | 99.95
70506 | BENLLECH SEWERAGE SYSTEM | CG0341901 |  | N | North West | Coastal Waters off Benllech | Red Wharf | Benllech | 0 | 0 | 0 | 98.64 | BW | 5 in Bathing Season
3219 | LLANFAES WWTW STORM TANK | CG0342902 |  | N | North West | Menai Strait | Menai E |  | 676.25 | 76 | 76 | 91.22
3220 | LLANFAES PS (EMERGENCY) , , | CG0342903 |  | N | North West | unnamed watercourse | Menai E |  | 4.25 | 3 | 3 | 99.69
3221 | MOUNT FIELD P.S. BEAUMARIS , | CG0342904 |  | N | North West | Menai Strait | Menai E |  | 0 | 0 | 0 | 100
3221 | MOUNT FIELD P.S. BEAUMARIS , | CG0342905 |  | N | North West | Menai Strait | Menai E |  | 93 | 31 | 31 | 100
70506 | WENDON CAR PARK PS BENLLECH | CG0345201 |  | N | North West | Coastal Waters off Benllech | Red Wharf | Benllech | 0 | 0 | 0 | 98.64
2478 | CSO NEAR MINAFON QUEENS PARK WREXH | CG0346601 |  | N | North East | Gwenfro |  |  | 465 | 37 | 37 | 99.72
72269 | CSO NR KING'S MILLS QUEENS PARK WR | CG0346602 |  | N | North East | Gwenfro |  |  | 32.25 | 14 | 14 | 100
1229 | COAST ROAD PS RHYL | CG0347301 |  | N | North |  |  |  | 40.75 | 80 | 80 | 96.44
1120 | FLINT BARDYN PS , , | CG0348401 |  | N | North East | River Dee Estuary | Dee W |  | 21.25 | 31 | 31 | 100
3268 | FELINHELI PS (OPP SEA CADET CORPS) | CG0349401 |  | N | North West | Menai Straits | Menai E |  | 0 | 0 | 0 | 100
3266 | FELINHELI PS (QUAY COTTAGE) , , | CG0349501 |  | N | North West | Menai Straits | Menai E |  | 288 | 26 | 26 | 100
3267 | FELINHELI PS (ADJ TO QUAY TOILETS) | CG0349701 |  | N | North West | Menai Straits | Menai E |  | 0 | 0 | 0 | 100
70648 | CSO NR RIVULET RD QUEENS PARK WREX | CG0350401 |  | N | North | Gwenfro |  |  | 0 | 0 | 0 | 99.73
1323 | ABERDYFI WHARF PS SEAVIEW TERRACE | CG0351301 |  | N | North West | Afon Dyfi | Dyfi | Aberdyfi | 369.5 | 35 | 35 | 99.99
3244 | TYWYN STW MORFA GWYLLT TYWYN | CG0351402 |  | N | North West | Un-named trib north of Afon Dyffyn-G |  | Tywyn | 252.5 | 46 | 46 | 99.88
3244 | TYWYN STW MORFA GWYLLT TYWYN | CG0351403 |  | N | North West | Cardigan Bay North |  | Tywyn | 1817.5 | 103 | 103 | 99.88
1326 | BEACH ROAD PS BANGOR , Short Sea Outfall | CG0351701 |  | N | North West | Menai Strait | Menai E |  | 35.25 | 17 | 17 | 99.5
1326 | BEACH ROAD PS BANGOR , Long Sea | CG0351702 |  | N | North West | Menai Strait | Menai E |  | 250.75 | 64 | 64 | 99.51
832 | LLANBERIS PS | CG0352001 |  | N | North West | Nant Peris |  |  | 1 | 3 | 3 | 93.44
3270 | GORAD ROAD PS (STORM/EMERG) , , | CG0353701 |  | N | North West | Menai Strait | Menai E |  | 0 | 0 | 0 | 100
72427 | GORAD ROAD PS (STORM/EMERG) , , | CG0353702 |  | N | North West | Menai Strait | Menai E |  | 122.75 | 71 | 71 | 100
70525 | MEIRION ROAD PS (STORM/EMERG) | CG0353801 |  | N | North West | Menai Strait | Menai E |  | 2.75 | 4 | 4 | 100
72149 | MYNYDD ISA WYLFA HILL , , | CG0355001 |  | N | North East | Alyn - Leadmill to Hope, US STW |  |  | 211.5 | 66 | 57 | 100
2803 | O/S TOP RANK CLUB BROOK ST WREXHAM | CG0355301 |  | N | North East |  |  |  | 103.25 | 21 | 21 | 68.2 |  |  |  | Communications issue, resolved in August 2021.
3171 | REAR HAMDEN WAY PLAS MADOC , , | CG0355501 |  | N | North East | Dee - Ceiriog to Alwen |  |  | 8.25 | 3 | 3 | 99.73
2038 | SANDYCROFT FACTORY ROAD , , | CG0355701 |  | N | North East | Sandycroft Drain |  |  | 3.75 | 1 | 1 | 99.45
2064 | NEAR CASTLE GIFT SHOP LLANBERIS , | CG0355801 |  | N | North West | Nant Peris |  |  | 94.5 | 34 | 26 | 99.07
71772 | LLANWRST OLD NURSERY CSO LLANWRST | CG0356001 |  | N | North East | Conwy - tidal limit to Merddwr |  |  | 1.25 | 2 | 1 | 99.62
72255 | COLLIERY ROAD RHOSTYLLEN , | CG0356101 |  | N | North East | Black Brook |  |  | 30 | 20 | 16 | 100
2624 | LEVEL CROSSING ROSSETT , | CG0356201 |  | N | North East | Alyn - Hope to confluence with Dee |  |  | 91.25 | 22 | 18 | 44.41 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
72051 | RUTHIN/BERSE ROAD COEDPOETH , | CG0356301 |  | N | North East | Gwenfro |  |  | 218 | 58 | 42 | 99.88
2658 | LLANDULAS MILL ST CSO | CG0356501 |  | N | North East | River Dulas | Llanddulas |  | 0.75 | 2 | 2 | 99.18 | BW | 5 in Bathing Season
2667 | BEDDGELERT EAST BANK CSO , , | CG0356701 |  | N | North | Glaslyn - Nanmor to Colwyn |  |  | 852.25 | 78 | 76 | 94.57
2672 | TREFOR , , | CG0356901 |  | N | North | Un-named to Caernarfon Bay South |  |  | 12 | 11 | 8 | 99.18
653 | HARLECH TERMINAL PS (OUTFALL B) | CG0357101 |  | N | North West | unnamed watercourse |  | Harlech | 398.25 | 65 | 63 | 99.97
2731 | HARLECH OUTSIDE LAUNDRY , , | CG0357201 |  | N | North West | unnamed Stream |  | Harlech | 16.25 | 5 | 4 | 11.26 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
2732 | LLANUWCHLYN , , | CG0357301 |  | N | North | Dee - above Afon Lliw |  |  | 326.5 | 46 | 46 | 98.92
2736 | TRAWSFYNYDD MAESGWINDY EST , , | CG0357401 |  | N | North West | Prysor |  |  | 182.75 | 68 | 68 | 100
2738 | TRAWSFYNYDD NR BRON GWYNDY , , | CG0357501 |  | N | North West | Prysor |  |  | 19 | 18 | 18 | 99.3
2739 | REAR OF PRYSOR FILLING STATION TRAW | CG0357601 |  | N | North West | Prysor |  |  | 1.25 | 5 | 5 | 100
2754 | SALTNEY BRIDGE STREET , , | CG0357701 |  | N | North East | Balderton drain |  |  | 0 | 0 | 0 | 99.73
2776 | CHAPEL STREET/MADOG STREET PORTHM | CG0357801 |  | N | North West | Nant y Cyt | Glaslyn |  | - | - | - | 0 |  |  |  | Data unreliable from 01/01/2021 to 31/12/2021. Due to erratic telemetry signal. Instrumentation task escalated through business as usual for instrumentation defect.
2777 | BAKERS LANE/CHANDLERS PLACE PORTH | CG0357901 |  | N | North West | Nant y Cyt | Glaslyn |  | 0 | 0 | 0 | 83.11 |  |  |  | Communications issue, resolved in April 2021.
2782 | PADDOCK ROAD RUABON , | CG0358201 |  | N | North East | Eitha |  |  | 8.25 | 3 | 2 | 99.72
2784 | RUTHIN ROAD GEGIN , | CG0358301 |  | N | North East | Gwenfro |  |  | 6.75 | 10 | 4 | 99.63
2786 | CHAPEL LANE OPPOSITE GARDEN CENTRE | CG0358401 |  | N | North East | Alyn - Hope to confluence with Dee |  |  | 45.5 | 30 | 30 | 98.41
2735 | INLET MANHOLE PENRHYNDEUDRAETH , , | CG0359101 |  | N | North West | Un-named tributary Dwyryd estuary |  |  | 980.25 | 115 | 115 | 99.96
2623 | FFORDD OFFA RHOSLANERCHRUGOG , | CG0359501 |  | N | North East | Black Brook |  |  | 32 | 32 | 16 | 97.67
2664 | MERLLYN LANE BAGILLT , | CG0359701 |  | N | North East | Unnamed Watercourse | Dee W |  | 0.75 | 3 | 0 | 99.44
2793 | WOODLAND VIEW CEFN Y BEDD , | CG0360001 |  | N | North East | Cegidog |  |  | 0 | 0 | 0 | 95.52
1143 | LLANDEGLA CSO | CG0360101 |  | North |  | Alyn - upper river above Rhydymwyn |  |  | 23 | 5 | 5 | 99.95
1094 | OUTSIDE 24 OFFA CHIRK , | CG0360201 |  | N | North East | Dee - Ceiriog to Alwen |  |  | 665.25 | 55 | 55 | 99.25
2108 | CHAMBERS LANE/MERCIA DRIVE MYNYDD I | CG0360301 |  | N | North East | Alyn - Leadmill to Hope, US STW |  |  | 4.5 | 5 | 3 | 99.97
1024 | NEAR PS NO 2 TREFRIW , | CG0360401 |  | N | North West | Conwy |  |  | 189.5 | 55 | 44 | 99.97
2801 | CORNER STATION YARD CORWEN , | CG0360501 |  | N | North East | Dee - Ceiriog to Alwen |  |  | 47 | 4 | 4 | 91.98
2804 | PARK ROAD RHOSYMEDRE , | CG0360601 |  | N | North East | Trefnant Brook |  |  | - | - | - | 0 |  |  |  | Data unreliable from 01/01/2021 to 31/12/2021. Due to erratic telemetry signal. Instrumentation task escalated through business as usual for instrumentation defect.
2810 | YSCEIFIOG CSO , , | CG0360701 |  | N | North East | Wheeler - un-named upper tributary |  |  | 0.5 | 2 | 0 | 99.97
1123 | GREENFIELD IND EST NO 1 HOLYWELL | CG0360801 |  | N | North East | River Dee (Tidal) | Dee W |  | 285 | 20 | 20 | 99.98
520 | LLANNOR STW (SETTLED STORM) , , | CG0363001 |  | N | North West | Rhyd-Hir |  |  | 1216 | 119 | 111 | 95.57
3264 | LLYN Y FELIN PS | CG0363401 |  | N | North West | Menai Strait | Menai E |  | 0 | 0 | 0 | 99.89
3264 | LLYN Y FELIN PS (EMERGENCY OVERFLOW) | CG0363402 |  | N | North West | Menai Strait | Menai E |  | 0 | 0 | 0 | 99.89
3261 | PUMPING STATION NO.1 (FAELOG CAUSEWAY) | CG0363501 |  | N | North West | Menai Strait | Menai E |  | 1065.5 | 96 | 96 | 100
3261 | PUMPING STATION NO.1 (FAELOG CAUSEWAY) (EMERGENCY OVERFLOW) | CG0363502 |  | N | North West | Menai Strait | Menai E |  | 1065.5 | 96 | 96 | 100
3262 | PS NO 2 (PORTH WRACH) | CG0363601 |  | N | North West | Menai Strait | Menai E |  | 7.25 | 15 | 15 | 99.98
3262 | PS NO 2 (PORTH WRACH) (EMERGENCY OVERFLOW) | CG0363602 |  | N | North West | Menai Strait | Menai E |  | 7.25 | 15 | 15 | 99.98
3263 | PS NO 3 (SUSPENSION BRIDGE) | CG0363701 |  | N | North West | Menai Strait | Menai E |  | 1365.5 | 108 | 108 | 99.97
3263 | PS NO 3 (SUSPENSION BRIDGE) (EMERGENCY OVERFLOW) | CG0363702 |  | N | North West | Menai Strait | Menai E |  | 1365.5 | 108 | 108 | 99.97
3265 | LLANDEGFAN (MENAI) PUMPING STATION | CG0363801 |  | N | North West | Menai Strait | Menai E |  | 2114 | 115 | 115 | 100
2593 | PENTREFELIN STW | CG0364501 |  | N | North West | Un-named tributary Tremadog Bay |  |  | 924.75 | 116 | 106 | 99.62
70500 | STORM TANK ARMY CADET CENTRE GLAN | CG0364901 |  | N | North West | Goch Amlwch |  |  | 162.75 | 29 | 29 | 100
70664 | GLAENTRAETH ESTATE PS BANGOR , | CG0365101 |  | N | North West | Afon Cegin | Menai E |  | 0 | 0 | 0 | 100
2989 | TREBORTH STW (FINAL) BANGOR | CG0366101 |  | N | North West | Menai Strait | Menai E |  | 823.25 | 69 | 69 | 99.85
3242 | TREBORTH STW (FINAL) BANGOR | CG0366201 |  | N | North West | Menai Strait | Menai E |  | 33.5 | 14 | 14 | 99.83
70025 | CHURCH RD PS CHURCH RD RHOS ON SEA | CG0366401 |  | N | North West | Coastal Waters of Penrhyn Bay | Rhos on S |  | 1063.5 | 87 | 87 | 100 | BW | 5 in Bathing Season | YES
70644 | CSO ADJ MOUNT ST/YORKE ST WREXHAM | CG0366801 |  | N | North | Gwenfro |  |  | 0 | 0 | 0 | 99.73
3321 | BETHEL CSO BETHEL NEAR CAERNARFON | CG0367101 |  | N | North West | Afon Cadnant | Menai W |  | 61 | 24 | 24 | 100
71933 | WOODLANDS P.S WOODLANDS ESTATE MARL | CG0368701 |  | N | North West | Afon Wydden | Conwy |  | 1 | 2 | 1 | 100
956 | RUTHIN STW CSO | CG0369001 |  | N | North East | Afon Clwyd |  | Rhyl | 195.25 | 39 | 39 | 99.74
3249 | PS OFF LLANELION ROAD COLWYN BAY | CG0369401 |  | N | North West | Nant y Ffynnon |  | Colwyn Bay | 0 | 0 | 0 | 99.95 | BW | 5 in Bathing Season
819 | GELLILYDAN STW (SETTLED STORM) | CG0369901 |  | N | North West | Dwyryd - lower |  |  | 959.75 | 101 | 97 | 99.89
972 | PORTHMADOG STW STORM STORAGE PORT | CG0375401 |  | N | North West | Glaslyn Estuary within Glaslyn Marshes | Glaslyn |  | 10.25 | 12 | 12 | 99.93
972 | PORTHMADOG STW STORM STORAGE PORT | CG0375402 |  | N | North West | Glaslyn Estuary within Glaslyn Marshes | Glaslyn |  | 83.25 | 37 | 37 | 99.97
71134 | GANOL STW PS GLAN CONWY CORNER | CG0377602 |  | N | North West | Afon Ganol | Conwy |  | 0.5 | 2 | 2 | 99.34
3333 | GANOL WWTW (STW) GLAN CONWY CORNER | CG0377701 |  | N | North West | Coastal waters of Penrhyn Bay | Conwy |  | 3037.5 | 364 | 364 | 99.81
71134 | GANOL STW PS GLAN CONWY CORNER | CG0377702 |  | N | North West | Afon Ganol | Conwy |  | 0.5 | 2 | 2 | 99.34
3115 | LLANDUDNO JUNCTION PS | CG0379201 |  | N | North West | Estuarial Waters of Afon Conwy | Conwy | Llandudno West Shore | 10.5 | 10 | 10 | 75.41 |  |  |  | Communications issue, resolved in May 2021.
70028 | CONWY ROAD STORM PS | CG0379301 |  | N | North West | Afon Wydden | Conwy |  | 547.5 | 53 | 48 | 99.84 | BW | 5 in Bathing Season | YES
70029 | TYWYN PS | CG0379401 |  | N | North West | Afon Conwy | Conwy |  | 63.25 | 51 | 51 | 99.95
3113 | DEGANWY PS MARINE CRESCENT DEGANWY | CG0379501 |  | N | North West | Afon Conwy | Conwy | Llandudno West Shore | 261.5 | 143 | 143 | 100
3214 | BENLLECH WWTW (STW) LSO BENLLEC | CG0381901 |  | N | North West | Anglesey North | Red Wharf | Benllech | 480.75 | 70 | 64 | 98.64
661 | GREENFIELD WWTW (STW) GREENFIELD | CG0382601 |  | N | North East | Esturial Waters of the River Dee | Dee W |  | 90.25 | 42 | 42 | 99.93
71238 | RHOSNEIGR SPS RHOSNEIGR | CG0383001 |  | N | North West | Irish Sea |  | Rhosneigr | 749 | 39 | 39 | 100
3137 | RHYL (KINMEL BAY) WWTW KINMEL BAY | CG0391301 |  | North |  | Gele |  |  | 574.25 | 56 | 56 | 99.75
70011 | PENMAENMAWR WWTW PENMAENMAWR | CG0393801 |  | N | North West | Coastal Waters of Conwy Bay | Conwy | Penmaenmawr | 2574 | 175 | 175 | 99.96 | BW | 5 in Bathing Season | YES
70011 | PENMAENMAWR WWTW PENMAENMAWR | CG0393901 |  | N | North West | Coastal Waters of Conwy Bay | Conwy | Penmaenmawr | 34.25 | 23 | 23 | 99.96 | BW | 5 in Bathing Season | YES
70567 | DOLWYDDELAN STW DOLWYDDELAN CONWY | CG0397001 |  | N | North West | Lledr |  |  | 2898.25 | 166 | 163 | 99.98
71724 | DOLWYDDELAN WWTW | CG0397101 |  | N | North West | Lledr |  |  | 190.5 | 38 | 38 | 98.6
846 | LLANASA PS CSO / EO | CG0404501 |  | N | North East | Gutter Fawr | Dee West |  | 657.25 | 59 | 59 | 99.9
2927 | CEFN MAWR STW HEOL BERWYN CEFN MAWR | CG0405901 |  | N | North East | Trefnant Brook |  |  | 636.25 | 75 | 75 | 99.9
702 | ABERFFRAW SPS GLAN Y MOR ABERFFRAW | CG0406201 |  | N | North West | Afon Ffraw |  | Aberffraw | 0.5 | 2 | 0 | 100
1324 | ABERFFRAW WASTE WATER TREATMENT WKS | CG0406301 |  | N | North West | Aberffraw Bay |  | Aberffraw | 2104.5 | 103 | 103 | 100
715 | BEDDGELERT WASTE WATER TREATMENT | CG0406401 |  | N | North West | Glaslyn - Nanmor to Colwyn |  |  | 2870.75 | 174 | 168 | 100
2852 | LLANRWST STW LLANRWST CONWY | CG0408101 |  | N | North West | Conwy - tidal limit to Merddwr | Conwy/Conwy Bridge |  | 416 | 91 | 91 | 99.97
72032 | STATION ROAD CSO | CG0412401 |  | N | North West | Coastal waters via a culvert |  | Penmaenmawr | 14.5 | 14 | 9 | 100 | BW | 5 in Bathing Season
71860 | DISCHARGE A 14 FFORDD DDYFRDWY | CG0412601 |  | N | North East | A drain tributary of the Dee estuary | Dee West |  | 4.5 | 15 | 15 | 99.73
71302 | FAIRBOURNE WWTW STORM TANKS | CG0413701 |  | N | North West | coastal waters | Mawddach |  | 1665.75 | 89 | 89 | 99.95
2948 | LLANYSTUMDWY PUMPING STATION | CG0414101 |  | N | North West | Dwyfawr - lower |  |  | 0 | 0 | 0 | 99.83
511 | CAERNARFON WWTW INLET PUMP ST 6MM | CG0415001 |  | N | North West | Seiont - lower | Menai West |  | 404 | 34 | 34 | 99.96
2409 | CHURCH STREET CSO | CG0415401 |  | N | North East | Dee - Ceiriog to Alwen |  |  | - | - | - | 0 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
71508 | COLEG NORMAL SEWAGE PUMPING STATION | CG0415701 |  | N | North West | Menai Strait | Menai East |  | 25.75 | 6 | 5 | 100
499 | MALLTRAETH WWTW TERMINAL SPS | CG0415901 |  | N | North West | Cefni Estuary | Dee West |  | 2.5 | 4 | 2 | 99.69
1232 | SANDY LANE SPS CELYN CRESCENT SALTN | CG0418001 |  | North |  | Balderton drain |  |  | 399.5 | 66 | 66 | 99.46
71652 | EDERN Sewage Pumping Station CSO | CG0426701 |  | N | North West | Afon Geirch |  | Morfa Nefyn | 173 | 27 | 27 | 99.93
71651 | NEFYN WWTW | CG0426801 |  | N | North West | Afon Geirch |  | Morfa Nefyn | 2454.25 | 160 | 160 | 100
71651 | MORFA NEFYN PUMPING STATION CSO (B) | CG0426901 |  | N | North West | Afon Geirch |  | Morfa Nefyn | 235 | 71 | 65 | 99.03
71648 | LLANERCH CSO | CG0427001 |  | N | North West | unnamed watercourse |  | Morfa Nefyn | 9.25 | 14 | 14 | 99.49
71651 | NEFYN WWTW (CONT. S/WATER OUTFALL) | CG0427101 |  | N | North West | unnamed tributary of Afon Geirch |  | Morfa Nefyn | 48.25 | 25 | 25 | 43.3 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
71817 | KERFOOT CARAVAN PARK CSO | CG0428101 |  | N | North East | Ffynnon y Ddol channel |  | Sandy Cove | 24.25 | 4 | 3 | 99.42
1108 | MAES Y LLAN CSO | CG0428201 |  | N | North East | Ffynnon y Ddol channel |  | Sandy Cove | 21.5 | 4 | 3 | 86.09 |  |  |  | Communications issue, resolved in November 2021.
73421 | BETWS Y COED WWTW | CG0428601 |  | N | North West | Llugwy - Conwy to Nant gwryd |  |  | 1543 | 94 | 91 | 98.61
508 | BALA WWTW (STORM) | CG0428901 |  | N | North East | Tryweryn - Dee to Mynach |  |  | 1116.5 | 117 | 117 | 99.83
910 | MAENTWROG WWTW | CG0429001 |  | N | North West | Prysor |  |  | 833.25 | 81 | 69 | 99.92
2183 | WESTBOURNE AVENUE CSO NO.2 | CG0429601 |  | N | North East | CLYWD |  | Rhyl | 0 | 0 | 0 | 99.73
2451 | CLIFTON PARK CSO NO.2 | CG0429701 |  | N | North East | Rhyl Cut |  | Rhyl | 0 | 0 | 0 | 99.45
2917 | NORTHOP WASTEWATER TREATMENT WORKS | CG0429901 |  | N | North East | Lead Brook |  |  | 1345 | 95 | 94 | 100
73638 | LLANBEDR TERMINAL PS (STORM) | CG0430001 |  | N | North West | Artro |  | Llandanwg | 1810.75 | 156 | 153 | 99.97
71653 | LLANDANWG TERMINAL PS | CG0430201 |  | N | North West | Tremadog Bay |  | Llandanwg | 647 | 46 | 46 | 99.85
653 | HARLECH TERMINAL PS (OUTFALL A) | CG0430301 |  | N | North West | Tremadog Bay |  | Harlech | 558.5 | 77 | 76 | 99.97 | BW | 5 in Bathing Season
885 | OVERTON WWTW (STORM) | CG0430701 |  | North |  | Dee - Chester Weir to Ceiriog |  |  | 110.5 | 22 | 22 | 100
506 | ABERERCH WWTW STORM OVERFLOW | CG0431301 |  | N | North West | Erch - lower |  |  | 3429.25 | 182 | 181 | 99.95
2611 | BARMOUTH WWTW LONG SEA OUTFALL | CG0431501 |  | N | North West | Cardigan Bay | Mawddach | Barmouth | 498 | 179 | 143 | 99.97
2144 | BLAENAU FFESTINIOG WWTW STORM (B) | CG0432201 |  | N | North West | Goedol |  |  | 24.25 | 23 | 12 | 99.84
72583 | TREARDDUR BAY PS (GRAVITY) | CG0433201 |  | N | North West | Unnamed Watercourse |  | Trearddur | 290.75 | 37 | 37 | 98.75
71863 | VALLEY STORM PS (GRAVITY DISCHARGE) | CG0433301 |  | N | North West | Un-named - Crigyll/Caradog catchment |  |  | 860.25 | 71 | 71 | 99.97
71863 | VALLEY STORM PS (PUMPED DISCHARGE) | CG0433401 |  | N | North West | Un-named - Crigyll/Caradog catchment |  |  | 343.5 | 50 | 44 | 99.97
71634 | AFONWEN WWTW PS | CG0433901 |  | N | North West | Tremadog Bay |  |  | 181.5 | 22 | 22 | 100
3061 | BETHESDA WWTW STORM | CG0437401 |  | N | North West | Ogwen - lower |  |  | 1306.5 | 130 | 124 | 100
722 | CERRIGYDRUDION WWTW | CG0438301 |  | N | North East | Nug |  |  | 443.75 | 85 | 79 | 99.91
71979 | FFRITH PS/CSO | CG0438701 |  | N | North East | Cegidog |  |  | 33 | 2 | 2 | 99.81
1134 | CYMAU PUMPING STATION/CSO | CG0438801 |  | N | North East | Cegidog |  |  | 23.75 | 15 | 11 | 100
71715 | TREFOR WWTW | CG0438901 |  | N | North West | Un-named to Caernarfon Bay South |  |  | 85.75 | 29 | 29 | 99.86
71715 | TREFOR WWTW | CG0439001 |  | N | North West | Un-named to Caernarfon Bay South |  |  | 1609.25 | 144 | 144 | 99.86
71976 | BRYN AFON CSO, NEBO ROAD, LLANWRST | CG0439401 |  | N | North East | Nant y Goron |  |  | 11 | 33 | 2 | 99.54
73059 | MARIAN MAWR SPLITTER CHAMBER CSO | CG0441301 |  | N | North | Wnion - lower |  |  | 167 | 23 | 23 | 99.71
72048 | MORFA BYCHAN WWTW | CG0448101 |  | N | North West | unnamed stream | Glaslyn |  | 0.75 | 1 | 1 | 100
72048 | MORFA BYCHAN WWTW | CG0448201 |  | N | North West | coastal waters |  | Craig Du | 231.5 | 64 | 64 | 100
72052 | Y MAES CSO | CG0450201 |  | N | North West | estuarial waters of Afon Rhyd Hir |  | Pwllheli | 0 | 0 | 0 | 100 | BW | 5 in Bathing Season
481 | Betws yn Rhos waste water treatment works storm tank | CG0462901 |  | N | North East | Dulas - un-named tributary |  |  | 1676.5 | 135 | 123 | 99.96
71632 | LLWYNGWRIL WWTW TERMINAL PS | CG0463401 |  | N | North West | Cardigan Bay North |  |  | 399.75 | 40 | 39 | 99.91
512 | LLANARMON YN IAL WWTW (STORM) | CM0001202 |  | N | North East | Alyn - upper river above Rhydymwyn |  |  | 168.75 | 70 | 52 | 100
757 | LLANGOLLEN PUMPING STATION | CM0005401 |  | N | North East | Dee - Ceiriog to Alwen |  |  | 472 | 46 | 42 | 100
2193 | FIVE FORDS STW - SETTLED STORM | CM0005702 |  | N | North East | Clywedog - Dee to Gwenfro |  |  | 305.25 | 31 | 31 | 68.73 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
71784 | LLWYN ONN CSO | CM0005901 |  | N | North East | Clywedog - Dee to Gwenfro |  |  | 164.25 | 73 | 73 | 100
1136 | LEESWOOD BETHANIA PUMPING STATION | CM0006401 |  | N | North East | Alyn - Leadmill to Hope, US STW |  |  | 12.75 | 4 | 2 | 100
2906 | DOLYWERN & LLWYNMAWR STW | CM0009501 |  | N | North East | Ceiriog - confluence Dee to Teirw |  |  | 126.25 | 46 | 46 | 99.98
898 | LLANDRILLO STW PS | CM0009801 |  | N | North East | Ceidiog |  |  | 14.5 | 13 | 13 | 100
2427 | PLAS PIGOT CSO ABBEY ROAD DENBIGH | CM0010101 |  | N | North East | Clwyd - un-named tributary below Ystrad |  |  | 2.25 | 2 | 2 | 92.8
71267 | FLINT MOUNTAIN SPS FLINT MOUNTAIN | CM0010901 |  | N | North East | Un-named Dee Estuary South |  |  | 2096 | 106 | 106 | 99.97
956 | RUTHIN STW SETTLED STORM | CM0017602 |  | N | North East | Afon Clwyd |  | Rhyl | 1612.75 | 118 | 118 | 99.94
2929 | CORWEN WWTW STORM | CM0018302 |  | N | North East | Dee - Ceiriog to Alwen |  |  | 1798 | 116 | 113 | 100
783 | DENBIGH STW STORM | CM0028602 |  | N | North East | Afon Clwyd |  | Rhyl | 971.75 | 85 | 85 | 100
1183 | PENTRE HALKYN PS EMERGENCY , , | CM0030202 |  | N | North East | Swinchiard Brook |  |  | 277.75 | 20 | 20 | 100
71837 | LEESWOOD PUMPING STATION | CM0030801 |  | N | North East | Alyn - Leadmill to Hope, US STW |  |  | 757 | 48 | 48 | 99.91
491 | MOLD STW - STORM TANKS DISCHAR | CM0031002 |  | North |  | Alyn - Leadmill to Hope, US STW |  |  | 1183.75 | 118 | 118 | 99.95
2091 | MOLD COMMITTEE'S SEWERAGE SYSTEM | CM0031201 |  | N | North East | Alyn - Leadmill to Hope, US STW |  |  | 6.5 | 13 | 6 | 99.75
2092 | MOLD COMMITTEE'S SEWERAGE SYSTEM | CM0031301 |  | N | North East | Alyn - Leadmill to Hope, US STW |  |  | 0 | 0 | 0 | 93.79
2093 | MOLD COMMITTEE'S SEWERAGE SYSTEM | CM0031401 |  | N | North East | Alyn - Leadmill to Hope, US STW |  |  | 11.25 | 5 | 5 | 99.44
2094 | MOLD COMMITTEE'S SEWERAGE SYSTEM | CM0031501 |  | N | North East | Alyn - Leadmill to Hope, US STW |  |  | 0 | 0 | 0 | 96.66
2095 | MOLD COMMITTEE'S SEWERAGE SYSTEM | CM0031601 |  | N | North East | Terrig |  |  | 1.5 | 4 | 2 | 99.42
2096 | MOLD COMMITTEE'S SEWERAGE SYSTEM | CM0031701 |  | N | North East | Alyn - Leadmill to Hope, US STW |  |  | 11.75 | 24 | 6 | 92.68
2097 | MOLD COMMITTEE'S SEWERAGE SYSTEM | CM0031801 |  | N | North East | Alyn - Leadmill to Hope, US STW |  |  | 66.75 | 46 | 46 | 100
1240 | ARGOED PS | CM0034601 |  | N | North East | Gutter Fawr | Dee W |  | 10.75 | 5 | 4 | 99.94
1119 | FFYNNON WEST PS | CM0034901 |  | N | North East | Ffynnongroew Drain | Dee W |  | 549.25 | 30 | 30 | 99.93
1241 | STATION ROAD PS TALACRE | CM0035301 |  | N | North East | New Drain Talacre | Dee W |  | 383.25 | 27 | 27 | 100
800 | DYSERTH STW STORM | CM0035902 |  | N | North East | The Afon Glanffyddion |  | Rhyl | 168.25 | 56 | 56 | 99.94
800 | LOWER DYSERTH PS | CM0036001 |  | N | North East | Glanfyddion Cut |  |  | 32 | 8 | 8 | 99.94
2137 | CHIRK CHAPEL LANE -SSO | CM0036501 |  | N | North East | Dee - Ceiriog to Alwen |  |  | 1.5 | 3 | 1 | 96.26
73023 | OAKENHOLT PS | CM0038701 |  | N | North East | Un-named Dee Estuary South |  |  | 0 | 0 | 0 | 99.48
1161 | TAI TREVOR PS LLANNERCHYMOR | CM0038901 |  | N | North East | Afon Marsiandwr | Dee W |  | 0 | 0 | 0 | 99.81
71971 | BRIDGE INN PUMPING STATION | CM0039001 |  | N | North East | Alyn - Leadmill to Hope, US STW |  |  | 18 | 3 | 2 | 99.76
2033 | DRURY LOWER FARM ADJACENT SEWERAGE | CM0039401 |  | N | North East | Sandycroft Drain |  |  | 109.25 | 64 | 64 | 99.28
692 | Gresford WwTW | CM0040601 |  | N | North East | Alyn - Hope to confluence with Dee |  |  | 0 | 0 | 0 | 97.2
71315 | WESTBOURNE AVENUE PUMPING STATION | CM0044001 |  | N | North East | Coastal Waters/Irish Sea |  | Rhyl | 226.25 | 19 | 19 | 99.99
2851 | LYGAN Y WERN PS PENTRE HALKYN | CM0045801 |  | N | North East | Swinchiard Brook |  |  | 38.5 | 23 | 12 | 100
1116 | DENBIGH THE GREEN | CM0046901 |  | N | North East | Clwyd - un-named tributary below Ystrad |  |  | 262.25 | 39 | 39 | 99.97
2198 | NEW BROUGHTON COMBINED SEWERAGE (SE | CM0049601 |  | N | North East |  |  |  | 0.25 | 1 | 0 | 99.71
2201 | PANT CSO | CM0049901 |  | N | North East | Black Brook |  |  | 652.5 | 63 | 63 | 79.12 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
2203 | JOHNSTOWN COMBINED SEWERAGE SYSTEM | CM0050101 |  | N | North East |  |  |  | 47.5 | 26 | 26 | 100
72254 | RUABON COMBINED SEWERAGE SYSTEM | CM0050201 |  | N | North East | Black Brook |  |  | 2 | 5 | 2 | 98.63
72008 | HAWARDEN WOOD LANE SEWERAGE SYSTEM | CM0051101 |  | N | North East | Sandycroft Drain |  |  | 125.25 | 46 | 46 | 99.85
1202 | MARINE PARK PS | CM0052701 |  | N | North East | Rhyl Cut East of Ffordd Penrhwylfa |  | Prestatyn | 2.5 | 3 | 2 | 99.99 | BW | 5 in Bathing Season
1197 | CORONATION GARDENS PS | CM0052801 |  | N | North East | Prestatyn Gutter |  | Prestatyn | 32.5 | 25 | 18 | 71.58 |  |  |  | Communications issue, resolved in April 2021.
72529 | PRESTATYN SPS MARINE RD EAST | CM0052901 |  | N | North East | Prestatyn Gutter |  | Prestatyn | 115.5 | 36 | 36 | 99.46
2913 | FLINT STW FLINT FLINTSHIRE | CM0058402 |  | N | North East | Un-named Dee Estuary South |  |  | 928.5 | 95 | 94 | 99.96
728 | BANGOR ON DEE STW | CM0060702 |  | N | North East | Dee - Chester Weir to Ceiriog |  |  | 915.25 | 103 | 96 | 99.85
71218 | BAGILLT EAST SPS | CM0063501 |  | N | North East | Dee Estuary | Dee W |  | 260 | 31 | 31 | 99.73
71219 | BAGILLT WEST SPS BAGILLT | CM0063601 |  | N | North East | Dee Estuary | Dee W |  | 42.75 | 31 | 28 | 99.99
2894 | PWLLGLAS STW | CM0063902 |  | N | North East | Clwyd - upstream Hesbin |  |  | 1032 | 95 | 89 | 100
2894 | PWLLGLAS STW | CM0063903 |  | N | North East | Clwyd - upstream Hesbin |  |  | 1043 | 96 | 90 | 100
859 | CSO AT TREUDDYN STW | CM0066101 |  | N | North East | Cegidog |  |  | 30.5 | 16 | 12 | 100
1165 | MOSTYN ARMS PS MOSTYN | CM0070801 |  | N | North East | culverted tributary of River Dee | Dee W |  | 75.75 | 5 | 5 | 99.79
1166 | MOSTYN DOCKS CAR PARK - SSO | CM0070901 |  | N | North East | culverted tributary of River Dee | Dee W |  | 815 | 39 | 39 | 99.9
2206 | GWYNFRYN CSO | CM0072201 |  | N | North East | Clywedog - above Black Brook |  |  | 1020 | 69 | 68 | 21.1 |  |  |  | Communications issue, resolved in September 2021.
922 | CLAWDDNEWYDD STW | CM0072902 |  | N | North East | Melin-Dwr |  |  | 1936.25 | 111 | 104 | 100
1051 | Llanfair TH STW storm | CM0079201 |  | N | North East | River Elwy |  | Rhyl | 860.25 | 74 | 72 | 99.85
854 | LLANDYRNOG STW STORM | CM0079701 |  | N | North East | Llandyrnog Drain |  | Rhyl | 0 | 0 | 0 | 99.97
995 | BUCKLEY TY GWYN CSO BUCKLEY | CM0081001 |  | N | North East | Alyn - Leadmill to Hope, US STW |  |  | 228 | 58 | 58 | 99.91
3088 | PADESWOOD ROAD STORM TANK CSO | CM0081101 |  | N | North East | Alyn - Leadmill to Hope, US STW |  |  | 823 | 78 | 78 | 99.86
932 | QUEENSFERRY STW (SETTLED STORM) | CM0082301 |  | North |  | DEE (N. WALES) |  |  | 141.25 | 35 | 35 | 100
945 | RHUDDLAN WWTW STORM TANKS | CM0082601 |  | N | North East | Glanfyddion Cut |  | Rhyl | 59 | 27 | 27 | 100
2037 | CONNAH'S QUAY CESTRIAN STREET | CM0086801 |  | N | North East | Lead Brook |  |  | 7.25 | 3 | 2 | 98.3
2900 | HOLT STW | CM0102002 |  | N | North East | Dee - Chester Weir to Ceiriog |  |  | 4.75 | 2 | 1 | 99.89
70631 | HOLT STW | CM0102003 |  | N | North East | Dee - Chester Weir to Ceiriog |  |  | 511 | 68 | 65 | 99.89
2482 | SEWERAGE SYSTEM WEST OF WEALDS CHES | CM0109301 |  | N | North East | Gwenfro |  |  | 0 | 0 | 0 | 99.75
72391 | CAERGWRLE - RHYDDYN HILL ROAD | CM0116801 |  | N | North East | Alyn - Hope to confluence with Dee |  |  | 102.75 | 31 | 28 | 99.31
2028 | HOPE - SARN LANE. | CM0117001 |  | N | North East | Alyn - Hope to confluence with Dee |  |  | 9 | 20 | 6 | 99.96
1160 | CROOKED HORN SPS NO 3 BRYNFORD | CM0144301 |  | North |  | Afon Pant-gwyn |  |  | 41 | 26 | 26 | 76.11 |  |  |  | Communications issue, resolved in December 2021.
2186 | ROE PARC CSO | CM0147801 |  | N | North | Elwy - Clwyd to Afon Melai |  |  | 5.75 | 3 | 3 | 94.95
1193 | PRESTATYN SEVEN SISTERS ROAD SPS | CM0148301 |  | N | North East | Prestatyn Gutter |  | Prestatyn | 0 | 0 | 0 | 100 | BW | 5 in Bathing Season
3154 | CYNWYD STW FINAL EFFLUENT | CM0149302 |  | N | North East | Dee - Alwen to Outlet Llyn Tegid/ Bala Lake |  |  | 230.5 | 87 | 87 | 100
2633 | HIGHER KINNERTON SPS | CM0150001 |  | N | North East | Pulford Brook |  |  | 81.75 | 18 | 18 | 96.67
2975 | BRETTON PS | CM0151101 |  | N | North East | Sandycroft Drain |  |  | 23.5 | 2 | 2 | 98.63
2975 | BRETTON PS | CM0151102 |  | N | North East | Sandycroft Drain |  |  | 1086.25 | 83 | 83 | 52.03 |  |  |  | Data unreliable from 09/02 to 02/08/2022 . Due to static telemetry signal, resolved.
2709 | PENSARN SPS ABERGELE STORM | CM0153801 |  | N | North East | North Wales |  | Abergele | 641.25 | 111 | 111 | 99.83
3114 | COVENTRY CAMP SPS STORM | CM0154001 |  | N | North East | Coastal Waters |  | Sandy Cove | 158.5 | 37 | 37 | 100 | BW | 5 in Bathing Season | YES
1075 | BUCKLEY SOUTHDOWN PARK PS | CM0163501 |  | N | North East | Lead Brook |  |  | 13 | 4 | 2 | 100
2257 | HAWARDEN CROSS TREE LANE - SSO | CM0163701 |  | N | North East | Sandycroft Drain |  |  | 0.5 | 2 | 2 | 99.7
2259 | MANCOT LANE CSO | CM0163801 |  | N | North East | Sandycroft Drain |  |  | 115.5 | 17 | 17 | 100
2263 | CAERGWRLE DERBY ROAD - SSO | CM0164201 |  | North |  | Alyn - Hope to confluence with Dee |  |  | - | - | - | 0 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
2264 | CONNAHS QUAY DEVA AVENUE - SSO | CM0164301 |  | N | North East | Lead Brook |  |  | - | - | - | 0 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
1098 | CONNAHS QUAY LOW LEVEL SPS STORM | CM0164601 |  | N | North East | Lead Brook |  |  | 0.5 | 2 | 2 | 100
1096 | CONNAHS QUAY DOCK ROAD PS | CM0164901 |  | N | North East | Lead Brook |  |  | 9.75 | 2 | 2 | 100
2277 | CONNAHS QUAY GOLFTYN PS CSO/STORM | CM0165601 |  | N | North East | Kelsterton Brook |  |  | 977.75 | 70 | 70 | 100
1213 | CONNAHS QUAY WEPRE PS STORM | CM0165701 |  | N | North East | Lead Brook |  |  | 18 | 22 | 12 | 99.82
1235 | ASHGROVE PS SHOTTON STORM | CM0165801 |  | N | North East | Lead Brook |  |  | 50.25 | 21 | 21 | 92.75
71947 | GARDEN CITY BRITISH LEGION - SSO | CM0166001 |  | N | North East | Shotwick Brook |  |  | 0 | 0 | 0 | 99.99
71948 | SANDYCROFT PHOENIX STREET - SSO | CM0166201 |  | N | North East | Sandycroft Drain |  |  | 8.75 | 2 | 2 | 100
1063 | CEFN Y BEDD GWERN ALYN SPS | CM0166301 |  | N | North East | Alyn - Hope to confluence with Dee |  |  | 188 | 42 | 30 | 99.54
1185 | PEN Y FFORDD WEST VIEW SPS | CM0167001 |  | N | North East | Alyn - Leadmill to Hope, US STW |  |  | 0 | 0 | 0 | 99.97
72115 | MOLD BRYN AWELON - SSO | CM0167901 |  | N | North East | Alyn - Rhydymwyn to Leadmill |  |  | 122.25 | 36 | 34 | 100
71860 | DISCHARGE B 14 FFORDD DDYFRDWY | CM0168101 |  | N | North East | A drain tributary of the Dee estuary | Dee W |  | 696 | 40 | 40 | 97.05
2358 | MYNYDD ISA MOLD ROAD/MERCIA DR | CM0168301 |  | N | North East | Alyn - Leadmill to Hope, US STW |  |  | 521.25 | 93 | 79 | 97.64
2359 | NORTHOP HALL OFF ST MARYS DRIV | CM0168401 |  | N | North East | Lead Brook |  |  | 3.5 | 11 | 2 | 99.76
2360 | PEN Y FFORDD ADJ PEN Y FFORDD | CM0168501 |  | N | North East | Unnamed stream | Dee W |  | 30.75 | 11 | 8 | 99.67
2361 | BAGILLT TYDDYN MESHAM LANE - SSO | CM0168601 |  | N | North East | Unnamed stream | Dee W |  | 0.25 | 1 | 0 | 90.89
2362 | BAGILLT STATION ROAD - SSO | CM0168701 |  | N | North East | Ditch | Dee W |  | 36.5 | 14 | 14 | 99.71 | BW | 5 in Bathing Season
2363 | BAGILLT GREENACRE DRIVE - SSO | CM0168801 |  | N | North East | Ditch | Dee W |  | 48.25 | 19 | 12 | 99.39
2366 | FLINT IN GARDEN 102 MAES GWYN | CM0169101 |  | N | North East | Surface Water | Dee W |  | 71.25 | 48 | 48 | 93.27
2369 | GREENFIELD A548 NR ABBEY MILL | CM0169401 |  | N | North East | Unnamed Stream | Dee W |  | 1.5 | 2 | 2 | 100
2372 | GWESPYR OLD STW - SSO | CM0169501 |  | N | North East | Unnamed stream | Dee W |  | 0 | 0 | 0 | 99.45
2373 | HOLYWELL PEN Y MAES RD/PEN Y MAES GARDEN | CM0169601 |  | N | North | Greenfield Stream |  |  | 164.75 | 40 | 26 | 99.38
2374 | HOLYWELL STRAND WALK NR STRAND | CM0169701 |  | N | North East | Unnamed stream | Dee W |  | 0 | 0 | 0 | 99.65
2375 | HOLYWELL CAR PARK STRAND WALK/RING RD | CM0169801 |  | N | North East | Surface Water |  |  | 0 | 0 | 0 | 98.4
71764 | LLANGOLLEN HAND HOTEL GARDENS | CM0170501 |  | N | North | Dee - Ceiriog to Alwen |  |  | 258 | 56 | 40 | 100
2411 | ROYAL HOTEL CSO | CM0170601 |  | N | North East | Dee - Ceiriog to Alwen |  |  | 1.25 | 3 | 2 | 100
2413 | EAST STREET CSO | CM0170801 |  | N | North East | Dee - Ceiriog to Alwen |  |  | 0 | 0 | 0 | 47.1 |  |  |  | Communications issue - access issue
2414 | WEST STREET CSO | CM0170901 |  | N | North East | Dee - Ceiriog to Alwen |  |  | 4.75 | 8 | 8 | 99.99
2415 | RIVERSIDE CSO | CM0171001 |  | N | North East | Dee - Ceiriog to Alwen |  |  | 0 | 0 | 0 | 99.93
2416 | PRINTING WORKS CSO | CM0171101 |  | N | North East | Dee - Ceiriog to Alwen |  |  | 0 | 0 | 0 | 99.73
71762 | ABBEY ROAD CSO | CM0171201 |  | N | North East | Dee - Ceiriog to Alwen |  |  | 136.25 | 35 | 35 | 100
71765 | PARK AVENUE CSO | CM0171301 |  | N | North East | Dee - Ceiriog to Alwen |  |  | 75 | 9 | 9 | 100
2423 | THE REAR OF THE TANNERY | CM0171401 |  | N | North East | Dee - Ceiriog to Alwen |  |  | 45.25 | 24 | 17 | 100
71763 | BERWYN STREET CSO | CM0171501 |  | N | North East | Dee - Ceiriog to Alwen |  |  | 16.25 | 9 | 9 | 100
2424 | HENLLAN STREET CSO | CM0171901 |  | N | North East | Clwyd - un-named tributary below Ystrad |  |  | 3.5 | 1 | 1 | 99.7
71752 | PANTON HALL CSO | CM0172001 |  | N | North East | Clwyd - un-named tributary below Ystrad |  |  | 41.75 | 37 | 37 | 64.12 |  |  |  | Communications issue, resolved in August 2021.
2426 | DENBIGH FRONGOCH SSO | CM0172101 |  | N | North East | Clwyd - un-named tributary below Ystrad |  |  | 28 | 6 | 5 | 98.36
71880 | DALAR WEN SPS DALAR WEN DENBIGH | CM0172201 |  | N | North | Clwyd - un-named tributary below Ystrad |  |  | 58.75 | 52 | 27 | 99.93
2430 | CORWEN REAR OF THE PAVILLION - | CM0172301 |  | N | North East | Dee - Ceiriog to Alwen |  |  | 55.25 | 23 | 23 | 95.99
72421 | TREFOR ISAF - SSO | CM0172401 |  | N | North East | Trefnant Brook |  |  | 15.75 | 10 | 6 | 100
2432 | DOL Y WERN - SSO | CM0172501 |  | N | North East | Ceiriog - confluence Dee to Teirw |  |  | 16.75 | 12 | 12 | 94.24
2433 | GLYNCEIRIOG Y GAMMER - SSO | CM0172601 |  | N | North East | Ceiriog - confluence Dee to Teirw |  |  | 15 | 27 | 27 | 90.86
71816 | CLIFTON PARK ROAD CSO NO.1 | CM0173001 |  | N | North East | Rhyl Cut |  | Rhyl | 0 | 0 | 0 | 92.81 | BW | 5 in Bathing Season
2454 | PRESTATYN MELIDEN ROAD - SSO | CM0173101 |  | N | North East | Prestatyn Gutter |  | Prestatyn | 13 | 13 | 13 | 99.66 | BW | 5 in Bathing Season
2461 | MELIDEN HOLDING TANK - SSO | CM0173201 |  | N | North | Rhyl cut |  |  | 378.25 | 52 | 46 | 34.54 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
2464 | ETON PARK CSO | CM0173501 |  | N | North East | Afon Ffyddion |  | Rhyl | 0.75 | 3 | 0 | 92.76
2484 | WREXHAM PARK AVENUE - SSO | CM0175001 |  | N | North East |  |  |  | 2.5 | 3 | 3 | 95.89
2486 | CEFN MONSANTO - SSO | CM0175201 |  | N | North East | Trefnant Brook |  |  | 58.5 | 30 | 30 | 68.75 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
71940 | GWERSYLLT GLAN LLYN (FISHPOND) CSO | CM0175301 |  | N | North East | Alyn - Hope to confluence with Dee |  |  | 1.25 | 2 | 2 | 30.36 |  |  |  | Communications issue, resolved in September 2021.
71746 | TALWRN ROAD NO 2 CSO | CM0175501 |  | N | North East | Gwenfro |  |  | 101 | 32 | 32 | 44.38 |  |  |  | Data unreliable from 01/01 to 22/07/2021. Due to static telemetry signal, resolved
2491 | NEWBRIDGE PUMPING STATION | CM0175701 |  | N | North East | Trefnant Brook |  |  | 15 | 7 | 7 | 90.34
71748 | AFON EITHA CSO | CM0175901 |  | N | North East | Black Brook |  |  | 234 | 71 | 71 | 98.78
71749 | BERSHAM COLLIERY CSO | CM0176001 |  | N | North East | Black Brook |  |  | 11.25 | 10 | 5 | 100
2494 | RHOSLLANERCHGRUGOG ABERDERFYN | CM0176101 |  | N | North East | Black Brook |  |  | - | - | - | 0 |  |  |  | Installation set-up issue
1184 | PEN Y CAE PS | CM0176201 |  | N | North East | Eitha |  |  | 208.25 | 32 | 29 | 99.9
2497 | PEN Y CAE SCHOOL FIELD - SSO | CM0176401 |  | N | North East | Eitha |  |  | 0.5 | 1 | 1 | 99.16
71836 | SOUTHSEA ROLLERS ARMS - CSO | CM0176501 |  | N | North East | Gwenfro |  |  | 530.25 | 83 | 83 | 100
1078 | CEFN Y BEDD PS | CM0176601 |  | North |  | Alyn - Hope to confluence with Dee |  |  | 0.75 | 3 | 0 | 98.88
1258 | PANDY PUMPING STATION | CM0176801 |  | N | North East | Alyn - Hope to confluence with Dee |  |  | 15 | 11 | 11 | 99.9
2504 | LAVISTER - SSO | CM0177001 |  | N | North East | Pulford Brook |  |  | 1589.25 | 138 | 138 | 83.23 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
1181 | PENLEY PS | CM0177201 |  | N | North East | Emral Brook - upper |  |  | 42.25 | 21 | 15 | 100
71753 | RUTHIN ROAD ROUNDABOUT CSO DENBIGH | CM0185801 |  | N | North East | Ystrad |  |  | 85.75 | 43 | 43 | 98.97
2500 | BRADLEY OLD STW - SSO | CM0186301 |  | N | North East | Alyn - Hope to confluence with Dee |  |  | 217.75 | 59 | 51 | 99.95
2583 | EYTON SPS - EMERGENCY SCREENED | CM0186601 |  | N | North East | Dee - Chester Weir to Ceiriog |  |  | 2 | 2 | 2 | 95.14
2762 | POWYS CAER ESTYN PS | CM0188401 |  | N | North East | Alyn - Hope to confluence with |  |  | 1 | 4 | 4 | 99.94
2909 | OVERTON WWTW (STORM) | CM0188602 |  | N | North East | Dee - Chester Weir to Ceiriog |  |  | 136.75 | 80 | 80 | 100
70641 | RUABON PS | CM0190801 |  | N | North East | Black Brook |  |  | 235.25 | 50 | 50 | 99.96
1071 | BRYMBO PS | CM0190901 |  | N | North East | Cegidog |  |  | 121 | 27 | 24 | 99.84
1257 | COEDPOETH NANT PS | CM0191001 |  | N | North East | Clywedog - above Black Brook |  |  | 260.75 | 44 | 44 | 99.63
2637 | CEFN PS | CM0191101 |  | N | North | Trefnant Brook |  |  | 324 | 67 | 57 | 99.86
2378 | FFYNNONGROYW TAN LAN BACH PS | CM0191601 |  | N | North East | Tan Lan Drains |  |  | 290.75 | 19 | 19 | 100
2379 | TALACRE STATION ROAD PS | CM0191701 |  | N | North East | Un-named Dee Estuary South |  |  | - | - | - | 0 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
1617 | PONTBLYDDYN NO 1 PUMPING STATION | CM0192001 |  | N | North East | Alyn - Leadmill to Hope, US STW |  |  | 23.5 | 2 | 2 | 100
1190 | PONT Y BODKIN MAIN PS | CM0192201 |  | N | North East | Alyn - Leadmill to Hope, US STW |  |  | 44.25 | 10 | 10 | 100
2386 | PONT Y BODKIN LOWER PS | CM0192301 |  | N | North East | Alyn - Leadmill to Hope, US STW |  |  | 18.25 | 17 | 17 | 99.66
1169 | MYNYDD ISA WATS DYKE AVE PS | CM0192401 |  | North |  | Alyn - Leadmill to Hope, US STW |  |  | 149.75 | 34 | 33 | 99.96
1170 | NANNERCH PS | CM0192501 |  | North |  | Wheeler - upper |  |  | 6 | 4 | 4 | 97.13
2434 | CORWEN CLAWDD PONCEN PS | CM0192601 |  | N | North East | Dee - Ceiriog to Alwen |  |  | 51 | 6 | 6 | 100
2435 | PENTRE LLANRHAEDR PS | CM0192701 |  | N | North East | Nant Mawr |  |  | 6.75 | 2 | 2 | 99.81
1146 | LLANFERRIS PS | CM0192801 |  | N | North East | Alyn - upper river above Rhydymwyn |  |  | 231.25 | 21 | 21 | 100
1194 | PRESTATYN NANT PS | CM0193101 |  | N | North East | Overflow via Sewage System Surcharge |  | Prestatyn | 0 | 0 | 0 | 100 | BW | 5 in Bathing Season
71984 | THE BOULEVARD PS | CM0193201 |  | N | North East | Via surface water sewer to ditch discharging to Prestatyn Gutter |  | Prestatyn | 7.25 | 1 | 1 | 99.63
1201 | PRESTATYN MALL PS | CM0193301 |  | N | North East | Overflow via Sewage System Surcharge |  | Prestatyn | 0.5 | 1 | 1 | 100
1204 | PRESTATYN PURBECK PS | CM0193501 |  | N | North East | Overflow via Sewage System Surcharge |  | Prestatyn | 6 | 2 | 2 | 100 | BW | 5 in Bathing Season
1131 | HOLT PS | CM0193901 |  | N | North East | Dee - Chester Weir to Ceiriog |  |  | 161.5 | 97 | 97 | 99.99
1250 | ACTON PS | CM0194001 |  | N | North East | Alyn - Hope to confluence with Dee |  |  | 0 | 0 | 0 | 100
1255 | MEASGWYN SEWAGE PUMPING STATION | CM0194101 |  | N | North East | Gwenfro |  |  | 175.5 | 19 | 15 | 98.09
1121 | FLINT DEE COTTAGES PS | CM0194301 |  | N | North East | River Dee | Dee W |  | 36.5 | 9 | 6 | 100 | BW | 5 in Bathing Season | YES
1163 | MARSH FARM PUMPING STATION | CM0194401 |  | N | North East | A drain tributary of the Dee estuary | Dee W |  | 667 | 72 | 64 | 99.93
2030 | NORTHOP HALL PUMPING STATION | CM0194501 |  | N | North East | Lead Brook |  |  | 38.75 | 20 | 20 | 100
2348 | LLANSANNAN DDOL - SSO | CM0194701 |  | N | North East | Aled - above Deunant |  |  | 0.75 | 1 | 1 | 99.89
71949 | BUCKLEY LIVERPOOL ROAD - SSO | CM0195901 |  | N | North East | Lead Brook |  |  | 136.5 | 45 | 45 | 100
2205 | LLAY SINGRET (BOREEN CAM) CSO | CM0197701 |  | N | North East | Alyn - Hope to confluence with Dee |  |  | 168.75 | 72 | 72 | 92.55
1162 | MOSTYN NEAR FUN SHIP - SSO | CM0198601 |  | N | North East | Llanerchymor Gutter | Dee W |  | 132.5 | 32 | 30 | 88.73 |  |  |  | Communications issue, resolved in October 2021.
2797 | MYNYDD ISA CHAMBERS LANE/MERCI | CM0198701 |  | N | North East | Alyn - Leadmill to Hope, US STW |  |  | 216.25 | 77 | 60 | 96.84
71641 | PULFORD - SSO | CM0199001 |  | N | North East | Pulford Brook |  |  | 116.75 | 42 | 42 | 99.51
2202 | BERSHAM COLLIERY CSO | CM0199101 |  | N | North East | Black Brook |  |  | 100.75 | 45 | 45 | 96.87
2179 | RHOSWIEL WESTON RHYN - SSO | CM0199201 |  | N | North East | Ceiriog - confluence Dee to Teirw |  |  | - | - | - | 0 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
2089 | TREFNANT NANT Y PATRICK - SSO | CM0200001 |  | N | North East | Clwyd - tidal limit to Hesbin |  |  | 10.75 | 7 | 4 | 99.69
2088 | TREFNANT VILLAGE - SSO | CM0200101 |  | N | North East | Clwyd - tidal limit to Hesbin |  |  | 7.25 | 6 | 2 | 98.16
2870 | GWYDDELWERN PS. - EMERGENCY SC | CM0208701 |  | N | North East | Camddwr |  |  | 0 | 0 | 0 | 99.97
70634 | CHIRK BANK PS | CM0230601 |  | N | North East | Ceiriog - confluence Dee to Teirw |  |  | 258.75 | 29 | 29 | 99.97
2869 | DOBSHILL PS | CM0231601 |  | N | North East | Sandycroft Drain |  |  | 0 | 0 | 0 | 100
50634 | Henllan WWTW CSO, Henllan, Ceredigion, SA44 5TE | DB3297TS |  | SW | South West | Teifi - conf with Nant Wern-Macwydd to tidal limit |  |  | 214.25 | 47 | 47 | 100
73288 | Peblig Ind Est CSO, Peblig Mill, Ffordd Llanbeblig, Caeathro, Caernarfon, Gwynedd, LL55 2SE Caethro | DB3393HK |  | N | North | Seiont - lower |  |  | 129 | 28 | 28 | 99.49
72299 | CSO near 11 Upper Station Road, Garnant, Ammanford, SA18 1JG | EP3223XD |  | SW | West | Aman - conf with Garnant to conf with Loughor |  |  | 848 | 91 | 91 | 99.91
50682 | Llanpumsaint WWTW Storm overflow, Llanpumsaint, Carmarthenshire, SA33 6BS | FB3690HH |  | SW | South West | Gwili - conf with Alltwalis to conf with Duad |  |  | 927.75 | 106 | 91 | 100
72498 | CSO to rear of 8 Griffin Park, Pentre | JP3524XT |  | SE | South East | Rhondda R - source to conf Afon Rhondda Fach |  |  | 104 | 33 | 33 | 100
2763 | COMBINED SEWER OVERFLOW SERVING | MP3323XX |  | N | North East | Alyn - Hope to confluence with |  |  | 96 | 6 | 6 | 100
72796 | 92 Penryn Isaf CSO, Penrhyn Bay | MP3324XK | [6 empty] | 200 | 91 | 76 | 98.89
71645 | HARLECH RUM HOLE | MP3326GR |  | N | North | Dwyryd estuary south |  |  | 0.25 | 1 | 1 | 99.72
2305 | Rachub Maes Bleddyn CSO, Rachub, Gwynedd | MP3328XV |  | N | North West | Trib of Afon Ogwen |  |  | 431.5 | 68 | 49 | 99.59
71566 | 4 Toad Hall, Aberaeron, Cardigna | MP3424XH |  | SW | West | Aeron - confluence with Gwili to tidal limit |  |  | 0 | 0 | 0 | 99.45
73377 | 1 TEIFI TERRACE CSO NEWCASTLE E | MP3425XC |  | SW | West | Teifi - conf with Nant Wern-Macwydd to tidal limit |  |  | 500.25 | 70 | 61 | 98.07
70770 | EMLYN ARMS CSO NEWCASTLE EMLYN | MP3426GY |  | SW | West | Teifi - conf with Nant Wern-Macwydd to tidal limit |  |  | 1458.75 | 266 | 238 | 93.3
71348 | TEIFI TERRACE CSO | MP3521XX |  | South West |  | Teifi - Afon Clettwr to Afon Ceri |  |  | 1134.25 | 171 | 171 | 96.43
51888 | CSO at Bronwydd STW, Bronwydd Road, Bronwydd, Carmarthen, SA33 6HT | QB3690HY |  | SW | South West | Gwili - Duad conf to conf with Tywi at spring TL |  |  | 58.5 | 7 | 7 | 99.92
71745 | Heol Y Fro Combined Sewer Overflow, Coedpoeth, Wrexham, LL11 3LA | QP3629GF |  | N | North | Gwenfro |  |  | 73.25 | 26 | 26 | 100
72735 | RHYDDINGS TERRACE UPLANDS SWANSEA | TB3593HM |  | SW | Swansea | Brynmill Stream | Swans W | Swansea | 1.25 | 5 | 0 | 99.15 | BW | 5 in Bathing Season
72967 | CSO at 18 Min y Ddol, Penparcau, Aberystwyth, SY23 1RG | UB3593HU |  | SW | West | Rheidol - confluence with Castell to tidal limit |  |  | 0 | 0 | 0 | 99.73
32132 | Forge Lane Car Park CSO, Pontypool | UB3693HG |  | South East |  | Afon Lwyd - source to Mon and Brecon Canal |  |  | - | - | - | 0 |  |  |  | Communications issue - access issue
70929 | CSO at Jobswell Road, Carmarthen, SA31 3HG | UB3893HF |  | SW | West | Tawelon - headwaters to tidal limit |  |  | 113.75 | 62 | 62 | 99.63
33404 | Cedarwood Drive CSO, Cedarwood Drive, Rogerstone,Newport | UB3993HZ |  | SE | South East | Ebbw R - conf Ebbw Fach R to Maes-glas |  |  | 3.75 | 14 | 1 | 94.13
548 | Llanfair Dtffryn Clwyd SWK | Unpermitted-00548 | [6 empty] | 347.75 | 67 | 67 | 99.99
2019 | Conwy Harbour CSO | Unpermitted-2019 |  | North |  | CONWY |  |  | - | - | - | 0 |  |  |  | Telemetry archiving issue - escalated through business as usual process
2148 | Slaughterhouse CSO, Blaenau Ffestiniog | Unpermitted-2148 |  | North |  | Goedol |  |  | 0 | 0 | 0 | 12.25 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
2218 | Holyhead CSO | Unpermitted-2218 |  | N | North | Holyhead Bay |  |  | 7.5 | 2 | 2 | 81.61 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
2276 | Dee Road CSO, Connahs Quay | Unpermitted-2276 | [6 empty] | 0 | 0 | 0 | 31.39 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
2356 | Bro Alun CSO, Mold | Unpermitted-2356 |  | North |  | Alyn - Rhydymwyn to Leadmill |  |  | 69.25 | 44 | 44 | 99.18
2484 | Wrexham Park Avenue CSO | Unpermitted-2484 | [6 empty] | 0 | 0 | 0 | 100
2492 | Trofyn CSO | Unpermitted-2492 | [6 empty] | 1.25 | 1 | 1 | 59.52 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered
1280 | Maes Yr Orsedd SPS, Bodffordd | Unpermitted-2678 |  | North |  | Cefni - Cefni reservoir west |  |  | 0 | 0 | 0 | 65.9 |  |  |  | Communications issue, resolved in May 2021.
657 | Tre Taliesin SPS | Unpermitted-2707 |  | North |  | Leri - lower |  |  | 597 | 52 | 52 | 100
1011 | Tal-y-Bont SPS Overflow | Unpermitted-2744 |  | North |  | Leri - lower |  |  | 1773.5 | 93 | 93 | 100
561 | Trawsfynydd WwTW | Unpermitted-2746 |  | N | North West | Prysor |  |  | 757 | 95 | 88 | 99.97
843 | Isallt Bach SPS, Trearddur Bay | Unpermitted-2770 |  | North |  | Caernarfon Bay North |  |  | 16 | 14 | 14 | 100
2775 | Tai Lleuar CSO, Pontllyfni | Unpermitted-2775 |  | North |  | Llyfni |  |  | 0 | 0 | 0 | 60.51 |  |  |  | Communications issue, resolved in May 2021.
2847 | Flint Castle No1 SPS | Unpermitted-2794 |  | N | North East | Swinchiard Brook |  |  | 0 | 0 | 0 | 100
656 | Trefnant WwTW | Unpermitted-2891 |  | North |  | Clwyd - tidal limit to Hesbin |  |  | 761.25 | 116 | 116 | 96.71
852 | Lavister WwTW Overflow | Unpermitted-2901 |  | North |  | Pulford Brook |  |  | 2121 | 127 | 127 | 100
834 | Glyn Ceiriog WwTW | Unpermitted-2907 |  | North |  | Ceiriog - confluence Dee to Teirw |  |  | 488.75 | 86 | 86 | 100
741 | Connahs Quay WwTW Storm overflow | Unpermitted-2912 |  | North |  | Wepre Brook |  |  | 0 | 0 | 0 | 99.61
1058 | Llanuwchllyn WwTW | Unpermitted-2930 |  | North |  | Twrch |  |  | 3359.25 | 282 | 282 | 99.95
517 | Llangybi WwTW, Pwllheli | Unpermitted-2998 |  | North |  | Erch - lower |  |  | 4613.5 | 244 | 244 | 99.99
30806 | Bonvilston East WwTW Overflow | Unpermitted-30806 |  | South East |  | Llancarfan |  |  | 362.25 | 45 | 45 | 31.58 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
31103 | Tintern SWK | Unpermitted-31103 | [6 empty] | 0 | 0 | 0 | 100
31925 | Netherton SPS, Ross | Unpermitted-31925 | [6 empty] | 0 | 0 | 0 | 99.11
31201 | Ddole Rd SPS, Llandrindod Wells | Unpermitted-31962 |  | South East |  | Ithon - conf Camddwr Bk to conf R Wye |  |  | 641.5 | 58 | 58 | 51.99 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
32106 | Rear of Bush Hotel CSO, Abertillery | Unpermitted-32106 |  | South East |  | Ebbw Fach R - source to conf Ebbw R |  |  | 0 | 0 | 0 | 99.61
32118 | Woodland Rd Recreation Ground CSO, Cwmbran | Unpermitted-32118 |  | South East |  | Afon Lwyd - below Mon and Brecon Canal |  |  | 836.5 | 104 | 104 | 87.67 |  |  |  | Communications issue from 01/01/ to 10/02/21, resolved.
32269 | Taff Terrace CSO, Abercynon | Unpermitted-32269 |  | South East |  | Nant Clydach - source to conf R Taff |  |  | 1.75 | 7 | 7 | 98.98
32285 | Martins Terrace CSO, Abercynon | Unpermitted-32285 |  | South East |  | Taff - conf R Cynon to conf Rhondda R |  |  | 1.25 | 5 | 5 | 99.61
32331 | Rear of William St CSO, Ystrad | Unpermitted-32331 |  | South East |  | Rhondda R - source to conf Afon Rhondda Fach |  |  | 17.5 | 23 | 23 | 12.67 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
32354 | TREHERBERT GEORGE STREET | Unpermitted-32354 |  | SE | South East | Rhondda R - source to conf Afon Rhondda Fach |  |  | 17.5 | 9 | 9 | 99.55
32405 | River Row CSO, Abercynon | Unpermitted-32405 |  | South East |  | Cynon - conf Aman R to conf R Taff |  |  | 710 | 78 | 78 | 97.19
32487 | Pit Place CSO, Cwmbach | Unpermitted-32487 |  | South East |  | Cynon - conf Aman R to conf R Taff |  |  | - | - | - | 0 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
32500 | ABERAMAN FFORCHAMAN STREET CAPEL SOAR | Unpermitted-32500 |  | SE | South East | Aman R - source to conf Afon Cynon |  |  | 0 | 0 | 0 | 99.89
32602 | Rear of No134 Gladstone Rd CSO | Unpermitted-32602 |  | SE | South East | Cadoxton - headwaters to tidal limit |  |  | 69.25 | 70 | 70 | 94.63
32603 | Rear of No144 Gladstone Rd CSO | Unpermitted-32603 |  | SE | South East | Cadoxton - headwaters to tidal limit |  |  | 0 | 0 | 0 | 99.59
33313 | Lewistown Park CSO, Treforest | Unpermitted-33313 |  | South East |  | Taff - conf Rhondda R to Castle Street |  |  | 83.25 | 29 | 29 | 15.23 |  |  |  | Data unreliable from 26/02 to 31/12/2021. Due to erratic telemetry signal. Instrumentation task escalated through business as usual for instrumentation defect.
33314 | 95 James St CSO, Pontypridd | Unpermitted-33314 |  | South East |  | Taff - conf Rhondda R to Castle Street |  |  | 18.25 | 30 | 30 | 90.74
33315 | 38 Poplar Rd CSO, Rhydyfelin | Unpermitted-33315 |  | South East |  | Taff - conf Rhondda R to Castle Street |  |  | 0.5 | 2 | 2 | 99.89
33316 | Llys Tripp CSO, Gwaelod-y-Garth | Unpermitted-33316 |  | South East |  | Taff - conf Rhondda R to Castle Street |  |  | 31.25 | 40 | 40 | 99.41
33347 | Prospect Place CSO, Llanhilleth | Unpermitted-33347 |  | South East |  | Ebbw R - conf Ebbw Fach R to Maes-glas |  |  | 17.75 | 14 | 14 | 96.24
33356 | Castle St CSO | Unpermitted-33356 | [6 empty] | 15.25 | 23 | 23 | 100
33357 | Rose Hayworth CSO | Unpermitted-33357 | [6 empty] | 0 | 0 | 0 | 99.79
33367 | Beaufort Terrace Clubhouse CSO, Ebbw Vale | Unpermitted-33367 |  | South East |  | Ebbw R - source to conf Ebbw Fach R |  |  | 5 | 11 | 11 | 99.59
33375 | Holland St CSO, Ebbw Vale | Unpermitted-33375 |  | South East |  | Ebbw R - source to conf Ebbw Fach R |  |  | 49 | 44 | 44 | 98.74
33383 | Muriel Terrace CSO, Dowlais | Unpermitted-33383 |  | South East |  | Taff - conf Taf Fechan to conf R Cynon |  |  | 0 | 0 | 0 | 99.89
31180 | Castle Coch SPS | Unpermitted-33395 |  | South East |  | Mill Reen - source to R Severn Estuary |  |  | 1683.75 | 171 | 171 | 98.9
33403 | Allt Yr Yn Avenue CSO | Unpermitted-33403 | [6 empty] | 10.5 | 19 | 19 | 99.59
33520 | Westville CSO, Abertysswg | Unpermitted-33520 |  | South East |  | Rhymney R - source to conf Nant Bargod Rhymni |  |  | 0 | 0 | 0 | 98.5
31322 | Mill Lane SPS, Usk | Unpermitted-33569 |  | South East |  | Usk - conf R Gavenny to conf Olway Bk |  |  | 280.25 | 83 | 83 | 98.53
31213 | Erwood SPS | Unpermitted-33625 |  | South East |  | Clettwr Bk - source to conf R Wye |  |  | 110.25 | 25 | 25 | 66.08 |  |  |  | Communications issue, resolved in November 2021.
31323 | Mill St SPS, Rhayader | Unpermitted-33643 |  | South East |  | Wye - conf to conf Afon Marteg to conf Afon Elan |  |  | 48.5 | 11 | 11 | 98.37
50704 | Meidrim WwTW | Unpermitted-50704 |  | South West |  | Dewi Fawr - headwaters to confluence with Cynin |  |  | 188 | 56 | 56 | 100
51900 | Dwr Y Felin Rd CSO, Neath | Unpermitted-51900 |  | South West |  | Neath |  |  | 165.5 | 79 | 79 | 98.98
51924 | Bwrw Rd CSO, Loughor | Unpermitted-51924 |  | South West |  | Loughor Outer |  |  | 434.75 | 86 | 86 | 99.14
51947 | Newton Lady Housty CSO | Unpermitted-51947 |  | South West |  | Bristol Channel Outer North |  |  | 4.75 | 10 | 10 | 61.69 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
52043 | London Close CSO, Cwmafan | Unpermitted-52043 |  | South West |  | Afan - confluence with Pelenna to tidal limit |  |  | 681 | 98 | 98 | 99.95
52106 | Cynonville CSO | Unpermitted-52106 | [6 empty] | 64.5 | 12 | 12 | 58.24 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
52297 | LOUGHOR APPROX 100YDS D/S CONF LLIW&LLAN | Unpermitted-52297 |  | SW | West | LOUGHOR |  |  | 235.5 | 51 | 51 | 95.19
52376 | NOTTAGE ROUNDABOUT POINT 59 INTO WILDERN | Unpermitted-52376 |  | SW | West | Ogmore - confluence with Llynfi to tidal limit |  |  | 0 | 0 | 0 | 99.73
52408 | Riverside Cottages CSO, Coytrahen | Unpermitted-52408 |  | South West |  | Llynfi - Lletty Brongu STW to conf with Ogmore |  |  | 8.75 | 20 | 20 | 99.67
52435 | Brynmenyn CSO | Unpermitted-52435 | [6 empty] | 0 | 0 | 0 | 60.73 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
50840 | BISHOPSTON G CHURCH LANE PS | Unpermitted-52459 |  | SW | Central | Bishopston Stream - headwaters to tidal limit |  |  | 0 | 0 | 0 | 99.94
52469 | NEWTON ROAD CSO | Unpermitted-52469 |  | SW | West |  |  |  | 187 | 84 | 84 | 94.23
52472 | Ynys Y Mond Rd CSO, Glais | Unpermitted-52472 |  | South West |  | Tawe -confluence with Twrch to tidal limit |  |  | 27 | 15 | 15 | 94.78
52579 | Cwmgrach STW Overflow | Unpermitted-52579 |  | SW | Central | Dewi Fawr - headwaters to confluence with Cynin |  |  | 2 | 2 | 2 | 86.07 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
50615 | Ffostrasol WwTW | Unpermitted-52804 |  | South West |  | Cerdin - headwaters to confluence with Teifi |  |  | - | - | - | 0 |  |  |  | Telemetry archiving issue - escalated through business as usual process
50691 | Llanybri WwTW | Unpermitted-52817 |  | South West |  | Mwche Stream - headwaters to tidal limit |  |  | 22.5 | 22 | 22 | 99.94
50810 | WICK | Unpermitted-52821 |  | SW | Central |  |  |  | 1792.75 | 147 | 147 | 99.97
70420 | Malpas Park CSO, Newport | Unpermitted-70420 |  | South East |  | Pantyreos Bk - source to Barrack Hill |  |  | 245.5 | 52 | 52 | 87.12 |  |  |  | Data unreliable from 25/02/21 to 08/03/21 and from 18/03/21 to 19/04/21. Due to erratic telemetry signal, resolved.
70689 | BLAENGARW OXFORD STREET NO 168 | Unpermitted-70689 |  | SW | West |  |  |  | 0.5 | 2 | 2 | 54.39 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
70696 | Mill Street CSO, Cwmfelin | Unpermitted-70696 |  | South West |  | Llynfi - headwaters to Lletty Brongu STW |  |  | - | - | - | 0 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
70708 | PORTHCAWL SANDERLING CLOSE NO 7 | Unpermitted-70708 | [6 empty] | 0 | 0 | 0 | 0.83 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
70716 | High St CSO, Pontycymer | Unpermitted-70716 | [6 empty] | 0 | 0 | 0 | 100
50664 | Llanfihangel-Ar-Arth WwTW Storm | Unpermitted-70877 |  | South West |  | Teifi - Afon Dulas to Afon Clettwr |  |  | 168.75 | 23 | 23 | 99.99
70930 | Carmarthen - Carm. Decorators | Unpermitted-70930 |  | SW | West |  |  |  | 305 | 95 | 95 | 98.94
70961 | No6 Heol Dyfan CSO, Morriston | Unpermitted-70961 |  | South West |  | Tawe -confluence with Twrch to tidal limit |  |  | 31.5 | 26 | 26 | 82.52 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
71079 | Newton Rd CSO | Unpermitted-71079 |  | South West |  | Swansea Bay |  |  | 56 | 34 | 34 | 63.23 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
71286 | Caerleon Rd CSO, Ponthir | Unpermitted-71286 |  | South East |  | Afon Lwyd - below Mon and Brecon Canal |  |  | 244.75 | 92 | 92 | 95.02
71317 | Drury Lane CSO, Aberaeron | Unpermitted-71317 |  | South West |  | Cardigan Bay Central |  |  | 25 | 13 | 13 | 99.38
71371 | Temple St CSO, Llandrindod Wells | Unpermitted-71371 |  | South East |  | Ithon - conf Camddwr Bk to conf R Wye |  |  | 208.25 | 60 | 60 | 80.57 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
31399 | Llangorse SPS | Unpermitted-71377 |  | South East |  | Afon Llynfi - source to conf Dulas Bk |  |  | 1.25 | 1 | 1 | 96.28
71387 | Saron CSO | Unpermitted-71387 |  | South West |  | Bargod - headwaters to confluence with Teifi |  |  | 0 | 0 | 0 | 16.46 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
71398 | RAILWAY TERRACE, CWYMLLYNFELL | Unpermitted-71398 |  | SW | West |  |  |  | 245 | 89 | 89 | 86.62 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
71402 | O/S 3 BRYNYMOR ROAD GOWERTON | Unpermitted-71402 |  | SW | West |  |  |  | 1 | 2 | 2 | 86.64 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
71408 | 72 Bethel Rd CSO, Lower Cwmtwrch | Unpermitted-71408 |  | South West |  | Twrch - conf with Nant Gwys to conf with Tawe |  |  | 973 | 87 | 87 | 74.08 |  |  |  | Communications issues, resolved in July 2021.
71427 | Swan Rd CSO, Baglan | Unpermitted-71427 |  | South West |  | Baglan Brook - headwaters to conf with River Neath |  |  | 120.75 | 80 | 80 | 99.14
71430 | 22 Cricklewood Close CSO Bridgend | Unpermitted-71430 |  | South West |  | Ogmore - confluence with Llynfi to tidal limit |  |  | 13.75 | 12 | 12 | 99.34
71437 | Adj 1 Commercial Street Nantymoel | Unpermitted-71437 |  | West | PENYBONT (MERTHYR MAWR) | Ogwr Fawr - headwaters to confluence with Ogmore |  |  | 202.25 | 76 | 59 | 99.33
71442 | No2 Oxford St CSO, Pontycymmer | Unpermitted-71442 |  | South West |  | Garw - headwaters to confluence with Ogmore |  |  | 44.75 | 30 | 30 | 99.61
71445 | Yr Hafon CSO, Pontycymmer | Unpermitted-71445 |  | South West |  | Garw - headwaters to confluence with Ogmore |  |  | 37.25 | 15 | 15 | 99.68
71570 | Woodfield Rd CSO, Blackwood | Unpermitted-71570 |  | South East |  | Sirhowy R - Rock Villas to conf Afon Ebwy |  |  | 154 | 53 | 53 | 97.88
71640 | 2 Pont Rectory Lane CSO, Llanllyfni | Unpermitted-71640 |  | North |  | Llyfni |  |  | 8.75 | 21 | 21 | 99.93
71663 | Penally Rd CSO | Unpermitted-71663 |  | South East |  | Ely R - conf Nant Clun to Allot Gardens, Ely |  |  | 0.75 | 3 | 3 | 99.29
71691 | School St CSO, Tirphil | Unpermitted-71691 |  | South East |  | Rhymney R - source to conf Nant Bargod Rhymni |  |  | 0.5 | 2 | 2 | 99.89
71696 | 30 Church St CSO, Ystrad Mynach | Unpermitted-71696 |  | South East |  | Rhymney R - conf Nant Cylla to Chapel Wood |  |  | 0.5 | 2 | 2 | 98.26
71953 | Eureka Place CSO, Ebbw Vale | Unpermitted-71953 |  | South East |  | Ebbw R - source to conf Ebbw Fach R |  |  | 15.75 | 37 | 37 | 99.28
72018 | Rock Park Close CSO | Unpermitted-72018 | [6 empty] | 242.5 | 53 | 53 | 99.12
72330 | Pwll y Glaw CSO, Front of No 2 | Unpermitted-72330 |  | SW | West | Afan - confluence with Pelenna to tidal limit |  |  | 4.75 | 9 | 1 | 95.64
72428 | Pentre Felin CSO, Betws Y Coed | Unpermitted-72428 |  | North |  | Llugwy - Conwy to Nant gwryd |  |  | 0 | 0 | 0 | 24.54 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
72447 | 25 Cricklewood Close CSO Bridgend | Unpermitted-72447 |  | South West |  | Ogmore - confluence with Llynfi to tidal limit |  |  | 22 | 17 | 17 | 99.72
72536 | Charles Street CSO, Blaenavon | Unpermitted-72536 |  | SE | South East | Afon Lwyd - source to conf Dowlais Bk |  |  | 298.75 | 57 | 45 | 98.71
72560 | Cynon Terrace CSO, Penrhiwceiber | Unpermitted-72560 |  | South East |  | Cynon - conf Aman R to conf R Taff |  |  | 12 | 42 | 42 | 99.89
72597 | 15 Alexandra Rd CSO, Treforest | Unpermitted-72597 |  | South East |  | Taff - conf Rhondda R to Castle Street |  |  | 0.75 | 3 | 3 | 99.62
72598 | 2 Clarence Street CSO Pentre | Unpermitted-72598 |  | East | CARDIFF BAY | Rhondda R - source to conf Afon Rhondda Fach |  |  | 0.75 | 3 | 0 | 99.33
72606 | 50 Mount Pleasant CSO, Saltney | Unpermitted-72606 |  | North |  | DEE (N. WALES) |  |  | 94.25 | 74 | 74 | 98.69
72624 | BLAEN-Y-CWM ROAD CSO BLAENCWM | Unpermitted-72624 |  | SE | East |  |  |  | 135.5 | 42 | 42 | 96.57
72631 | 9 Countess Place CSO, Penarth | Unpermitted-72631 |  | South East |  | Cadoxton - headwaters to tidal limit |  |  | 0 | 0 | 0 | 99.62
72669 | Foundry View CSO, Aberdare | Unpermitted-72669 |  | South East |  | Aman R - source to conf Afon Cynon |  |  | 0.25 | 1 | 1 | 99.47
72681 | Glyndwr Avenue CSO, Pontypridd | Unpermitted-72681 |  | South East |  | Taff - conf Rhondda R to Castle Street |  |  | 0.25 | 1 | 1 | 99.62
72760 | Libanus Road CSO Gorseinon | Unpermitted-72760 |  | SW | West | Lliw - headwaters to confluence with Llan |  |  | 93.5 | 45 | 45 | 86.39 |  |  |  | Communications issue, resolved in March 2021.
72762 | Higher Berse Rd CSO, Wrexham | Unpermitted-72762 |  | North |  | Gwenfro |  |  | 258.75 | 91 | 91 | 95.05
72770 | Bryngoleu St CSO, Cefn Fforest | Unpermitted-72770 |  | South East |  | Rhymney R - Nant Bargod Rhymni to conf Nant Cylla |  |  | 5.25 | 14 | 14 | 99.26
72810 | Parc Trostre No1 SPS | Unpermitted-72810 | [6 empty] | 8.5 | 4 | 4 | 31.65 |  |  |  | Communications issue, resolved in September 2021.
72835 | The Nook CSO Oxwich | Unpermitted-72835 |  | SW | West |  |  |  | 619.5 | 31 | 31 | 99.72
72902 | Lamb's Square/Lower Square, Beaufort | Unpermitted-72902 | [6 empty] | 40.75 | 51 | 51 | 80.95 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
73001 | Park Hill CSO, Penrhiwceiber Rd, Mountain Ash | Unpermitted-73001 |  | South East |  | Cynon - conf Aman R to conf R Taff |  |  | 3 | 7 | 7 | 99.89
31302 | Forge Bridge SPS, Machen | Unpermitted-73044 |  | South East |  | Rhymney R - conf Nant Cylla to Chapel Wood |  |  | 2 | 5 | 5 | 99.93
51166 | St Clears Car Park SPS Overflow | Unpermitted-73047 |  | South West |  | Cynin - headwaters to tidal limit |  |  | 2 | 6 | 6 | 100
73061 | CSO in rear of 79 St Annes Drive, Llantwit Fardre | Unpermitted-73061 |  | South East |  | Nant Clun - source to conf Ely R |  |  | 21.5 | 7 | 7 | 99.04
73072 | 18 Wainfelin Rd CSO, Pontypool | Unpermitted-73072 |  | South East |  | Afon Lwyd - source to Mon and Brecon Canal |  |  | 77 | 24 | 24 | 96.68
73075 | Bridgend Rd CSO, Llanharan | Unpermitted-73075 |  | South East |  | Ewenny Fach - headwaters to confluence with Ewenny |  |  | 0.75 | 2 | 2 | 99.33
72314 | Ty Mawr SPS, Holyhead | Unpermitted-73170 |  | North |  | Holyhead Bay |  |  | 0 | 0 | 0 | 100
51051 | MANORDEILO SPS CSO | Unpermitted-73180 |  | SW | South West | Tywi (Llandovery Bran to Cothi confl) |  |  | 2286 | 113 | 112 | 100
73214 | Waterton Park SPS, Bridgend | Unpermitted-73214 |  | South West |  | Ewenny - conf with Ewenny Fach to tidal limts |  |  | 0 | 0 | 0 | 100
73219 | Ivr Tor CSO, Wainfelin Rd, Pontypool | Unpermitted-73219 |  | South East |  | Afon Lwyd - source to Mon and Brecon Canal |  |  | 9.5 | 16 | 16 | 99.55
73252 | 2 Maple Road CSO Penarth | Unpermitted-73252 |  | SE | South East | Cadoxton - headwaters to tidal limit |  |  | 1.75 | 5 | 2 | 95.73
73254 | Blaenavon RFC | Unpermitted-73254 |  | SE | South East | Afon Lwyd - source to conf Dowlais Bk |  |  | 7.5 | 4 | 4 | 98.86
73314 | Duke St CSO | Unpermitted-73314 | [6 empty] | 22.25 | 30 | 30 | 99.86
73315 | Duffryn Rd CSO, Mountain Ash | Unpermitted-73315 |  | South East |  | Cynon - conf Aman R to conf R Taff |  |  | 78.5 | 32 | 32 | 99.77
73316 | Ty Mawr Rd CSO | Unpermitted-73316 | [6 empty] | 1.25 | 4 | 4 | 99.88
73328 | GLANOWEN ROAD CSO Swansea | Unpermitted-73328 |  | SW | West |  |  |  | 2.25 | 7 | 7 | 99.64
73332 | Richmond Rd CSO | Unpermitted-73332 | [6 empty] | 0 | 0 | 0 | 99.84
73334 | 153 Foryd Rd CSO, Kinmel Bay | Unpermitted-73334 |  | North |  | Gele |  |  | 0.25 | 1 | 1 | 99.73
73425 | Llanwrthwl WwTW | Unpermitted-73425 | [6 empty] | 0 | 0 | 0 | 1.92 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
50715 | Nanternis WwTW | Unpermitted-73430 |  | South West |  | Cardigan Bay Central |  |  | 2294 | 144 | 144 | 100
50752 | Porthgain WwTW | Unpermitted-73436 |  | South West |  | Cardigan Bay South |  |  | 808.75 | 58 | 58 | 100
50560 | Caio WwTW | Unpermitted-73438 |  | South West |  | Annell - headwaters to confluence with Cothi |  |  | 76.75 | 7 | 7 | 99.99
50687 | Llansteffan WwTW | Unpermitted-73493 |  | South West |  | Tywi & Cywyn & Gwendraeth |  |  | 316.75 | 72 | 72 | 96.21
50748 | Pontrhydyceirt WwTW | Unpermitted-73568 |  | South West |  | Morgenau - headwaters to confluence with Teifi |  |  | - | - | - | 0 |  |  |  | Telemetry archiving issue - escalated through business as usual process
50765 | Rhossili WwTW | Unpermitted-73571 |  | South West |  | Carmarthen Bay |  |  | 28.75 | 12 | 12 | 99.95
31024 | Norton WwTW Storm Overflow | Unpermitted-73637 |  | South East |  | Norton Bk - source to conf R Lugg |  |  | 1.5 | 2 | 2 | 88.93 |  |  |  | Communications issue, resolved in September 2021.
73721 | O/S 23 Y Gaer Dafen CSO Llanelli | Unpermitted-73721 |  | SW | West | Dafen - headwaters to tidal limit |  |  | 5.25 | 13 | 5 | 96.05
73799 | Ysgol Griffith Jones CSO | Unpermitted-73799 |  | SW | West | Dewi Fawr - headwaters to confluence with Cynin |  |  | 211.5 | 34 | 32 | 99.45
74540 | Prospect Rd CSO, Osbaston | Unpermitted-74540 |  | South East |  | Monnow - conf Afon Honddu to conf R Wye |  |  | 0 | 0 | 0 | 99.7
74688 | 57 Glandwr St CSO, Abertillery | Unpermitted-74688 |  | South East |  | Ebbw Fach R - source to conf Ebbw R |  |  | 0 | 0 | 0 | 99.62
74689 | Pontypridd Railway Station CSO | Unpermitted-74689 |  | South East |  | Taff - conf Rhondda R to Castle Street |  |  | 0.25 | 1 | 1 | 99.62
74695 | 48 Eaton St CSO, Swansea | Unpermitted-74695 |  | South West |  | Tawe -confluence with Twrch to tidal limit |  |  | 0 | 0 | 0 | 97.99
74727 | Forgeside Rd CSO, Blaenavon | Unpermitted-74727 |  | South East |  | Afon Lwyd - source to Mon and Brecon Canal |  |  | 0 | 0 | 0 | 99.62
74766 | Tan Y Bryn Gardens CSO, Llwydcoed | Unpermitted-74766 |  | South East |  | Afon Cynon - source to conf Aman R |  |  | 185.5 | 42 | 42 | 99.15
74812 | Mach Worth Rd CSO, Porthcawl | Unpermitted-74812 |  | South West |  | Bristol Channel Outer North |  |  | 19.25 | 29 | 29 | 99.71
74868 | Crown St CSO, Caernarfon | Unpermitted-74868 |  | North |  | Menai Strait |  |  | 0 | 0 | 0 | 66.59 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
484 | Bryngwran WwTW Storm Overflow | Unpermitted-74870 |  | North |  | Crigyll |  |  | 3582.25 | 226 | 226 | 99.99
51193 | LLANELLI TROSTRE ROAD NO 2 SPS | Unpermitted-74958 |  | SW | Central |  |  |  | 2068.75 | 93 | 93 | 100
50604 | Drefach WwTW | Unpermitted-74959 |  | SW | South West |  |  |  | 1776.75 | 231 | 231 | 94.49
1053 | Llangernyw WwTW Storm Overflow | Unpermitted-74960 |  | North |  | Elwy - Melai to Gallen |  |  | 1449.25 | 122 | 122 | 100
75024 | Paddys Goose CSO | Unpermitted-75024 | [6 empty] | 400 | 84 | 84 | 98.95
51073 | Nolton Haven SPS | UP3629XK |  | SW | South West | UNCONSENTED |  | Nolton Haven | 378.75 | 32 | 29 | 100 | BW | 5 in Bathing Season
72128 | RUMNEY HILL CONTROL POINT CSO | WQD000381 |  | SE | Cardiff | SEVERN LOWER |  |  | 14 | 14 | 14 | 99.84
72380 | LUGG BRIDGE CSO | WQD000441 |  | SE | West | R Lugg - conf Norton Bk to conf R Arrow |  |  | 15.5 | 4 | 4 | 86 |  |  |  | Communications issue - escalated through business as usual process for communications failures.
3283 | MOELFRE PS MOELFRE | WQD001089 |  | N | North West | Coastal Waters of the Irish Sea |  | Traeth Lligwy | 113.25 | 20 | 20 | 100
72079 | CSO IN FOOTPATH ADJ BETHEL RD | WQD001597 |  | SW | Bridgend Hereford & Mid Wales | Neath - conf with Nedd Fechan and Mellte to TL |  |  | 173.25 | 37 | 31 | 99.97
31966 | MATHERN SPS MATHERN CHEPSTOW | WQD002763 |  | SE | South East | Monks Ditch - source to Wainbridge |  |  | 5.5 | 3 | 3 | 99.94
73320 | End of Park Place CSO, Cilfynydd | WQD004364 | [6 empty] | 7 | 10 | 4 | 99.36
72252 | ST CADOCS AVENUE CSO | WQD004639 |  | SE | Cardiff | Cadoxton - headwaters to tidal limit |  |  | 19.75 | 12 | 12 | 99.81 | BW | 5 in Bathing Season
73167 | A SEWAGE PUMPING STATION CRAIG Y | WQD004680 |  | N | North West | Goch Amlwch |  |  | 409.75 | 55 | 55 | 99.96
72259 | RHYDDLAN NETWORK TANK CSO | WQD004714 |  | N | North East | tidal estuary of river Clwyd |  | Rhyl | 23.5 | 3 | 3 | 100
32819 | WARREN SLADE SPS, OPP NO 13 BLUEBELL DRIVE | WQD004799 |  | SE | South East | WYE |  |  | 0 | 0 | 0 | 97.77
72180 | DYFATTY PARK SPS, BURRY PORT | WQD004967 |  | SW | Central | a drain leading to the river Loughor | Burry N |  | 0 | 0 | 0 | 100 | BW | 5 in Bathing Season
72175 | BRYN AVENUE CSO, BURRY PORT | WQD004969 |  | SW | West | Barnaby Pill | Burry N |  | 0 | 0 | 0 | 99.73 | BW | 5 in Bathing Season
72423 | BRITANNIA COEDCAE ROAD PONTYPRIDD | WQD005457 |  | SE | Cardiff | Rhondda R - conf Afon Rhondda Fach to conf R Ta |  |  | 1021.25 | 136 | 136 | 94.2
71452 | BLACKMILL CSO & STORAGE TANKS BR'ND | WQD005458 |  | SW | Bridgend Hereford & Mid Wales | Ogmore - Ogwr Fach and Ogwr Fawr conf |  |  | 1437 | 81 | 81 | 97.68
72274 | SWN Y DWR CSO | WQD005679 |  | N | North East | afon y Garth | Dee W |  | 22 | 14 | 10 | 99.51
72251 | BRYNDULAIS CSO, SEVEN SISTERS | WQD005680 |  | SW | Swansea | The Afon Dulais |  |  | 169.5 | 41 | 41 | 100
72275 | JAMES STREET CSO | WQD005714 |  | SW | Swansea | Upper Clydach - headwaters to confluen |  |  | 254 | 72 | 53 | 99.27
50546 | BLAENFFOS WWTW CSO | WQD005734 |  | SW | Central | Nyfer - headwaters to confluence with Brynberia |  |  | 1187.75 | 75 | 72 | 99.98
2466 | GAMEKEEPER PH, LOWER STREET, ST ASAPH | WQD005890 |  | N | North | Elwy - Clwyd to Afon Melai |  |  | 0.25 | 1 | 1 | 100
72164 | Combined Sewer Overflow at Beach Hill | WQD007456 |  | SW | West | Milford Haven Outer |  |  | 115.75 | 68 | 68 | 100
31253 | HOWEY SEWAGE PUMPING STATION CSO EO | WQD009237 |  | SE | South East | Howey Bk - source to conf R Ithon |  |  | 331.5 | 45 | 44 | 99.92
70292 | LLANDDEWI BREFI CSO | WQD009363 |  | SW | West | Brefi - headwaters to confluence with Teifi |  |  | 365.5 | 63 | 46 | 98.98
72310 | COMBINED SEWER OVERFLOW AT | WQD009366 |  | SE | Valleys | Ebbw R - source to conf Ebbw Fach R |  |  | 0.75 | 1 | 1 | 99.93
50591 | CWMDUAD STW | WQD009506 |  | SW | South West | Duad - headwaters to confluence with Gochen |  |  | 1659.75 | 106 | 103 | 100
31429 | USK ROAD PS USK ROAD CAERLEON | WQD009717 |  | SE | South East | Llwynau Bk - source to conf R Usk |  |  | - | - | - | 0 |  |  |  | Telemetry archiving issue - escalated through business as usual process
72336 | COMBINED SEWER OVERFLOW SERVING | WQD009830 |  | SE | Gwent | Rhymney R - conf Nant Cylla to Chapel Wood |  |  | 0.25 | 1 | 0 | 99.93
30822 | BUILTH WELLS WWTW STORM | WQD009903 |  | SE | South East | R Wye - conf R Irfon to Brewardine Br |  |  | 1181.25 | 96 | 95 | 99.92
50876 | CILGERRAN PUMPING STATION | WQD009904 |  | SW | South West | Teifi - conf with Nant Wern-Macwydd to |  |  | 1185.25 | 106 | 102 | 100
50856 | BRYNOG ARMS PUMPING STATION | WQD009964 |  | SW | South West | Aeron - confluence with Gwili to tidal limit |  |  | 659 | 43 | 43 | 99.99
72384 | PENYFFORDD TERMINAL SPS | WQD009965 |  | N | North East | Pulford Brook |  |  | 105.75 | 29 | 27 | 100
72377 | GREENFIELD PARENT CSO HOLYWELL | WQD009966 |  | N | North East | Holywell Stream | Dee W |  | 310.5 | 94 | 68 | 99.89
1125 | PEN Y MAES PUMPING STATION | WQD009968 |  | N | North East | Unnamed tributary of the River Dee | Dee W |  | 452 | 60 | 52 | 100
486 | Henllan (nr Denbigh) STW CSO asset 2982 | WQD011014 |  | N | North East | Afon Meirchion |  | Rhyl | 144 | 81 | 65 | 99.97
51212 | CSO serving Wolfsdale SPS, Wolfsdale, Pembrokeshire, SA62 6JH | XB3990HH |  | SW | South West | W. Cleddau - Anghof conf to Cartlett Brook conf |  |  | 814 | 63 | 62 | 53.7 |  |  |  | Data unreliable from 01/01 to 18/06/2021. Due to static telemetry signal, resolved
72712 | EAST OF KINGFISHER COURT | XP3425XQ |  | SW | West | SEVERN LOWER |  |  | 248 | 23 | 23 | 96.16 | SFW | 26 in the Year
73648 | SCLEDDAU WORKS INLET . . | ZB3590HM |  | SW | South West | Cleddau N. - headwaters to conf with Nant y Bug |  |  | 3394.75 | 171 | 170 | 100
72682 | Heol Eithryn Combined Sewer Overflow, Clydach, Swansea. | ZP3126GM |  | SW | West | Lower Clydach - headwaters to confluence with Tawe |  |  | 84.5 | 19 | 19 | 71.51 |  |  |  | Deterioration of 4G network coverage. Alternative solutions are being considered.
Note on D1: Lennox, Gillian: do we have more than one on a permit
Note on H1: Lennox, Gillian: EDMs with rB5 or S8 drivers will have been associated with a bathing water or shellfishery to support their inclusion onto the NEP for EDM, so information should be available.
Note on J1: Lennox, Gillian: The “Duration (hours)” column is the total duration that the spills were measured to occur. This is not to be derived from the 12-24 counts. It is to be derived from the sum of the difference between end and start times.
Note on M1: Lennox, Gillian: condition reads Percentage of time in the recording period that event duration monitoring equipment is operational